## PMIS_Config (hidden)
BEDFORD VA EHRM PMIS — CONFIG / BUILDING MAP | [7 empty] | Selector IDs
Purpose | Central building list used for selectors, validation, QA, and future dashboard mapping. Edit only if buildings/sheet names change. | [6 empty] | 01 | B01_Assessment
[8 empty] | 02 | B02_Assessment
Display Building | Assessment Sheet | PMIS_Data Row | Open Assessment Link | Has Sheet? | Has PMIS Row? | Has Trade Notes? | Notes | 03 | B03_Assessment
B01 | B01_Assessment | 3 | Open | Yes | Yes | Yes |  | 04 | B04_Assessment
B02 | B02_Assessment | 4 | Open | Yes | Yes | Yes |  | 05 | B05_Assessment
B03 | B03_Assessment | 5 | Open | Yes | Yes | Yes |  | 06 | B06_Assessment
B04 | B04_Assessment | 6 | Open | Yes | Yes | Yes |  | 07 | B07_Assessment
B05 | B05_Assessment | 7 | Open | Yes | Yes | Yes |  | 08 | B08_Assessment
B06 | B06_Assessment | 8 | Open | Yes | Yes | Yes |  | 09 | B09_Assessment
B07 | B07_Assessment | 9 | Open | Yes | Yes | Yes |  | 10 | B10_Assessment
B08 | B08_Assessment | 10 | Open | Yes | Yes | Yes |  | 12 | B12_Assessment
B09 | B09_Assessment | 11 | Open | Yes | Yes | Yes |  | 13 | B13_Assessment
B10 | B10_Assessment | 12 | Open | Yes | Yes | Yes |  | 14 | B14_Assessment
B12 | B12_Assessment | 13 | Open | Yes | Yes | Yes |  | 15 | B15_Assessment
B13 | B13_Assessment | 14 | Open | Yes | Yes | Yes |  | 16 | B16_Assessment
B14 | B14_Assessment | 15 | Open | Yes | Yes | Yes |  | 17 | B17_Assessment
B15 | B15_Assessment | 16 | Open | Yes | Yes | Yes |  | 18 | B18_Assessment
B16 | B16_Assessment | 17 | Open | Yes | Yes | Yes |  | 20 | B20_Assessment
B17 | B17_Assessment | 18 | Open | Yes | Yes | Yes |  | 21 | B21_Assessment
B18 | B18_Assessment | 19 | Open | Yes | Yes | Yes |  | 22 | B22_Assessment
B20 | B20_Assessment | 20 | Open | Yes | Yes | Yes |  | 33 | B33_Assessment
B21 | B21_Assessment | 21 | Open | Yes | Yes | Yes |  | 61 | B61_Assessment
B22 | B22_Assessment | 22 | Open | Yes | Yes | Yes |  | 62 | B62_TR_Assessment
B33 | B33_Assessment | 23 | Open | Yes | Yes | Yes |  | 70 | B70_TR_Assessment
B61 | B61_Assessment | 24 | Open | Yes | Yes | Yes |  | 78 | B78_Assessment
B62 | B62_TR_Assessment | 25 | Open | Yes | Yes | Yes |  | 80 | B80_Assessment
B70 | B70_TR_Assessment | 26 | Open | Yes | Yes | Yes |  | 82 | B82_Assessment
B78 | B78_Assessment | 27 | Open | Yes | Yes | Yes |  | BCH | BCH_Assessment
B80 | B80_Assessment | 28 | Open | Yes | Yes | Yes |  | MCR | MCR_Assessment
82B | B82_Assessment | 29 | Open | Yes | Yes | Yes |  | SITE | SITE_Assesment
CH | BCH_Assessment | 30 | Open | Yes | Yes | Yes
MCR | MCR_Assessment | 31 | Open | Yes | Yes | Yes
SITE | SITE_Assesment | 32 | Open | Yes | Yes | Yes

## Data_Health (hidden)
BEDFORD VA EHRM PMIS — DATA HEALTH / RELEASE QA
Purpose | Quick confidence panel for workbook architecture, missing mappings, and dashboard data flow. Formulas recalculate when opened in Excel.
Check | Current Value | Expected | Status | Notes
Assessment sheets mapped | 30 | 30 | OK | Mapped source assessment sheets from PMIS_Config.
PMIS_Data building rows | 30 | 30 | OK | One row per building / area in PMIS_Data.
PMIS_Trade_Notes rows | 33 | 30 | OK | One row per building / area in PMIS_Trade_Notes.
Command Center selected building | 61 | Not blank | OK | Building selector drives Command Center cards.
Command Center PMIS match row | 22 | >=1 | OK | Helper row used to retrieve PMIS_Data values.
Open risks total | 0 | >=0 | OK | Campus-wide open risks.
Open questions total | 0 | >=0 | OK | Campus-wide open questions.
Open photos total | 0 | >=0 | OK | Campus-wide open photos.
Active shutdown total | 0 | >=0 | OK | Campus-wide shutdown indicators.
Missing trade notes | 0 | 0 | OK | PMIS_Trade_Notes mapping check.
Missing assessment sheets | 0 | 0 | OK | Assessment sheet existence check.
Today's Focus rows | 30 | >=1 | OK | Formula-fed worklist built from PMIS_Data.
Top focus item | SITE | Not blank | OK | Highest priority work item calculated from shutdowns, risks, questions, and readiness.
Command Center quick link | Today's Focus | Visible | OK | Command Center includes shortcut to Today's Focus.

## README_ARCHITECTURE (hidden)
BEDFORD VA EHRM PMIS — ARCHITECTURE / USER GUIDE
What this is | A lightweight Project Management Information System for multidisciplinary facility assessments. The workbook is designed so building assessment sheets remain the source of truth while dashboards display the current operational picture.
Core workflow | 1. Update the building assessment sheet. 2. PMIS_Data rolls up metrics. 3. PMIS_Trade_Notes rolls up narrative/trade notes. 4. Command_Center displays the selected building. 5. V4_Mission_Control summarizes campus-wide health.
Non-negotiable rules | • Edit project data on Building Assessment sheets only. • Do not manually overwrite formulas in PMIS_Data. • Do not manually overwrite formulas in PMIS_Trade_Notes. • Use PMIS_Config when building names or sheet names change. • Use Data_Health to verify workbook readiness before reports or meetings.
Primary user paths | • COR / PM: start at V4_Mission_Control. • Field / QC / Engineer: start at Command_Center. • Data audit: start at Data_Health. • Mapping maintenance: start at PMIS_Config.
Current architecture | Building Assessment Sheets → PMIS_Data + PMIS_Trade_Notes → Command_Center / V4_Mission_Control / Reports.
Today's Focus | Formula-fed priority worklist ranking buildings by shutdowns, open risks, open questions, and readiness gaps. Use it as the morning planning screen. | Command Center | PMIS_Data | PMIS_Trade_Notes | Data Health | Config

## V4_Mission_Control (hidden)
BEDFORD VA EHRM PMIS MISSION CONTROL V5 | [13 empty] | Last refresh | 2026-07-16 11:56 | SelectedIndex | SelectedSheet | SelectedBuilding
Mission Control rebuilt from live PMIS_Data + Building Assessment rollups. Select a building below; all cards update automatically. | [15 empty] | 1 | B01_Assessment | 01
OVERALL PROGRESS |  | BUILDINGS ASSESSED |  | OPEN RISKS |  | OPEN QUESTIONS |  | OPEN PHOTOS |  | ACTIVE SHUTDOWNS |  | NOT READY | NEXT ACTION
0.50667 |  | 30 |  | 0 |  | 0 |  | 0 |  | 0 |  | 29 | READY BUILDING
SELECT BUILDING |  |  |  | MISSION STATUS |  |  |  | PROGRESS OVERVIEW |  |  |  | NEXT REQUIRED ACTION
Building | 01
|  |  |  | Selected Building Readiness |  |  |  | Rooms | 29 | Fire Protection | Not Started | Action | READY BUILDING
50%
Assessment Sheet | B01_Assessment | [6 empty] | HVAC | Not Started | IT/Telecom | Not Started
[12 empty] | Why | No major exception detected.
Overall Status | Yellow |  |  | Decision |  |  |  | Electrical | Not Started
Continue assessment / monitoring
Construction Ready | No | [6 empty] | Telecom | Not Started
[12 empty] | Next Step | Maintain monitoring.
Open selected Building Assessment | [7 empty] | Fire Alarm | Not Started
RISK SUMMARY |  |  |  | OPEN QUESTIONS |  |  |  | DOCUMENTS / PHOTOS |  |  |  | SHUTDOWNS
Open Risks |  | 0 |  | Selected Open |  | 0 |  | Open Photos |  | 0 |  | Selected Active | 0
Campus Open |  | 0 |  | Campus Open |  | 0 |  | Campus Docs |  | 40 |  | Campus Active | 0
Selected Rank |  | 1 |  | High Priority |  | #REF! |  | Campus Photos |  | 1 |  | Not Ready | 29
SELECTED BUILDING DETAIL — LIVE FROM PMIS_Data
Building | Sheet | Status | Readiness | Ready | Rooms | Risks | Questions | Photos | Shutdowns
01 | B01_Assessment | Yellow | 50% | No | 29 | 0 | 0 | 0 | 0

## Dashboard (hidden)
BEDFORD VA EHRM PROGRAM DASHBOARD | [11 empty] | Mission | Command | Building | Risks | Data
GCC PMIS / Executive Status View | [15 empty] | EXECUTIVE COMMAND CENTER
PROJECT SNAPSHOT | [15 empty] | Open Risks
Project | 518-22-700 Bedford VA EHRM Infrastructure Upgrades |  | Current Phase | Procurement / Preconstruction |  | VA POC | Cameron Labbree |  | GCC POC | Brian Koches | [5 empty] | Open Actions
Contract Status | Pending Award |  | Prime Contractor | TBD |  | NTP Date | TBD |  | Dashboard Updated | 2026-07-16 | [5 empty] | Open Questions | 0
Current Building | Campus |  | Primary Tool | Building_View / Mini Digital Twin |  | Input Cell | Building_View!B4 |  | Mode | Owner Support | [5 empty] | Open Assumptions | 0
AT-A-GLANCE METRICS
#REF! |  | #REF! |  | #REF! |  | #REF! |  | Telecom Rooms 45 |  | Shutdowns 1 | [5 empty] | TOP RISKS
SELECTED BUILDING SUMMARY
Selected Building Campus |  | #REF! |  | #REF! |  | Telecom Rooms 0 |  | Building Docs 40 |  | Building Shutdowns 0
KEY OPEN QUESTIONS
TOP RISKS | [5 empty] | BUILDING SHUTDOWNS
Risk ID | Description | Building | Impact | Owner | Status | ID | System | Building | Scheduled | Status | Notes
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
OPEN QUESTIONS | [5 empty] | THIS WEEK / NEXT WEEK
Question ID | Question | Why It Matters | Owner | Priority | Status | Period | Objective | Owner | Status | Notes
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | This Week | Use Building_View to validate building records | Paul | In Progress | B4 controls selected building
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | This Week | Track active Building 62 shutdown | Paul | In Progress | Confirm stakeholders and scheduled date
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | This Week | Keep source tabs normalized | Paul | Open | Building values must match B4 values
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Next Week | Add verified existing conditions | Paul | Open | Only add useful field observations
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Next Week | Align reporting expectations | GCC | Open | Avoid duplicate reporting systems
DASHBOARD NOTES
Dashboard is formula-driven and reads from existing PMIS source tabs. It does not replace Building_View; it summarizes the overall project and selected building. To change the selected building, update Building_View!B4.
If a dashboard section appears blank, the matching source register likely has no records for the selected building yet.
NOTE: PMIS_Home is now the combined Dashboard + Building View + Command Center sheet. This tab is retained for legacy reference.

## Building_View (hidden)
BUILDING VIEW / MINI DIGITAL TWIN | [11 empty] | Mission | Command | Building | Risks | Data
Enter a building number or area and return risks, actions, existing conditions, telecom rooms, documents, photos, shutdowns, and stakeholders.
Enter Building / Area | Campus |  | B4 controls the lookup. Pick Campus to see project-wide items. Pick a building number for building-specific rooms/records. Blank sections mean source tabs have no matching rows yet.
BUILDING SNAPSHOT
Building | Campus | Open Risks | #REF! | Open Actions | #REF!
Existing Conditions | 0 | Telecom Rooms | 0 | Documents | 40
Photos | #REF! | Shutdowns | 0 | Stakeholders | 3
RISKS
Risk ID | Description | Building | System | Probability | Impact | Risk Score | Mitigation | Owner | Status | Notes | Related Doc
OPEN ACTIONS
Action ID | Date | Action Item | Building | System | Assigned To | Due Date | Priority | Status | Notes
EXISTING CONDITIONS
Building | Room / Area | Existing Condition | Deficiency | Photo Ref | Potential Impact | Verified By | Date
TELECOM ROOMS
Building | Room | TR/IDF/MDF | Rack Capacity | Power | Cooling | Access | Readiness | Notes
DOCUMENTS
Doc ID | File / Document | Discipline | Sheet No | Title | Revision | Date | Building | System | Keywords | Link / Path
DOC-001 | 00 41 13.10 - Construction Estimate Breakdown Template.pdf | 0 | 0 | 00 41 13.10 - Construction Estimate Breakdown Template.pdf | 0 | 0 | Campus | 0 | 0 | Plans\00 41 13.10 - Construction Estimate Breakdown Template.pdf
DOC-002 | 01 00 00.B - Appendix B - Submittal Log.pdf | Submittals | 0 | 01 00 00.B - Appendix B - Submittal Log.pdf | 0 | 0 | Campus | Project Controls | submittal, log | Plans\01 00 00.B - Appendix B - Submittal Log.pdf
DOC-003 | 01 00 00.C - Appendix C - VHA ICRA-1.3 (Dec 9 2024).pdf | Safety / Infection Control | 0 | 01 00 00.C - Appendix C - VHA ICRA-1.3 (Dec 9 2024).pdf | 0 | 0 | Campus | ICRA | ICRA, infection control, safety | Plans\01 00 00.C - Appendix C - VHA ICRA-1.3 (Dec 9 2024).pdf
DOC-004 | 01 00 00.D - Appendix D - VHA PCRA 2024 1.1 Final.Template Fillable.pdf | Safety / Risk | 0 | 01 00 00.D - Appendix D - VHA PCRA 2024 1.1 Final.Template Fillable.pdf | 0 | 0 | Campus | PCRA | PCRA, safety, risk | Plans\01 00 00.D - Appendix D - VHA PCRA 2024 1.1 Final.Template Fillable.pdf
DOC-005 | 01 00 00.E - Appendix E - J2247012 Bedford MA VAMC ACM Inspection LCP Testing Report Final 11-20-2024 - signed-unlocked.pdf | Hazardous Materials | 0 | 01 00 00.E - Appendix E - J2247012 Bedford MA VAMC ACM Inspection LCP Testing Report Final 11-20-2024 - signed-unlocked.pdf | 0 | 0 | Campus | ACM / LCP | asbestos, lead, hazardous material | Plans\01 00 00.E - Appendix E - J2247012 Bedford MA VAMC ACM Inspection LCP Testing Report Final 11-20-2024 - signed-unlocked.pdf
PHOTOS
Photo ID | Date | Building | Location | Description | File Name | Linked Ref
SHUTDOWNS
Shutdown ID | System | Building | Requested Date | Approved Date | Scheduled Date | Duration | Stakeholders Notified | Status | Notes
STAKEHOLDERS
Building | Name | Organization | Role | Phone | Email | Authority / Influence | Notes
Campus | Cameron Labbree | VA Bedford | Healthcare Engineer / Primary VA POC | 0 | 0 | Primary daily VA contact | 0
Campus | Brian Koches | GCC | Sr. Vice President / Primary GCC POC | 0 | 0 | GCC primary contact | 0
Campus | Paul Thibodeau | GCC | Construction Quality Inspector | 0 | 0 | Field support / project intelligence | 0
HOW TO USE
1. Enter a building value in B4.
2. Use the same value in the Building column of each source register.
3. This view returns up to five matching rows per section using Excel-compatible formulas.
4. For campus-wide items, use Campus as the Building value.
5. This is a project intelligence view, not an official contract deliverable.
SOURCE DATA NOTE
If a section is blank, that source tab has no matching Building value yet.
Campus-wide records use Building = Campus.
Building-specific records use the exact building value, such as 1, 2, 80, or MCR/DC.

## Command_Center
BEDFORD VA EHRM — CAMPUS COMMAND STATUS | [15 empty] | Last refresh | 2026-07-16 11:56 | SelectedIndex | SelectedSheet | SelectedBuilding
| MISSION STATUS: AT RISK ██████████░░░░░░░░░░ 51% | [16 empty] | 22 | B61_Assessment | 61
SELECTED BUILDING SOURCE DETAIL — ASSESSMENT SHEETS
B01 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B02 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B03 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B04 50% █████░░░░░ ⚠ 0 ❓ 0
B05 55% ██████░░░░ ⚠ 0 ❓ 0 |  |  |  | B06 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B07 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B08 50% █████░░░░░ ⚠ 0 ❓ 0
B09 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B10 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B12 60% ██████░░░░ ⚠ 0 ❓ 0 |  |  |  | B13 50% █████░░░░░ ⚠ 0 ❓ 0
B14 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B15 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B16 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B17 50% █████░░░░░ ⚠ 0 ❓ 0
B18 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B20 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B21 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B22 50% █████░░░░░ ⚠ 0 ❓ 0
B33 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B61 55% ██████░░░░ ⚠ 0 ❓ 0 PILOT |  |  |  | B62 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B70 50% █████░░░░░ ⚠ 0 ❓ 0
B78 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B80 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B82 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | BCH 50% █████░░░░░ ⚠ 0 ❓ 0
MCR 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | SITE 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | SPEC 0% ░░░░░░░░░░ ⚠ - ❓ - | [6 empty] | QA | Data Health
[15 empty] | Guide | Architecture
| CAMPUS HEALTH |  | BUILDINGS ASSESSED |  | OPEN RISKS |  | OPEN QUESTIONS |  | OPEN PHOTOS |  | ACTIVE SHUTDOWNS |  | NOT READY |  | Focus | Today's Focus
| 50.67% |  | 30 |  | 0 |  | 0 |  | 0 |  | 0 |  | 29
| ACTIVE MISSION | [7 empty] | PROGRESS OVERVIEW
| MISSION TARGET | 61 |  |  | READINESS SIGNAL
| SELECTED ASSET | Building 61 |  |  | BAR | ███████░░░░░ |  |  | ROOMS 29 |  | FIRE Not Started
| MISSION STATUS | AT RISK |  |  | 55%
| ASSESSMENT SHEET | B61_Assessment
[9 empty] | HVAC Not Started |  | ELECTRICAL Not Started
| OVERALL STATUS | PILOT PHASE
| CONSTRUCTION READY | YES | [6 empty] | TELECOM Not Started |  | SECURITY Not Started
| RISK SUMMARY |  |  |  | OPEN QUESTIONS |  |  |  | DOCUMENTS / PHOTOS |  |  |  | SHUTDOWNS
| Open Risks |  | 0 |  | Selected Open |  | 0 |  | Open Photos |  | 0 |  | Selected Active | 0
| Campus Open |  | 0 |  | Campus Open |  | 0 |  | Campus Docs |  | 40 |  | Campus Active | 0
| Selected Rank |  | 30 |  | High Priority |  | #REF! |  | Campus Photos |  | 1 |  | Not Ready | 29
SELECTED BUILDING DETAIL — LIVE FROM PMIS_Data
Open selected Building Assessment
Building | Sheet | Status | Readiness | Ready | Rooms | Risks | Questions | Photos | Shutdowns | Pilot Gate | Open Gates
61 | B61_Assessment | PILOT PHASE | 0.55 | YES | 29 | 0 | 0 | 0 | 0 | 0% | 0 | [7 empty] | Selected_Assessment_Sheet | • Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. • Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. • Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. • Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | • Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. • Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. • Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. • Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | • Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. • Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. • Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. • Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | • 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. • 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. • 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. • 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service. | • Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. • Verify TR door hardware and access control, CCTV camera, network door controller and integration. • Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. • Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | • High: Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • High: Hazardous material abatement plans exist for first and second levels — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation • Critical: Existing server/demarc equipment may remain active during cutover — Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path • Critical: Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified — Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements • High: Large cable tray scope creates coordination and firestop risk — Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies
Selected Building | Selected Sheet | Payment Confidence | Payment Decision | OIT Readiness | OIT Status | OIT Blocker | Material Compliance | Productivity | Acceptance Readiness | Owner Decision | Signal | [6 empty] | Selected_Display_Label
61 | B61_Assessment | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 0% | 0% | 0% | Resolve OIT Blocker | 🔴 ATTENTION | [6 empty] | 61
B61_Assessment
BUILDING MISSION MODULES — CLICK TILE TO OPEN ASSESSMENT | [5 empty] | B61 |  | Use the selector to refresh the Command Center. Tiles are hyperlinks to source assessment sheets.
SELECTED BUILDING WORKSPACE — B61 OPERATIONAL PICTURE
🏢 BUILDING B61 Status: PILOT PHASE Readiness: 55% Construction Ready: YES Rooms Captured: 29 |  |  |  | ⚠ CURRENT BLOCKERS Open Risks: 0 Open Questions: 0 Major Blocker: Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. |  |  |  | 📷 FIELD CAPTURE Open Photo Items: 0 HVAC: Not Started Electrical: Not Started Telecom: Not Started |  |  |  | ✅ NEXT REQUIRED ACTION Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence. Source: B61_Assessment
MISSION FEED — NEXT ACTIONS / RELEASE POSTURE
🏢 B61 Mission Feed • Next Action: Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence. • Major Blocker: Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. • Risks/RFIs/Photos: 0 / 0 / 0
TRADE SECTION CARDS — SELECTED BUILDING NOTES
🔥 FIRE / LIFE SAFETY • Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. • Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. • Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. • Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | [7 empty] | ❄ HVAC / COOLING • Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. • Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. • Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. • Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected.
⚡ ELECTRICAL / UPS • Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. • Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. • Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. • Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | [7 empty] | 📡 TELECOM / FIBER • 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. • 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. • 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. • 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service.
🔐 SECURITY / PACS / CCTV • Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. • Verify TR door hardware and access control, CCTV camera, network door controller and integration. • Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. • Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | [7 empty] | ❓ RISKS / OPEN QUESTIONS Owner Risks: • High: Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • High: Hazardous material abatement plans exist for first and second levels — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation • Critical: Existing server/demarc equipment may remain active during cutover — Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path • Critical: Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified — Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements • High: Large cable tray scope creates coordination and firestop risk — Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies Open Questions:
SOURCE OF TRUTH: Building assessment sheets remain authoritative. The Command Center reads from PMIS_Data, _Command_Card_Index, and _Assessment_Full_View.
SELECTED BUILDING SOURCE DETAIL — FIRST 25 ASSESSMENT ROWS (HIDDEN)
Section |  | Room / Area |  | Item / System |  |  | Impact / Detail |  |  | Status / Owner |  |  | Notes
1. ROOM INVENTORY |  | 1. ROOM INVENTORY / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
1. ROOM INVENTORY |  | Building / Room |  | Floor / Existing Use |  |  | New Use / Rack Count |  |  | Drawing Ref |  |  | Notes
1. ROOM INVENTORY |  | 61 / B13H-A |  | Basement / Basement telecom / support area |  |  | Telecom Room / 1 |  |  | 61A-400 / 61E-401 / 61T-100 / 61T-401 / 61T-604 / 61T-701 |  |  | Basement TR identified as RM B13H-A with Rack ID TR01-B13H-A-1. Schedules identify 88 WAO total, 74 active ports, 129 scheduled ports, 142 ports with 10% allowance. Electrical panels include B61-TRB13A/B. Mechanical cooling includes IU-0-01/CU-0-01.
1. ROOM INVENTORY |  | 61 / 124 |  | First / First-level telecom area |  |  | Telecom Room / 1 |  |  | 61A-400 / 61E-402 / 61T-101 / 61T-401 / 61T-604 / 61T-701 |  |  | First-level TR identified as Room 124 / Rack ID TR01-124-1. Electrical panels include B61-TR124A/B. Mechanical cooling includes IU-1-01/CU-1-01. Verify room naming against electrical schedule references that also call out RM137B rack receptacles.
1. ROOM INVENTORY |  | 61 / 226 |  | Second / Second-level telecom area |  |  | Telecom Room / 1 |  |  | 61A-401 / 61E-402 / 61T-102 / 61T-401 / 61T-605 / 61T-702 |  |  | Second-level TR identified as Room 226 / Rack ID TR01-226-1. Schedules identify 109 WAO total, 126 active ports, 156 scheduled ports, 172 ports with 10% allowance. Electrical panels include B61-TR226A/B. Mechanical cooling includes IU-2-01/CU-2-01.
1. ROOM INVENTORY |  | 61 / 137 / 137A |  | First / Existing server/demarc/telecom equipment rooms |  |  | Existing demarc / server transition point / 11 |  |  | 61T-402 / 61T-606 / 61T-607 / 61R-900 |  |  | Existing Room 137/137A rack inventory and demarc/server equipment include existing 4-post racks, PACS/equipment racks, APC UPS/PDU equipment, Fujitsu FLM equipment, wall-mounted patch panels, and local elevations. Protect active services and verify what remains, transfers, or is modified.
1. ROOM INVENTORY |  | 0 / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
2. ROOM READINESS |  | 2. ROOM READINESS / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
2. ROOM READINESS |  | Room / Walls / 1-hr Rating |  | Ceiling / Floor / SDC |  |  | Penetrations / Access Control |  |  | Overall |  |  | Comments
2. ROOM READINESS |  | B13H-A / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Basement TR; verify rated walls/open-to-deck conditions, door/security, floor finish, ladder rack/cable tray, future rack clearance, wall backing, and pathway entries.
2. ROOM READINESS |  | 124 / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | First-level TR; verify rated construction, door hardware, ceiling/deck, rack/future rack clearances, wall backing, and riser/pathway entries.
2. ROOM READINESS |  | 226 / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Second-level TR; verify rated construction, door hardware, ceiling/deck, rack/future rack clearances, wall backing, and riser/pathway entries.
2. ROOM READINESS |  | 137 / 137A / Existing / Verify |  | Existing / Verify / Existing / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Existing demarc/server rooms; verify existing rack inventory, operational continuity, active circuits, access control, airflow and protection-in-place.
2. ROOM READINESS |  | 0 / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
3. FIRE PROTECTION |  | 3. FIRE PROTECTION / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
3. FIRE PROTECTION |  | Room / Sprinkler |  | Cage / Detector |  |  | Horn/Strobe / Extinguisher <75 ft |  |  | Overall |  |  | Risk / Notes
3. FIRE PROTECTION |  | B13H-A / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping.
3. FIRE PROTECTION |  | 124 / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems.
3. FIRE PROTECTION |  | 226 / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping.
3. FIRE PROTECTION |  | 137 / 137A / Verify |  | N/A / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work.
3. FIRE PROTECTION |  | 0 / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
4. HVAC / COOLING |  | 4. HVAC / COOLING / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
4. HVAC / COOLING |  | Room / Dedicated Unit |  | Capacity Verified / Emergency Power |  |  | Controls / BACnet / Condensate Routed |  |  | Overall |  |  | Risk / Notes
4. HVAC / COOLING |  | B13H-A / IU-0-01 / CU-0-01 |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms.
4. HVAC / COOLING |  | 124 / IU-1-01 / CU-1-01 |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm.

## COMMAND CENTERS (hidden)
BEDFORD VA EHRM — CAMPUS COMMAND STATUS | [15 empty] | Last refresh | 2026-07-16 11:56 | SelectedIndex | SelectedSheet | SelectedBuilding
| MISSION STATUS: AT RISK ██████████░░░░░░░░░░ 51% | [16 empty] | 22 | B61_Assessment | 61
SELECTED BUILDING SOURCE DETAIL — ASSESSMENT SHEETS
B01 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B02 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B03 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B04 50% █████░░░░░ ⚠ 0 ❓ 0
B05 55% ██████░░░░ ⚠ 0 ❓ 0 |  |  |  | B06 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B07 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B08 50% █████░░░░░ ⚠ 0 ❓ 0
B09 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B10 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B12 60% ██████░░░░ ⚠ 0 ❓ 0 |  |  |  | B13 50% █████░░░░░ ⚠ 0 ❓ 0
B14 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B15 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B16 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B17 50% █████░░░░░ ⚠ 0 ❓ 0
B18 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B20 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B21 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B22 50% █████░░░░░ ⚠ 0 ❓ 0
B33 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B61 55% ██████░░░░ ⚠ 0 ❓ 0 PILOT |  |  |  | B62 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B70 50% █████░░░░░ ⚠ 0 ❓ 0
B78 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B80 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | B82 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | BCH 50% █████░░░░░ ⚠ 0 ❓ 0
MCR 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | SITE 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | SPEC 0% ░░░░░░░░░░ ⚠ - ❓ - | [6 empty] | QA | Data Health
[15 empty] | Guide | Architecture
| CAMPUS HEALTH |  | BUILDINGS ASSESSED |  | OPEN RISKS |  | OPEN QUESTIONS |  | OPEN PHOTOS |  | ACTIVE SHUTDOWNS |  | NOT READY |  | Focus | Today's Focus
| 50.67% |  | 30 |  | 0 |  | 0 |  | 0 |  | 0 |  | 29
| ACTIVE MISSION | [7 empty] | PROGRESS OVERVIEW
| MISSION TARGET | 61 |  |  | READINESS SIGNAL
[5 empty] | BAR | ███████░░░░░ |  |  | ROOMS 29 |  | FIRE Not Started
| MISSION STATUS | AT RISK |  |  | 55%
[9 empty] | HVAC Not Started |  | ELECTRICAL Not Started
| OVERALL STATUS | PILOT PHASE
| CONSTRUCTION READY | YES | [6 empty] | TELECOM Not Started |  | SECURITY Not Started
| RISK SUMMARY |  |  |  | OPEN QUESTIONS |  |  |  | DOCUMENTS / PHOTOS |  |  |  | SHUTDOWNS
| Open Risks |  | 0 |  | Selected Open |  | 0 |  | Open Photos |  | 0 |  | Selected Active | 0
| Campus Open |  | 0 |  | Campus Open |  | 0 |  | Campus Docs |  | 40 |  | Campus Active | 0
| Selected Rank |  | 29 |  | High Priority |  | #REF! |  | Campus Photos |  | 1 |  | Not Ready | 29
Open selected Building Assessment
Building | Sheet | Status | Readiness | Ready | Rooms | Risks | Questions | Photos | Shutdowns
61 | B61_Assessment | PILOT PHASE | 0.55 | YES | 29 | 0 | 0 | 0 | 0 | [9 empty] | Selected_Assessment_Sheet | • Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. • Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. • Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. • Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | • Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. • Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. • Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. • Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | • Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. • Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. • Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. • Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | • 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. • 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. • 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. • 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service. | 0 | • High: Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • High: Hazardous material abatement plans exist for first and second levels — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation • Critical: Existing server/demarc equipment may remain active during cutover — Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path • Critical: Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified — Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements • High: Large cable tray scope creates coordination and firestop risk — Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | • B61-Q1 — Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? [Open] Impact: Room inventory could miss scope • B61-Q2 — What active services and circuits are currently housed in Room 137/137A? [Open] Impact: Potential outage/cutover risk • B61-Q3 — Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? [Open] Impact: Electrical PMIS mapping risk • B61-Q4 — Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? [Open] Impact: Cooling continuity unclear • B61-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B61-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown
Selected Building | Selected Sheet | Payment Confidence | Payment Decision | OIT Readiness | OIT Status | OIT Blocker | Material Compliance | Productivity | Acceptance Readiness | Owner Decision | Signal | [6 empty] | Selected_Display_Label
61 | B61_Assessment | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 0% | 0% | 0% | Resolve OIT Blocker | 🔴 ATTENTION | [6 empty] | 61
B61_Assessment
BUILDING MISSION MODULES — CLICK TILE TO OPEN ASSESSMENT | [5 empty] | B61 |  | Use the selector to refresh the Command Center. Tiles are hyperlinks to source assessment sheets.
SELECTED BUILDING WORKSPACE — B61 OPERATIONAL PICTURE
🏢 BUILDING B61 Status: PILOT PHASE Readiness: 55% Construction Ready: YES Rooms Captured: 29 |  |  |  | ⚠ CURRENT BLOCKERS Open Risks: 0 Open Questions: 0 Major Blocker: Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. |  |  |  | 📷 FIELD CAPTURE Open Photo Items: 0 HVAC: Not Started Electrical: Not Started Telecom: Not Started |  |  |  | ✅ NEXT REQUIRED ACTION Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence. Source: B61_Assessment
MISSION FEED — NEXT ACTIONS / RELEASE POSTURE
🏢 B61 Mission Feed • Next Action: Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence. • Major Blocker: Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. • Risks/RFIs/Photos: 0 / 0 / 0
TRADE SECTION CARDS — SELECTED BUILDING NOTES
🔥 FIRE / LIFE SAFETY • Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. • Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. • Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. • Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | [7 empty] | ❄ HVAC / COOLING • Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. • Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. • Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. • Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected.
⚡ ELECTRICAL / UPS • Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. • Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. • Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. • Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | [7 empty] | 📡 TELECOM / FIBER • 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. • 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. • 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. • 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service.
🔐 SECURITY / PACS / CCTV • Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. • Verify TR door hardware and access control, CCTV camera, network door controller and integration. • Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. • Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | [7 empty] | ❓ RISKS / OPEN QUESTIONS Owner Risks: • High: Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • High: Hazardous material abatement plans exist for first and second levels — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation • Critical: Existing server/demarc equipment may remain active during cutover — Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path • Critical: Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified — Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements • High: Large cable tray scope creates coordination and firestop risk — Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies Open Questions: • B61-Q1 — Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? [Open] Impact: Room inventory could miss scope • B61-Q2 — What active services and circuits are currently housed in Room 137/137A? [Open] Impact: Potential outage/cutover risk • B61-Q3 — Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? [Open] Impact: Electrical PMIS mapping risk • B61-Q4 — Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? [Open] Impact: Cooling continuity unclear • B61-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B61-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown
SOURCE OF TRUTH: Building assessment sheets remain authoritative. The Command Center reads from PMIS_Data, _Command_Card_Index, and _Assessment_Full_View.
SELECTED BUILDING SOURCE DETAIL — FIRST 25 ASSESSMENT ROWS (HIDDEN)
Section |  | Room / Area |  | Item / System |  |  | Impact / Detail |  |  | Status / Owner |  |  | Notes
1. ROOM INVENTORY |  | 1. ROOM INVENTORY / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
1. ROOM INVENTORY |  | Building / Room |  | Floor / Existing Use |  |  | New Use / Rack Count |  |  | Drawing Ref |  |  | Notes
1. ROOM INVENTORY |  | 61 / B13H-A |  | Basement / Basement telecom / support area |  |  | Telecom Room / 1 |  |  | 61A-400 / 61E-401 / 61T-100 / 61T-401 / 61T-604 / 61T-701 |  |  | Basement TR identified as RM B13H-A with Rack ID TR01-B13H-A-1. Schedules identify 88 WAO total, 74 active ports, 129 scheduled ports, 142 ports with 10% allowance. Electrical panels include B61-TRB13A/B. Mechanical cooling includes IU-0-01/CU-0-01.
1. ROOM INVENTORY |  | 61 / 124 |  | First / First-level telecom area |  |  | Telecom Room / 1 |  |  | 61A-400 / 61E-402 / 61T-101 / 61T-401 / 61T-604 / 61T-701 |  |  | First-level TR identified as Room 124 / Rack ID TR01-124-1. Electrical panels include B61-TR124A/B. Mechanical cooling includes IU-1-01/CU-1-01. Verify room naming against electrical schedule references that also call out RM137B rack receptacles.
1. ROOM INVENTORY |  | 61 / 226 |  | Second / Second-level telecom area |  |  | Telecom Room / 1 |  |  | 61A-401 / 61E-402 / 61T-102 / 61T-401 / 61T-605 / 61T-702 |  |  | Second-level TR identified as Room 226 / Rack ID TR01-226-1. Schedules identify 109 WAO total, 126 active ports, 156 scheduled ports, 172 ports with 10% allowance. Electrical panels include B61-TR226A/B. Mechanical cooling includes IU-2-01/CU-2-01.
1. ROOM INVENTORY |  | 61 / 137 / 137A |  | First / Existing server/demarc/telecom equipment rooms |  |  | Existing demarc / server transition point / 11 |  |  | 61T-402 / 61T-606 / 61T-607 / 61R-900 |  |  | Existing Room 137/137A rack inventory and demarc/server equipment include existing 4-post racks, PACS/equipment racks, APC UPS/PDU equipment, Fujitsu FLM equipment, wall-mounted patch panels, and local elevations. Protect active services and verify what remains, transfers, or is modified.
1. ROOM INVENTORY |  | 0 / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
2. ROOM READINESS |  | 2. ROOM READINESS / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
2. ROOM READINESS |  | Room / Walls / 1-hr Rating |  | Ceiling / Floor / SDC |  |  | Penetrations / Access Control |  |  | Overall |  |  | Comments
2. ROOM READINESS |  | B13H-A / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Basement TR; verify rated walls/open-to-deck conditions, door/security, floor finish, ladder rack/cable tray, future rack clearance, wall backing, and pathway entries.
2. ROOM READINESS |  | 124 / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | First-level TR; verify rated construction, door hardware, ceiling/deck, rack/future rack clearances, wall backing, and riser/pathway entries.
2. ROOM READINESS |  | 226 / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Second-level TR; verify rated construction, door hardware, ceiling/deck, rack/future rack clearances, wall backing, and riser/pathway entries.
2. ROOM READINESS |  | 137 / 137A / Existing / Verify |  | Existing / Verify / Existing / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Existing demarc/server rooms; verify existing rack inventory, operational continuity, active circuits, access control, airflow and protection-in-place.
2. ROOM READINESS |  | 0 / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
3. FIRE PROTECTION |  | 3. FIRE PROTECTION / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
3. FIRE PROTECTION |  | Room / Sprinkler |  | Cage / Detector |  |  | Horn/Strobe / Extinguisher <75 ft |  |  | Overall |  |  | Risk / Notes
3. FIRE PROTECTION |  | B13H-A / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping.
3. FIRE PROTECTION |  | 124 / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems.
3. FIRE PROTECTION |  | 226 / Verify |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping.
3. FIRE PROTECTION |  | 137 / 137A / Verify |  | N/A / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work.
3. FIRE PROTECTION |  | 0 / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
4. HVAC / COOLING |  | 4. HVAC / COOLING / 0 |  | 0 / 0 |  |  | 0 / 0 |  |  | 0 |  |  | 0
4. HVAC / COOLING |  | Room / Dedicated Unit |  | Capacity Verified / Emergency Power |  |  | Controls / BACnet / Condensate Routed |  |  | Overall |  |  | Risk / Notes
4. HVAC / COOLING |  | B13H-A / IU-0-01 / CU-0-01 |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms.
4. HVAC / COOLING |  | 124 / IU-1-01 / CU-1-01 |  | Verify / Verify |  |  | Verify / Verify |  |  | Verify |  |  | Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm.

## Command_Tile_Copy_Block (hidden)
COPY-READY COMMAND CENTER BUILDING TILE BLOCK
Copy A3:P10 from this sheet and paste over Command_Center!A3:P10. Formulas use ⚠ for risks and ❓ for questions; tile fill is conditional on PMIS_Data readiness.
B01 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B02 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B03 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B04 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN
B05 55% ██████░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B06 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B07 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B08 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN
B09 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B10 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B12 60% ██████░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B13 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN
B14 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B15 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B16 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B17 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN
B18 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B20 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B21 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B22 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN
B33 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B61 55% ██████░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B62 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B70 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN
B78 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B80 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | B82 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | BCH 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN
MCR 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | SITE 50% █████░░░░░ ⚠ 0 ❓ 0 ↗ OPEN | SPEC 0% ░░░░░░░░░░ ⚠ - ❓ - ↗ OPEN

## Executive Brief (hidden)
BEDFORD VA EHRM |  |  |  | BEDFORD VA EHRM PROGRAM | [18 empty] | 2026-07-16
|  |  |  | COMMAND CENTER – EXECUTIVE BRIEF | [18 empty] | Thursday
One Campus. One Plan. One Standard.
CAMPUS READINESS |  |  |  |  | BUILDINGS ASSESSED |  |  |  |  | CONSTRUCTION READY |  |  |  |  | OPEN QUESTIONS |  |  |  |  | OPEN RISKS |  |  |  | SHUTDOWNS
| 50.67% |  |  |  |  | 30 |  |  |  |  | 1 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  | 0
| Overall Average |  |  |  |  | Assessment Sheets |  |  |  |  | 29 Not Ready |  |  |  |  | Campus Total |  |  |  |  | Campus Total |  |  |  | Active
ACTIVE BUILDING | [8 empty] | TRADE READINESS – BUILDING 61 | [9 empty] | MISSION INTELLIGENCE – BUILDING 61
BUILDING PHOTO PLACEHOLDER |  |  |  | 61 |  |  |  |  | TRADE | [5 empty] | STATUS |  | TREND
[19 empty] | Open Questions |  |  |  |  | 0
[9 empty] | Fire Protection |  |  |  |  | FIRE Not Started |  |  | ↗
[19 empty] | Open Risks |  |  |  |  | 0
[9 empty] | HVAC |  |  |  |  | HVAC Not Started |  |  | ↗
[19 empty] | Open Photos |  |  |  |  | 0
|  |  |  | READINESS SCORE 55% |  |  |  |  | Electrical |  |  |  |  | ELECTRICAL Not Started |  |  | ↗
[19 empty] | Active Shutdowns |  |  |  |  | Selected Active
[9 empty] | Telecom / IT |  |  |  |  | TELECOM Not Started |  |  | ↗
[19 empty] | Campus Questions |  |  |  |  | 0
[9 empty] | Security |  |  |  |  | SECURITY Not Started |  |  | ↗
[19 empty] | Campus Risks |  |  |  |  | 0
Assessment Sheet: B61_Assessment
Selected Status: PILOT PHASE
[5 empty] | PAYMENT CONFIDENCE |  | PAYMENT DECISION |  |  | OIT READINESS | OIT STATUS | OIT BLOCKERS |  | MATERIAL COMPLIANCE | PRODUCTIVITY | ACCEPTANCE READINESS |  | OWNER DECISION
[5 empty] | 0% |  | Withhold / Review |  |  | 0% | Blocked | No blocker documented |  | 0% | 0% | 0% |  | Resolve OIT Blocker
0
51% campus readiness across 30 assessed buildings. 0 open risks, 0 open questions, and 0 active shutdowns are currently tracked. Active mission is Building 61 (Building 61), readiness 55%.
❓ RISKS / OPEN QUESTIONS Owner Risks: • High: Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • High: Hazardous material abatement plans exist for first and second levels — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation • Critical: Existing server/demarc equipment may remain active during cutover — Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path • Critical: Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified — Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements • High: Large cable tray scope creates coordination and firestop risk — Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies Open Questions:
CAMPUS BUILDING STATUS MAP | [22 empty] | READINESS LEGEND
B01 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B02 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B03 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B04 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B05 55% ██████░░░░ ⚠ 0 ❓ 0 |  |  | B06 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B07 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B08 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | 80% or Greater
B09 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B10 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B12 60% ██████░░░░ ⚠ 0 ❓ 0 |  |  | B13 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B14 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B15 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B16 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B17 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | 60%–79%
B18 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B20 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B21 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B22 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B33 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B61 55% ██████░░░░ ⚠ 0 ❓ 0 PILOT |  |  | B62 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B70 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  |  | 40%–59%
B78 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B80 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | B82 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | BCH 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | MCR 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | SITE 50% █████░░░░░ ⚠ 0 ❓ 0 |  |  | SPEC 0% ░░░░░░░░░░ ⚠ - ❓ - |  |  | 0 |  |  |  | Less than 40%
PILOT BUILDING DECISION MATRIX │ B61 vs B08 | [9 empty] | PILOT EXIT CRITERIA
Criteria | Weight | B61 Score | B61 Weighted | B08 Score | B08 Weighted | Preferred | Why it Matters | Source | Notes | Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal | Requirement | What it Means |  |  | Verification
Representative Complexity | 20 | 5 | 100 | 4 | 80 | B61 | Tests more of the actual campus work | Assessments |  | Approved Submittals | No |  |  |  |  | 🟡 |  | Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
Recoverability if Contractor Struggles | 15 | 4 | 60 | 5 | 75 | B08 | Pilot should not create MCR-level risk | Risk review |  | ICRA / PCRA | No |  |  |  |  | 🟡 |  | ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
Discipline Coverage | 15 | 5 | 75 | 3 | 45 | B61 | Must test fire/HVAC/electrical/telecom/security | Assessments |  | QA/QC Reports | No |  |  |  |  | 🟡 |  | QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Operational Risk | 15 | 3 | 45 | 4 | 60 | B08 | Lower operational risk is better for first work | Owner risk review |  | Firestopping | No |  |  |  |  | 🟡 |  | Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Documentation Burden | 10 | 5 | 50 | 3 | 30 | B61 | Tests whether documentation process works | PMIS |  | Cable Tests | No |  |  |  |  | 🟡 |  | Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
Cutover / OIT Learning Value | 10 | 5 | 50 | 3 | 30 | B61 | Pilot should prove the cutover process | OIT coordination |  | OIT Acceptance | No |  |  |  |  | 🟡 |  | OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Constructability / Access | 10 | 4 | 40 | 4 | 40 | Tie | Both likely workable | Field input |  | Photos | No |  |  |  |  | 🟡 |  | Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Owner Confidence Value | 5 | 5 | 25 | 3 | 15 | B61 | Bigger confidence return if successful | PMO judgment |  | Zero Critical Punch Items | No |  |  |  |  | 🟡 |  | Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
RESULT
B61 Total | 445 | B08 Total | 375 | Recommendation | B61
Recommendation Language
Use Building 61 as the preferred pilot because it is complex enough to prove contractor competency without exposing the project to MCR-level risk.
Controls Required | Pilot completion criteria must include approved submittals, ICRA/PCRA, QA/QC reports, firestopping, cable tests, OIT acceptance, photos, and zero critical punch items.

## Pilot
PILOT BUILDING DECISION MATRIX │ B61 vs B08
Purpose: select the first building used to prove contractor competency before authorizing wider campus rollout.
Criteria | Weight | B61 Score | B61 Weighted | B08 Score | B08 Weighted | Preferred | Why it Matters | Source | Notes
Representative Complexity | 20 | 5 | 100 | 4 | 80 | B61 | Tests more of the actual campus work | Assessments
Recoverability if Contractor Struggles | 15 | 4 | 60 | 5 | 75 | B08 | Pilot should not create MCR-level risk | Risk review
Discipline Coverage | 15 | 5 | 75 | 3 | 45 | B61 | Must test fire/HVAC/electrical/telecom/security | Assessments
Operational Risk | 15 | 3 | 45 | 4 | 60 | B08 | Lower operational risk is better for first work | Owner risk review
Documentation Burden | 10 | 5 | 50 | 3 | 30 | B61 | Tests whether documentation process works | PMIS
Cutover / OIT Learning Value | 10 | 5 | 50 | 3 | 30 | B61 | Pilot should prove the cutover process | OIT coordination
Constructability / Access | 10 | 4 | 40 | 4 | 40 | Tie | Both likely workable | Field input
Owner Confidence Value | 5 | 5 | 25 | 3 | 15 | B61 | Bigger confidence return if successful | PMO judgment
RESULT
B61 Total | 445 | B08 Total | 375 | Recommendation | B61
Use Building 61 as the preferred pilot because it is complex enough to prove contractor competency without exposing the project to MCR-level risk.
Controls Required | Pilot completion criteria must include approved submittals, ICRA/PCRA, QA/QC reports, firestopping, cable tests, OIT acceptance, photos, and zero critical punch items.
PILOT EXIT CRITERIA
Gate | Acceptance Criteria | Owner | Evidence Required | Status | Notes
1 | Existing conditions fully documented | GCC QA | Photos / room inventory | Open
2 | ICRA/PCRA and shutdown controls approved | VA / GCC | Permits / process documents | Open
3 | Install methods accepted | GCC / COR | Inspection reports / punch list | Open
4 | Cable testing accepted | OIT / Telecom | Copper/fiber test results | Open
5 | Firestop documentation accepted | GCC QA / COR | Before/during/after photos | Open
6 | Commissioning and turnover package complete | Cx / GCC | Cx reports / O&M / as-builts | Open
7 | Owner walkthrough complete | COR / VA | Acceptance signoff | Open
PILOT ACCEPTANCE GATE
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")

## Shutdown_Tracker (hidden)
SHUTDOWN TRACKER | [10 empty] | Mission | Command | Building | Risks | Data
Enter shutdowns here. Building_View pulls rows matching Building in column C.
Shutdown ID | System | Building | Requested Date | Approved Date | Scheduled Date | Duration | Stakeholders Notified | Status | Notes | Lookup #
62 | EQ | 62 | 2026-06-24 | 2026-06-25 | 2026-06-26 | 2 Hours | Paul Thibodeau Carroll, Kevin A. Tammelleo, Chadd D. Downes, Jennifer L. Filip, Joseph F. Lashomb, Kimberly R. Labbree, Cameron Oneil, Ellen M. Bradvica, Christina Cunneen, Edward M. Reagan, Stephen V. Boyden, John M. Range, Amy Honnellio, Anthony L. Mousseau, Kimberly A. Odiana, Edith U. | Pending | 06/22 Meeting with all Stake Holders

## Stakeholders (hidden)
STAKEHOLDER DIRECTORY
People, roles, authority, and contact map
Name | Organization | Role | Phone | Email | Authority / Decision Role | Notes
Cameron Labbree | VA Bedford | Healthcare Engineer & Lease Manager / Primary VA POC | 339-215-6829 | Cameron.Labbree@va.gov | VA POC / Owner-side coordination | Primary site contact; Building 80 Room 110
Josiah D. Curley | VA Bedford | Chief, Engineering Service | 781-687-3331 | josiah.curley@va.gov
Brian Koches | GCC | Sr. Vice President | 571-213-2287 | brian@gcc-llc.com | Primary GCC POC | Safety culture, communications, photos
Ali Khalaf | GCC | Director, Planning and Program Management | 949-293-2264 | ali@gcc-llc.com | GCC leadership / program management
Paul Thibodeau | GCC | Construction Quality Inspector | 724-320-4459 | paul.thibodeau@gcc-llc.com | Onsite GCC Inspector

## _Command_Lists (hidden)
Building Selector | Normalized
Campus | Campus
B01 | 01
B02 | 02
B03 | 03
B04 | 04
B05 | 05
B06 | 06
B07 | 07
B08 | 08
B09 | 09
B10 | 10
B12 | 12
B13 | 13
B14 | 14
B15 | 15
B16 | 16
B17 | 17
B18 | 18
B20 | 20
B21 | 21
B22 | 22
B33 | 33
B61 | 61
B62 | 62
B70 | 70
B78 | 78
B80 | 80
B82 | 82
BCH | BCH
MCR | MCR
SITE | SITE
SPEC | SPEC

## _PMIS_Config (hidden)
BEDFORD VA EHRM PMIS — CONFIGURATION / THEME SYSTEM
Central source for PMIS colors, icons, thresholds, navigation, validation lists, and status definitions.
Theme Token | Hex | Use | Notes | Spacer | Status | Icon | Sort
CommandBlue | #0F4C81 | Primary headers / mission bars | Executive command color |  | Ready | 🟩 | 1
ReadyTeal | #0F766E | Ready / complete state | Confirmed mission-ready modules |  | Active | 🟦 | 2
Amber | #D97706 | Watch / shutdown / pending | Action required / risk watch |  | Watch | 🟨 | 3
CriticalRed | #B91C1C | Critical exceptions | Immediate attention |  | Critical | 🟥 | 4
Slate | #4B5563 | Neutral inactive elements | Secondary labels |  | Not Started | ⬜ | 5
Canvas | #F3F6F9 | Dashboard background | Application canvas |  | Closed | ✅ | 6
Threshold | Value | Meaning | Applied To | Spacer | Icon | Meaning | Rule
ReadyPct | 0.9 | Ready / green | Readiness and mission modules |  | ⚠ | Open risk | Risk count > 0
WatchPct | 0.65 | Watch / amber | Readiness and mission modules |  | ❓ | Open question | Question count > 0
CriticalRisks | 7 | Critical / red | Open risks |  | 📷 | Photo/evidence action | Open photo count
ShutdownPresent | 1 | Shutdown / orange | Shutdown dependencies |  | ⚡ | Shutdown dependency | Shutdown count > 0
Navigation Label | Target Sheet | Formula Stub |  | Spacer | Validation List | Values
Mission Control | Mission_Control_v3.4 | #'Mission_Control_v3.4'!A1 |  |  | Status | Ready,Active,Watch,Critical,Not Started,Closed
Command Center | Command_Center | #'Command_Center'!A1 |  |  | Priority | Critical,High,Medium,Low
Building View | Building_View | #'Building_View'!A1 |  |  | Owner | VA,GCC,Oracle,OIT,Facilities,Utilities,Contractor,Paul
PMIS Data | PMIS_Data | #'PMIS_Data'!A1 |  |  | YesNo | Yes,No,TBD
Risk Register | Risk_Register | #'Risk_Register'!A1
Shutdowns | Shutdown_Tracker | #'Shutdown_Tracker'!A1
Maintenance Notes
1. Keep building assessment sheets as the source of truth.
2. Point dashboards at _PMIS_Helper / PMIS_Data instead of repeating long formulas.
3. Update colors, thresholds, and status definitions here first.
4. This sheet is hidden in the delivered workbook.

## Lookup_Lists (hidden)
LOOKUP LISTS
Controlled values for dropdowns and status tracking
Status | Priority | Probability | Impact | Phase | DATA VALIDATION LISTS
Open | Low | Low | Low | Procurement | Status | Yes/No/NA | QA Result
In Progress | Medium | Medium | Medium | Preconstruction | Not Started | Yes | Pending
Pending | High | High | High | Award | In Progress | No | Pass
Delayed | Critical |  | Critical | Mobilization | Complete | N/A | Fail
Closed |  |  |  | Construction | At Risk |  | N/A
Complete |  |  |  | Commissioning | Blocked
Not Started |  |  |  | Closeout
MEASURES OF SUCCESS
[5 empty] | Payment Confidence | Green ≥ 95% | Yellow 85–94%; Red <85%
[5 empty] | OIT Readiness | Green ≥ 90% | Yellow 70–89%; Red <70%
[5 empty] | QA Compliance | Green = 100% | Yellow 80–99%; Red <80%
[5 empty] | Contractor Performance | Green ≥ 100% | Yellow 80–99%; Red <80%
[5 empty] | Acceptance Readiness | Green = 100% | Yellow 80–99%; Red <80%
[5 empty] | Blocked Status | Always Red | Requires management attention

## System_Map (hidden)
PROJECT OPERATING SYSTEM MAP
How the workbook tabs relate to one another
Primary Relationship Model
The workbook is organized around a simple relational structure. Building_Register is the center of the project intelligence model. Risks, documents, telecom rooms, shutdowns, existing conditions, photos, open questions, and decisions should reference Building ID / Building Number whenever possible. This allows the Dashboard and Building_View tabs to summarize project intelligence by building, system, and status.
Core Tab | Purpose | Feeds / Supports
Building_Register | Master list of campus buildings and high-level scope | Building_View, Risk_Register, Documentation, Existing_Conditions, Telecom_Assessments
Doc_Register | Searchable index of drawings, narratives, specs, reports, and appendices | Building_View, Documentation, Weekly_Summary
Risk_Register | Project risk tracking by building/system/status | Dashboard, Risk_Heatmap, Weekly_Summary
Action_Log | Task/action tracking | Dashboard, Weekly_Summary
Open Questions | Discovery questions that need owner/GCC clarification | Dashboard, Weekly_Summary
Assumptions | Assumptions needing verification before becoming risks/issues | Dashboard, Risk_Register
Shutdown_Matrix | Defines approval/notification/recovery process by system | Shutdown_Tracker, Owner_Impact_Matrix
Project Intelligence | Informal observations and project learning | Lessons_Learned, Proposal_Language

## PMIS_Home (hidden)
BEDFORD VA EHRM PMIS │ EXECUTIVE HOME | [15 empty] | Data
Live management dashboard driven by standardized building assessment sheets. Edit building assessments → PMIS_Data maps the records → PMIS_Home rolls them up.
Selected Building / Area | Campus |  | Dashboard Updated | 2026-06-26 17:18 |  | Source Tables | 30 formula-fed assessments / 814 rooms / 66 risks / 231 questions |  |  | Mode | Owner PMIS / QA Controls
CAMPUS / SELECTED BUILDING KPIs
Assessments |  | Rooms / Areas |  | Avg Readiness |  | Construction Ready |  | Open Risks |  | Critical Risks |  | Open Questions |  | Open Photo Items
30 |  | 814 |  | 50.67% |  | 1 |  | 0 |  | 0 |  | 0 |  | 0
SELECTED BUILDING / AREA SNAPSHOT | [7 empty] | DISCIPLINE STATUS SUMMARY
Metric | Value | Metric | Value | Metric | Value | Notes |  | Discipline | Verify Items | Pass | Fail | Open Risk Hits | Notes
Overall Status | Campus Rollup | Sheet Readiness | 50.67% | Shutdowns | 0 |  |  | HVAC | 73 | 0 | 0 | 0 | Cooling / alarms / condensate / emergency power
Rooms / Scope | All mapped buildings, MCR, SITE, BCH, and TR packages. | [6 empty] | Electrical | 94 | 0 | 0 | 0 | Panels / UPS / PDU / SPD / load measurements
Major Blocker / Summary | Campus-wide concern: active-service protection, commissioning, site fiber, MCR activation, firestopping, and turnover documentation. | [6 empty] | Telecom | 84 | 0 | 0 | 0 | Racks / fiber / copper / labels / OIT acceptance
HVAC | 23 | Electrical | 26 | Telecom | 26 |  |  | Fire Protection | 86 | 0 | 0 | 0 | Sprinklers / FEC / clean agent / firestop
Fire Protection | 24 | Fire Alarm | 19 | Security | 20 |  |  | Security | 79 | 0 | 0 | 0 | PACS / cameras / VMS / door hardware
Open Questions | 0 | Open Risks | 0 | Open Photo Items | 0 |  |  | Site / Civil | 0 |  |  |  | Ductbank / utility locate / restoration
Construction Ready | 1 | Current Assessment Sheet | PMIS1_Data |  |  |  |  | Documentation | 0 |  |  |  | Photos / tests / reports / closeout
DATA HEALTH: B70 open-risk formula fixed; PMIS1_Data formulas are direct local sheet references; dashboard ranges patched to include all mapped risks/questions/photos.
LIVE DATA PATH: Building Assessment Sheets → PMIS1_Data formula staging layer → PMIS_Home dashboard. PMIS1_Data is not an input tab. Change the building sheets; the dashboard rolls up from them after Excel recalculation.
BUILDING / AREA HEATMAP — mapped from all standardized assessment sheets
Building | Sheet | Status | Readiness | Rooms | Risks | Questions | Photos | HVAC | Electrical | Telecom | FP | FA | Security | Shutdowns | Major Blocker / Focus
01 | B01_Assessment | Yellow | 50% | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify Room 107, existing B02, 138, and 282; confirm active services, existing rack/equipment transfer, B01-TR107A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 394 ft cable tray routes, and telecom cutover sequence. | 0
02 | B02_Assessment | Yellow | 50% | 30 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify new Rooms 141, 236, 342 and existing B-06/141/236; confirm active services, rack/equipment transfer, B02-TR141A/B, B02-TR236A/B, B02-TR342A/B panel sources, CU-1-01/CU-2-01/CU-3-01 cooling assignments, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, 2,560 ft cable tray routes, and telecom cutover sequence. | 0
03 | B03_Assessment | Yellow | 50% | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify Room 101E, existing Room 107, and existing DMARC Room 101C; confirm active services, existing rack/equipment transfer, B03-TR101CA/B panel sources, CU-01 cooling assignment, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 961 ft cable tray routes, Room 107 inventory, and telecom cutover/fiber transfer sequence. | 0
04 | B04_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify TR rooms B05, 141, and 244A; confirm cooling, panel/circuiting, fire alarm/sprinkler impacts, FEC locations, and cutover/phasing plan. | 0
05 | B05_Assessment | Yellow | 55% | 26 | 0 | 0 | 0 | N/A | Verify | Verify | N/A | Verify | Verify | Field verify Room 150 TE location, existing 153-A equipment to remain/transition, electrical source, UPS/PDU receptacles, PACS/CCTV requirements, firestopping, and cutover sequence. | 0
06 | B06_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify existing B-01 equipment, Rooms 178 and 233, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, and telecom cutover sequence. | 0
07 | B07_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify TR B-18 and 228A; confirm rack/equipment layout, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, and telecom cutover sequence. | 0
08 | B08_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify B-15, B12B, and 2065A; confirm active services, 2065A rack layout, panel/power source, IU/CU cooling, hazardous material/abatement impacts, FEC locations, PACS/CCTV, and telecom cutover sequence. | 0
09 | B09_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify B01, 104B, and 206A; confirm existing equipment and active services, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, and telecom cutover sequence. | 0
10 | B10_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify attic Telecom Room 200A, basement normal/emergency electrical source rooms B24/B25, existing wall-mounted rack/equipment, panel sources B10-TR200AA/AB, IU/CU-1-01 cooling, FEC/fire alarm/sprinkler impacts, hazardous/abatement scope, and telecom cutover plan. | 0
12 | B12_Assessment | Yellow | 60% | 26 | 0 | 0 | 0 | N/A | N/A / Verify | Verify | N/A / Verify | N/A / Verify | N/A / Verify | Field verify existing fiber pathway through Building 12, existing rack/demarc/serving closet condition, floor/wall penetrations, routing from basement/first/second level telecom plans, phasing/cutover approach, and test/label/as-built deliverables. | 0
13 | B13_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 124 and existing Tel Room 222; confirm active services, rack/equipment transfer, B13-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | 0
14 | B14_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 119 and existing basement Tel/F Panel B.01/B2; confirm active services, rack/equipment transfer, B14-TR119A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | 0
15 | B15_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 124A, existing Tel Room 222 and basement B01; confirm active services, rack/equipment transfer, B15-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | 0
16 | B16_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 015 and existing Room 014; confirm active services, rack/equipment transfer, B16-TR015A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, panel replacement/load measurement, and telecom cutover sequence. | 0
17 | B17_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 118, existing B35A, and Building 29 service path; confirm active services, B17-TR118A/B panel sources, BUS-B17-EQDP / BUS-B17-NPB1-R sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, hazardous material impacts, and cutover plan. | 0
18 | B18_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 110, existing TE 111B, existing Closet 213, and all active services; confirm B18-TR110A/B panel sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, lead-paint/hazardous impacts, and cutover plan. | 0
20 | B20_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Office 1B new TE location, existing Tel/Data Closet 8A, active services, TE01-1B-1 schedule, existing open TE cabinet, existing ground bar/patch panel/equipment box/indoor AC/backboard, 459 ft cable tray route, 10 Cat6A cross-connect cables, power/UPS/PDU source, and fiber Path A/B cutover. | 0
21 | B21_Assessment | Yellow | 50% | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify new TE location at M&O Foreman Office 100A, existing B21 B1.TR, existing B19 B05TR, B19-serving-B21 relationship, active services, TR01-104-1 / 100-A schedule, 659 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, and all firestopping/penetrations. | 0
22 | B22_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Break Room 102 new TE location, existing Room 103 wall/wall-mount TE, active services, TR01-102-1 schedule, 139 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, and existing B19 port relationship. | 0
33 | B33_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify EEO Manager Office B23 new TE location, existing Tel Closet B17, active services, TE01-B23-1 schedule, 102 ft basement cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, existing camera/security devices, and B17 legacy port/service relationships. | 0
61 | B61_Assessment | PILOT PHASE | 55% | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence. | 0
62 | B62_TR_Assessment | Yellow | 50% | 23 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Verify cooling power path, firestopping, extinguisher location, and existing conditions | 0
70 | B70_TR_Assessment | Yellow | 50% | 23 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Verify cooling power path, firestopping, extinguisher locations, and migration phasing | 0
78 | B78_Assessment | Yellow | 50% | 32 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify rooms B30, B35, 1232, 227A, 342, 401 and existing telecom rooms 15E, 1234, 353, 308A, 408A; confirm active equipment, rack transfers, HVAC units, panel sources, UPS/PDU power, FEC locations, FA/FP modifications, PACS/CCTV, hazardous material impacts, cable tray routes, firestopping, and cutover sequence. | 0
80 | B80_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 102 and existing 127A/126; confirm active services, existing rack/equipment transfer, B80-TR102A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, cable tray route, and telecom cutover sequence. | 0
82 | B82_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Excluded / Verify Existing | Field verify Room 102 new TE location, existing B01-A, active services, TR01-102-01 schedule, 278 ft cable tray route, 10 Cat6A cable legend, UPS/PDU source, B82-MDP/B82-P-EMER connections, IU-1-01/CU-1-01 cooling, fiber paths A/B, firestopping/sleeves, existing cameras and TE cutover plan. | 0
BCH | BCH_Assessment | Yellow | 50% | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Room 107, Room 00-107 rack/elevation reference, new TE/enclosure location, active services, cable tray route, power/UPS/PDU source, grounding/bonding, fiber Path A/B, 4-inch sleeve/firestop scope, camera/VMS scope, and confirm whether the BCH rack elevation is TE-only or new telecom room buildout. | 0
MCR | MCR_Assessment | Yellow | 50% | 31 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify new MCR Room 107 / Room 031 naming, MDA-A/B and HDA-A/B rack rows, existing MCR/server equipment in 107/137, UPS-A/B, CRAC units, clean-agent/preaction/fire alarm systems, MCR panel/ATS/generator sources, camera/access control devices, fiber Path A/B, service provider entrance, cable tray/firestop scope, third-party inspections, and phased activation/cutover sequence. | 0
SITE | SITE_Assesment | Yellow | 50% | 32 | 0 | 0 | 0 | N/A | Verify | Verify | N/A / Maintain Access | N/A | Verify Site Access | Field verify all THH/manhole locations, utility depths, trench routes, concrete ductbank sizes, Path A/B conduit counts, building tie-in points, site electrical conflicts, MCR/provider entrance points, restoration limits, traffic/pedestrian controls, inspection hold points, and fiber testing/acceptance sequence. | 0
TOP OPEN RISKS — static snapshot from PMIS_Data | [8 empty] | OPEN QUESTIONS — static snapshot from PMIS_Data
Building | Risk ID | Room | Impact | Prob. | Score | Owner | Risk |  | Building | Question ID | Assigned To | Status | Impact | Question | Notes
SITE | SITE-R1 | All | Critical | High | 9 | GC / Civil / VA | Existing utility locations are approximate and field conditions may vary from survey |  | 01 | B01-Q1 | VA / OIT / Designer | Open | Room inventory could miss scope | Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points?
#REF! | B01-R2 | B02/138/282 | Critical | Medium | 8 | Telecom / OIT | Existing equipment may remain active during transfer to Room 107 |  | 01 | B01-Q2 | OIT / Contractor | Open | Potential communications/security outage | What active services are currently fed from existing Rooms B02, 138 and 282?
01 | B01-R3 | 107 | Critical | Medium | 8 | Mechanical / Electrical | Dedicated cooling emergency power, condensate, BACnet and alarms not verified |  | 01 | B01-Q3 | OIT / Telecom | Open | Cutover and rack elevation risk | What equipment from existing racks transfers to new Room 107 versus remains/decommissions?
01 | B01-R6 | All | Critical | Medium | 8 | Telecom / OIT | Telecom/fiber cutover could affect active hospital communications across basement/first/second levels |  | 01 | B01-Q4 | Mechanical / Electrical / VA | Open | Cooling continuity unclear | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107?
02 | B02-R2 | Existing rooms | Critical | Medium | 8 | Telecom / OIT | Existing equipment may remain active during transfer to new TRs |  | 01 | B01-Q5 | GC / COR | Open | Life-safety acceptance risk | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107?
02 | B02-R3 | 141/236/342 | Critical | Medium | 8 | Mechanical / Electrical | Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified |  | 01 | B01-Q6 | Electrical / Designer | Open | Electrical readiness unknown | Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved?
02 | B02-R6 | All | Critical | Medium | 8 | Telecom / OIT | Telecom/fiber cutover could affect active hospital communications across several floors |  | 01 | B01-Q7 | GC / Firestop | Open | Fire/smoke spread risk | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified?
03 | B03-R2 | 107 / 101C | Critical | Medium | 8 | Telecom / OIT | Existing DMARC/fiber/telecom equipment may remain active during transfer to Room 101E |  | 01 | B01-Q8 | GC / Cx Manager / OIT | Open | Turnover package gap | Which third-party inspections and commissioning forms are required before VA/OIT acceptance?
03 | B03-R3 | 101E | Critical | Medium | 8 | Mechanical / Electrical | Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified |  | 02 | B02-Q1 | VA / OIT / Designer | Open | Room inventory could miss scope | Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points?
03 | B03-R6 | All | Critical | Medium | 8 | Telecom / OIT | Telecom/fiber cutover could affect active hospital communications and provider/DMARC services |  | 02 | B02-Q2 | OIT / Contractor | Open | Potential communications/security outage | What active services are currently fed from existing Rooms B-06, 141 and 236?
04 | B04-R4 | All | Critical | Medium | 8 | GCC / VA / Electrical | Cooling emergency power / 24/7 continuity not verified |  | 02 | B02-Q3 | OIT / Telecom | Open | Cutover and rack elevation risk | What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236?
04 | B04-R6 | All | Critical | Medium | 1900-01-07 | Telecom / OIT / GC | Telecom/fiber cutover could affect active hospital communications |  | 02 | B02-Q4 | Mechanical / Electrical / VA | Open | Cooling continuity unclear | Which IU/CU pair serves each TR and are they on emergency/backup power?
DATA ARCHITECTURE / HOW THIS HOME SHEET WORKS
1 | Assessment sheets keep the same section headings and columns. | → | PMIS_Data maps those sections into normalized tables. | → | PMIS_Home formulas roll up counts, readiness and status. |  |  | 2 | Change building details in the building assessment sheet first. | → | Re-run mapping refresh when new buildings/changes are added. | → | Dashboard updates from PMIS_Data.
Core mapped tables | Building Rollup, Rooms, Risks, Questions, Photos, Readiness, Discipline Status | [6 empty] | Critical control point | Do not manually overwrite PMIS_Home formulas; change source sheets or PMIS_Data refresh.
Recommended pilot | B61 |  | Why | Representative complexity without MCR-level campus criticality. |  |  |  | Final exam | MCR and SITE should not be used as first-work quality gate.
Program controls | Shutdown planning, active-service protection, ICRA/PCRA, firestop logs, photo evidence, OIT acceptance, commissioning, turnover documentation. | [6 empty] | Owner value | This is now an owner QA / PMIS control surface, not just a tracker.
Refresh note | If assessment sheets are edited later, PMIS_Data should be refreshed from the standardized sections. | [6 empty] | File generated | 2026-06-26 15:41

## Lists (hidden)
Status | Risk Priority | Question Status
Not Started | Low | Open
Verify | Medium | In Progress
Pass | High | Answered
Fail | Critical | Closed
N/A

## Telecom_Rooms (hidden)
TELECOM ROOMS / ASSESSMENTS
Source register for Building_View lookup. Auto-seeded from Building_Register raw room data.
Building | Room | TR/IDF/MDF | Rack Capacity | Power | Cooling | Access | Readiness | Notes | Lookup #
1 | 107 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | HR OFFICE
2 | 141 | TR | 2 RACKS |  |  |  | Open | PIV OFFICE
2 | 236 | TR | 2 RACKS |  |  |  | Open | IRM CLOSET
2 | 342 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | STORAGE
3 | 101C | TR | 2 RACKS |  |  |  | Open | TELECOM ROOM
4 | B18/19 | TR | 2 RACKS |  |  |  | Open | MOP STORAGE/BREAK ROOM
4 | 141 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | SOCIAL WORKER
4 | 244 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | CLINICAL PSYCHOLOGIST
5 | 150 | TE | TE |  |  |  | Open | FILE CABINETS TO BE RELOCATED
6 | 178 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | TELECOM ROOM
6 | 233 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | PATIENT TOILET
7 | B18/ 20G | TR | 1 NEW, 1 FUTURE |  |  |  | Open | OFFICE/ NEW ENTRY TO ADJACENT TOILET
7 | 228A | TR | 2 RACKS |  |  |  | Open | SHARED SOCIAL WORKER OFFICE
8 | 2065A | TR | 2 RACKS |  |  |  | Open | TELECOM ROOM
9 | B01 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | STORAGE ROOM
9 | 104B | TR | 1 NEW, 1 FUTURE |  |  |  | Open | INTERVIEW ROOM
9 | 206 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | HALF OF OFFICE/UNOCCUPIED
10 | 200A | TR | 1 NEW, 1 FUTURE |  |  |  | Open | UNOCCUPIED
13 | 124 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | HALF OF TELEHEALTH
14 | 119 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | OFFICE
15 | 124 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | HALF OF OFFICE
16 | 15 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | TELECOM ROOM
17_29 | 118 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | OFFICE
18 | 110 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | STORAGE
20_32 | 1B | TE | TE |  |  |  | Open | BOOKCASE TO BE RELOCATED
21_19 | 100A | TE | TE |  |  |  | Open | REFRIGERATOR/FILE CABINET RELOCATED
22 | 106 | TE | TE |  |  |  | Open
33 | B23 | TE | TE |  |  |  | Open | CABINET REMOVED/ FILE CABINETS RELOCATED
61 | B13 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | RESTROOM, CORRIDOR, ALCOVE
61 | 124 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | COPY ROOM, 2 STORAGE ROOMS
61 | 226 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | COPY/MAILROOM, FILE CABINET ALCOVE, WAITING ALCOVE
62 | B24A | TR | 1 NEW, 1 FUTURE |  |  |  | Open | RESTROOM BEING USED AS STORAGE
62 | 125 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | MEDICATION ROOM
62 | 225 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | OFFICE
70 | B27 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | OFFICE
70 | 125 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | OFFICE CUBICLES
70 | 262A | TR | 1 NEW, 1 FUTURE |  |  |  | Open | OFFICE
78_78A | 1232 | TR | 2 RACKS |  |  |  | Open | OFFICE
78_78A | 227A | TR | 2 RACKS |  |  |  | Open | STORAGE
78_78A | 342 | TR | 2 RACKS |  |  |  | Open | COUNSEL OFFICE
78_78A | 401 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | PSYCH OFFICE
80 | 102 | TR | 1 NEW, 1 FUTURE |  |  |  | Open | PEER SUPPORT OFFICE
81 | 100F, 104 | TE | (2) TE |  |  |  | Open | UNOCCUPIED
82 | 102 | TE | TE |  |  |  | Open | STORAGE
BCHCRESCEN T HOUSE | 107 | TE | TE |  |  |  | Open | PRINTER/CABINETS TO BE RELOCATED

## Building_Stakeholders (hidden)
BUILDING STAKEHOLDERS
Campus-wide and building-specific stakeholders. Building_View pulls selected building plus Campus.
Building | Name | Organization | Role | Phone | Email | Authority / Influence | Notes | Lookup #
Campus | Cameron Labbree | VA Bedford | Healthcare Engineer / Primary VA POC |  |  | Primary daily VA contact |  | 1
Campus | Brian Koches | GCC | Sr. Vice President / Primary GCC POC |  |  | GCC primary contact |  | 2
Campus | Paul Thibodeau | GCC | Construction Quality Inspector |  |  | Field support / project intelligence |  | 3

## Existing_Conditions (hidden)
EXISTING CONDITIONS
Enter field observations here. Building_View pulls rows matching Building in column A.
Building | Room / Area | Existing Condition | Deficiency | Photo Ref | Potential Impact | Verified By | Date | Lookup #

## Doc_Register (hidden)
DOCUMENT / DRAWING REGISTER
Searchable index for PDFs, drawings, narratives, specs, and appendices
Doc ID | File / Document | Discipline | Sheet No | Title | Revision | Date | Building | System | Keywords | Link / Path | Lookup #
DOC-001 | 00 41 13.10 - Construction Estimate Breakdown Template.pdf |  |  | 00 41 13.10 - Construction Estimate Breakdown Template.pdf |  |  | Campus |  |  | Plans\00 41 13.10 - Construction Estimate Breakdown Template.pdf | 1
DOC-002 | 01 00 00.B - Appendix B - Submittal Log.pdf | Submittals |  | 01 00 00.B - Appendix B - Submittal Log.pdf |  |  | Campus | Project Controls | submittal, log | Plans\01 00 00.B - Appendix B - Submittal Log.pdf | 2
DOC-003 | 01 00 00.C - Appendix C - VHA ICRA-1.3 (Dec 9 2024).pdf | Safety / Infection Control |  | 01 00 00.C - Appendix C - VHA ICRA-1.3 (Dec 9 2024).pdf |  |  | Campus | ICRA | ICRA, infection control, safety | Plans\01 00 00.C - Appendix C - VHA ICRA-1.3 (Dec 9 2024).pdf | 3
DOC-004 | 01 00 00.D - Appendix D - VHA PCRA 2024 1.1 Final.Template Fillable.pdf | Safety / Risk |  | 01 00 00.D - Appendix D - VHA PCRA 2024 1.1 Final.Template Fillable.pdf |  |  | Campus | PCRA | PCRA, safety, risk | Plans\01 00 00.D - Appendix D - VHA PCRA 2024 1.1 Final.Template Fillable.pdf | 4
DOC-005 | 01 00 00.E - Appendix E - J2247012 Bedford MA VAMC ACM Inspection LCP Testing Report Final 11-20-2024 - signed-unlocked.pdf | Hazardous Materials |  | 01 00 00.E - Appendix E - J2247012 Bedford MA VAMC ACM Inspection LCP Testing Report Final 11-20-2024 - signed-unlocked.pdf |  |  | Campus | ACM / LCP | asbestos, lead, hazardous material | Plans\01 00 00.E - Appendix E - J2247012 Bedford MA VAMC ACM Inspection LCP Testing Report Final 11-20-2024 - signed-unlocked.pdf | 5
DOC-006 | 01 00 00.F - Appendix F - GPRS REPORT - 689391 EX01.pdf | Existing Conditions |  | 01 00 00.F - Appendix F - GPRS REPORT - 689391 EX01.pdf |  |  | Campus | Utility / Scanning | GPRS, utility, locating | Plans\01 00 00.F - Appendix F - GPRS REPORT - 689391 EX01.pdf | 6
DOC-007 | 01 00 00.G - Appendix G - Geotechnical and Boring Reports.pdf | Geotechnical |  | 01 00 00.G - Appendix G - Geotechnical and Boring Reports.pdf |  |  | Campus | Site / Soils | geotechnical, boring, soils | Plans\01 00 00.G - Appendix G - Geotechnical and Boring Reports.pdf | 7
DOC-008 | 518-22-700.Bedford.EHRM.IFC.B01.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B01.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B01.20260316.pdf | 8
DOC-009 | 518-22-700.Bedford.EHRM.IFC.B02.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B02.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B02.20260316.pdf | 9
DOC-010 | 518-22-700.Bedford.EHRM.IFC.B03.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B03.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B03.20260316.pdf | 10
DOC-011 | 518-22-700.Bedford.EHRM.IFC.B04.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B04.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B04.20260316.pdf | 11
DOC-012 | 518-22-700.Bedford.EHRM.IFC.B05.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B05.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B05.20260316.pdf | 12
DOC-013 | 518-22-700.Bedford.EHRM.IFC.B06.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B06.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B06.20260316.pdf | 13
DOC-014 | 518-22-700.Bedford.EHRM.IFC.B07.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B07.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B07.20260316.pdf | 14
DOC-015 | 518-22-700.Bedford.EHRM.IFC.B08.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B08.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B08.20260316.pdf | 15
DOC-016 | 518-22-700.Bedford.EHRM.IFC.B09.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B09.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B09.20260316.pdf | 16
DOC-017 | 518-22-700.Bedford.EHRM.IFC.B10.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B10.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B10.20260316.pdf | 17
DOC-018 | 518-22-700.Bedford.EHRM.IFC.B12.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B12.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B12.20260316.pdf | 18
DOC-019 | 518-22-700.Bedford.EHRM.IFC.B13.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B13.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B13.20260316.pdf | 19
DOC-020 | 518-22-700.Bedford.EHRM.IFC.B14.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B14.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B14.20260316.pdf | 20
DOC-021 | 518-22-700.Bedford.EHRM.IFC.B15.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B15.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B15.20260316.pdf | 21
DOC-022 | 518-22-700.Bedford.EHRM.IFC.B16.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B16.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B16.20260316.pdf | 22
DOC-023 | 518-22-700.Bedford.EHRM.IFC.B17_29.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B17_29.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B17_29.20260316.pdf | 23
DOC-024 | 518-22-700.Bedford.EHRM.IFC.B18.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B18.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B18.20260316.pdf | 24
DOC-025 | 518-22-700.Bedford.EHRM.IFC.B20.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B20.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B20.20260316.pdf | 25
DOC-026 | 518-22-700.Bedford.EHRM.IFC.B21_19.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B21_19.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B21_19.20260316.pdf | 26
DOC-027 | 518-22-700.Bedford.EHRM.IFC.B22.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B22.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B22.20260316.pdf | 27
DOC-028 | 518-22-700.Bedford.EHRM.IFC.B33.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B33.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B33.20260316.pdf | 28
DOC-029 | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf | 29
DOC-030 | 518-22-700.Bedford.EHRM.IFC.B62.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B62.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B62.20260316.pdf | 30
DOC-031 | 518-22-700.Bedford.EHRM.IFC.B70.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B70.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B70.20260316.pdf | 31
DOC-032 | 518-22-700.Bedford.EHRM.IFC.B78_78A.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B78_78A.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B78_78A.20260316.pdf | 32
DOC-033 | 518-22-700.Bedford.EHRM.IFC.B80.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B80.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B80.20260316.pdf | 33
DOC-034 | 518-22-700.Bedford.EHRM.IFC.B81.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B81.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B81.20260316.pdf | 34
DOC-035 | 518-22-700.Bedford.EHRM.IFC.B82.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.B82.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.B82.20260316.pdf | 35
DOC-036 | 518-22-700.Bedford.EHRM.IFC.BCH.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.BCH.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.BCH.20260316.pdf | 36
DOC-037 | 518-22-700.Bedford.EHRM.IFC.MCR.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.MCR.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.MCR.20260316.pdf | 37
DOC-038 | 518-22-700.Bedford.EHRM.IFC.SITE.20260316.pdf | Telecom / EHRM |  | 518-22-700.Bedford.EHRM.IFC.SITE.20260316.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.EHRM.IFC.SITE.20260316.pdf | 38
DOC-039 | 518-22-700.Bedford.MA.EHRM.Specifications.IFC.20260413.pdf | Telecom / EHRM |  | 518-22-700.Bedford.MA.EHRM.Specifications.IFC.20260413.pdf |  |  | Campus | EHRM / Telecom | EHRM, telecom, fiber, drawings | Plans\518-22-700.Bedford.MA.EHRM.Specifications.IFC.20260413.pdf | 39
DOC-040 | 518-22-700.Summary Log_ADD1.20260225.pdf |  |  | 518-22-700.Summary Log_ADD1.20260225.pdf |  |  | Campus |  |  | Plans\518-22-700.Summary Log_ADD1.20260225.pdf | 40

## Documentation (hidden)
518-22-700 Bedford MA EHRM Narrative IFC.pdf
Plans\00 41 13.10 - Construction Estimate Breakdown Template.pdf
Doc ID
Plans\01 00 00.B - Appendix B - Submittal Log.pdf
Plans\01 00 00.C - Appendix C - VHA ICRA-1.3 (Dec 9 2024).pdf
Plans\01 00 00.D - Appendix D - VHA PCRA 2024 1.1 Final.Template Fillable.pdf
Plans\01 00 00.E - Appendix E - J2247012 Bedford MA VAMC ACM Inspection LCP Testing Report Final 11-20-2024 - signed-unlocked.pdf
Plans\01 00 00.F - Appendix F - GPRS REPORT - 689391 EX01.pdf
Plans\01 00 00.G - Appendix G - Geotechnical and Boring Reports.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B01.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B02.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B03.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B04.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B05.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B06.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B07.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B08.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B09.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B10.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B12.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B13.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B14.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B15.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B16.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B17_29.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B18.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B20.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B21_19.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B22.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B33.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B62.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B70.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B78_78A.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B80.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B81.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.B82.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.BCH.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.MCR.20260316.pdf
Plans\518-22-700.Bedford.EHRM.IFC.SITE.20260316.pdf
Plans\518-22-700.Bedford.MA.EHRM.Specifications.IFC.20260413.pdf
Plans\518-22-700.Summary Log_ADD1.20260225.pdf

## PMIS_Data (2) (hidden)
PMIS_DATA — FORMULA-FED BUILDING / AREA ROLLUP | [15 empty] | Data | [7 empty] | Building Selector
Building | Sheet | Overall Status | Sheet Readiness | Avg Readiness | Construction Ready | Room Count | Open Risks | Open Questions | Open Photos | HVAC | Electrical | Telecom | Fire Protection | Fire Alarm | Security | Next Action | Major Blocker | Risk Density | Question Density | Photo Density | Owner Focus | Execution Gate | Shutdowns | Source Health | Payment Confidence | Payment Recommendation | OIT Readiness | OIT Status | OIT Blocker / Constraint | Material Compliance | QA / Material Status | Productivity Score | Productivity Status | Acceptance Readiness | Acceptance Status | Pilot Gate Completion | Open Gate Count | Owner Decision Queue | Dashboard Signal | Owner Controls Health
01 | B01_Assessment | Yellow | 50% | 50% | No | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify Room 107, existing B02, 138, and 282; confirm active services, existing rack/equipment transfer, B01-TR107A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 394 ft cable tray routes, and telecom cutover sequence. | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
02 | B02_Assessment | Yellow | 50% | 50% | No | 30 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify new Rooms 141, 236, 342 and existing B-06/141/236; confirm active services, rack/equipment transfer, B02-TR141A/B, B02-TR236A/B, B02-TR342A/B panel sources, CU-1-01/CU-2-01/CU-3-01 cooling assignments, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, 2,560 ft cable tray routes, and telecom cutover sequence. | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
03 | B03_Assessment | Yellow | 50% | 50% | No | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify Room 101E, existing Room 107, and existing DMARC Room 101C; confirm active services, existing rack/equipment transfer, B03-TR101CA/B panel sources, CU-01 cooling assignment, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 961 ft cable tray routes, Room 107 inventory, and telecom cutover/fiber transfer sequence. | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
04 | B04_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify TR rooms B05, 141, and 244A; confirm cooling, panel/circuiting, fire alarm/sprinkler impacts, FEC locations, and cutover/phasing plan. | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
05 | B05_Assessment | Yellow | 55% | 55% | No | 26 | 0 | 0 | 0 | N/A | Verify | Verify | N/A | Verify | Verify | Field verify Room 150 TE location, existing 153-A equipment to remain/transition, electrical source, UPS/PDU receptacles, PACS/CCTV requirements, firestopping, and cutover sequence. | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
06 | B06_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify existing B-01 equipment, Rooms 178 and 233, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, and telecom cutover sequence. | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
07 | B07_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify TR B-18 and 228A; confirm rack/equipment layout, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, and telecom cutover sequence. | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
08 | B08_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify B-15, B12B, and 2065A; confirm active services, 2065A rack layout, panel/power source, IU/CU cooling, hazardous material/abatement impacts, FEC locations, PACS/CCTV, and telecom cutover sequence. | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
09 | B09_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify B01, 104B, and 206A; confirm existing equipment and active services, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, and telecom cutover sequence. | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
10 | B10_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify attic Telecom Room 200A, basement normal/emergency electrical source rooms B24/B25, existing wall-mounted rack/equipment, panel sources B10-TR200AA/AB, IU/CU-1-01 cooling, FEC/fire alarm/sprinkler impacts, hazardous/abatement scope, and telecom cutover plan. | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
12 | B12_Assessment | Yellow | 60% | 60% | No | 26 | 0 | 0 | 0 | N/A | N/A / Verify | Verify | N/A / Verify | N/A / Verify | N/A / Verify | Field verify existing fiber pathway through Building 12, existing rack/demarc/serving closet condition, floor/wall penetrations, routing from basement/first/second level telecom plans, phasing/cutover approach, and test/label/as-built deliverables. | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
13 | B13_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 124 and existing Tel Room 222; confirm active services, rack/equipment transfer, B13-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
14 | B14_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 119 and existing basement Tel/F Panel B.01/B2; confirm active services, rack/equipment transfer, B14-TR119A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 14 includes new first-level Telecom Room 119 and existing basement telecom rooms B.01/B2; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
15 | B15_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 124A, existing Tel Room 222 and basement B01; confirm active services, rack/equipment transfer, B15-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 15 includes new first-level Telecom Room 124A and existing telecom transition points at second-level Tel Room 222 and basement B01; field verification, active service cutover, 240V UPS/PDU power, dedicated heat-pump cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
16 | B16_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 015 and existing Room 014; confirm active services, rack/equipment transfer, B16-TR015A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, panel replacement/load measurement, and telecom cutover sequence. | Building 16 includes new basement Telecom Room 015 and existing basement Telecom Room 014; field verification, active service transfer, 240V UPS/PDU power, dedicated cooling, panel replacement/source coordination, firestopping, PACS/CCTV integration, and cable tray coordination remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
17 | B17_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 118, existing B35A, and Building 29 service path; confirm active services, B17-TR118A/B panel sources, BUS-B17-EQDP / BUS-B17-NPB1-R sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, hazardous material impacts, and cutover plan. | Building 17_29 includes new first-level Telecom Room 118 serving Building 17 and Building 29, plus existing basement Telecom Closet B35A; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, cable tray, firestopping, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
18 | B18_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 110, existing TE 111B, existing Closet 213, and all active services; confirm B18-TR110A/B panel sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, lead-paint/hazardous impacts, and cutover plan. | Building 18 includes new first-level Telecom Room 110 and existing telecom transition rooms 111B and 213; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, lead-paint/first-level hazardous material coordination, firestopping, cable tray, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
20 | B20_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Office 1B new TE location, existing Tel/Data Closet 8A, active services, TE01-1B-1 schedule, existing open TE cabinet, existing ground bar/patch panel/equipment box/indoor AC/backboard, 459 ft cable tray route, 10 Cat6A cross-connect cables, power/UPS/PDU source, and fiber Path A/B cutover. | Building 20 is a telecom-enclosure building, not a full TR buildout. Scope centers on new first-level Office 1B wall-mount TE enclosure and existing Tel/Data Closet 8A; mechanical and fire protection scope are excluded by the cover sheet, but field verification, active equipment transfer, fiber/copper cutover, cable tray, firestopping, power/UPS/PDU, and existing equipment protection remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
21 | B21_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify new TE location at M&O Foreman Office 100A, existing B21 B1.TR, existing B19 B05TR, B19-serving-B21 relationship, active services, TR01-104-1 / 100-A schedule, 659 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, and all firestopping/penetrations. | Building 21 is combined with Building 19 and is primarily a telecom-enclosure scope. New first-level M&O Foreman Office 100A / RM 104 schedule is served by a new 12RU TE enclosure, while existing Building 21 B1.TR and Building 19 B05TR equipment remain transition points. Fire protection scope is excluded, but mechanical/electrical sheets exist for equipment support. Field verification, active-service transfer, 659 ft cable tray, firestopping, UPS/PDU power, fiber/copper cutover, and B19/B21 scope boundary remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
22 | B22_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Break Room 102 new TE location, existing Room 103 wall/wall-mount TE, active services, TR01-102-1 schedule, 139 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, and existing B19 port relationship. | Building 22 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new first-level Break Room 102 TE enclosure and existing first-level wall/wall-mount TE Room 103. Field verification, active service transfer, 139 ft cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, and B19 utility service relationship remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
33 | B33_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify EEO Manager Office B23 new TE location, existing Tel Closet B17, active services, TE01-B23-1 schedule, 102 ft basement cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, existing camera/security devices, and B17 legacy port/service relationships. | Building 33 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new basement EEO Manager Office B23 TE enclosure and existing Tel Closet B17. Field verification, active service transfer, 102 ft basement cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, fiber/copper cutover, and legacy service relationships to Buildings 3, 80 and 82 remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
61 | B61_Assessment | PILOT PHASE | 55% | 55% | YES | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence. | Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. | 0 | 0 | 0 | Monitor | Ready | 0 | Mapped | 0% | Not Mapped |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped |  | Ready for Turnover | 0 / 8 Complete | 8 | Recommend Turnover | 🟢 READY | Mapped
62 | B62_TR_Assessment | Yellow | 50% | 50% | No | 23 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Verify cooling power path, firestopping, extinguisher location, and existing conditions | Cooling / emergency power not verified | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
70 | B70_TR_Assessment | Yellow | 50% | 50% | No | 23 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Verify cooling power path, firestopping, extinguisher locations, and migration phasing | Cooling / emergency power and existing TR phasing not verified | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
78 | B78_Assessment | Yellow | 50% | 50% | No | 32 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify rooms B30, B35, 1232, 227A, 342, 401 and existing telecom rooms 15E, 1234, 353, 308A, 408A; confirm active equipment, rack transfers, HVAC units, panel sources, UPS/PDU power, FEC locations, FA/FP modifications, PACS/CCTV, hazardous material impacts, cable tray routes, firestopping, and cutover sequence. | Building 78/78A is a very large full-scope TR building with basement through fourth-level telecom rooms, existing telecom rooms, hazardous abatement, architectural, fire protection, mechanical, electrical, security, telecom, rack elevations and photo references. Major open issues include active service cutover, dedicated HVAC validation, panel/UPS/PDU coordination, 4,849 ft cable tray routes, firestopping, PACS/CCTV, existing rack transfers, and turnover testing. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
80 | B80_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 102 and existing 127A/126; confirm active services, existing rack/equipment transfer, B80-TR102A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, cable tray route, and telecom cutover sequence. | Building 80 includes a new first-level Telecom Room 102 and existing Tel Closet 127A / photo-reference Room 126 transition point. Field verification, active equipment transfer, dedicated cooling IU-1-01/CU-1-01, B80-TR102A/B power, 811 ft cable tray, firestopping, PACS/CCTV, existing two-post rack migration, and room-number mapping remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
82 | B82_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Excluded / Verify Existing | Field verify Room 102 new TE location, existing B01-A, active services, TR01-102-01 schedule, 278 ft cable tray route, 10 Cat6A cable legend, UPS/PDU source, B82-MDP/B82-P-EMER connections, IU-1-01/CU-1-01 cooling, fiber paths A/B, firestopping/sleeves, existing cameras and TE cutover plan. | Building 82 is identified as a Telecom Enclosure (TE) building on the cover sheet, with fire protection scope excluded, but mechanical sheets show IU-1-01/CU-1-01 dedicated cooling for Room 102 and electrical drawings show B82-MDP/B82-P-EMER power. Scope centers on new first-level Telecom Room 102 / 12RU enclosure and existing first-level Telecom Room B01-A transition point. Field verification, active-equipment transfer, 278 ft cable tray, firestopping, UPS/PDU power, HVAC controls, fiber/copper cutover, and room/equipment mapping remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
BCH | BCH_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Room 107, Room 00-107 rack/elevation reference, new TE/enclosure location, active services, cable tray route, power/UPS/PDU source, grounding/bonding, fiber Path A/B, 4-inch sleeve/firestop scope, camera/VMS scope, and confirm whether the BCH rack elevation is TE-only or new telecom room buildout. | Crescent House/BCH is a Telecom Enclosure (TE) scope with mechanical and fire protection excluded by the cover sheet. Scope centers on first-level Room 107 and rack/equipment location shown as Room 00-107 / BCH Crescent House. Field verification, room naming, wall-mounted TE versus 45RU room/rack elevation conflict, active-service cutover, power/UPS/PDU source, firestopping, fiber A/B routing, and cable tray/WAO quantities remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
MCR | MCR_Assessment | Yellow | 50% | 50% | No | 31 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify new MCR Room 107 / Room 031 naming, MDA-A/B and HDA-A/B rack rows, existing MCR/server equipment in 107/137, UPS-A/B, CRAC units, clean-agent/preaction/fire alarm systems, MCR panel/ATS/generator sources, camera/access control devices, fiber Path A/B, service provider entrance, cable tray/firestop scope, third-party inspections, and phased activation/cutover sequence. | MCR is the most critical EHRM infrastructure building. Scope includes new Main Computer Room, new MDA A/B rows, HDA A/B rows, existing server/MCR equipment transfer from 107/137, redundant fiber Path A/B, new CRAC cooling, UPS A/B, electrical service/ATS/generator integration, clean-agent fire suppression, wet sprinkler/fire alarm interfaces, PACS/CCTV, 359 ft cable tray, and MCR activation window. Major risk is service continuity during backbone/core migration and VA activation. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
SITE | SITE_Assesment | Yellow | 50% | 50% | No | 32 | 0 | 0 | 0 | N/A | Verify | Verify | N/A / Maintain Access | N/A | Verify Site Access | Field verify all THH/manhole locations, utility depths, trench routes, concrete ductbank sizes, Path A/B conduit counts, building tie-in points, site electrical conflicts, MCR/provider entrance points, restoration limits, traffic/pedestrian controls, inspection hold points, and fiber testing/acceptance sequence. | Site package controls the redundant telecommunications backbone for the full EHRM campus. Scope includes site survey, electrical site plans, telecom site plans, enlarged views, plan/profile sheets for Path A/B, concrete ductbank, direct-bury conduit, handholes THH #1-#19, communication manholes with locking covers, concrete pullboxes, trench restoration, and the site one-line fiber diagram. Major risks are existing utility conflicts, A/B path separation, ductbank inspection before backfill, MCR activation sequencing, and coordination of multiple building tie-ins. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 80% | Partial / Verify |  | Ready | Clear | 0% | Not Mapped | 0% | Not Mapped | 0% | Not Mapped | 0 / 8 Complete | 8 | QA / Material Review | 🔴 ATTENTION | Mapped
33 | B33_Assessment | B33-R8 | B17 / Other Bldgs | Existing B17 cross-building service relationships may create cutover dependency | High | Medium | 6 | Verify ports to Bldgs 3, 80 and 82, SERTEX utility service, labels, test records, service provider dependency and OIT approval | Telecom / OIT | Closed | Existing B17 elevation identifies ports 1-72 to Bldg 3, 73-96 to Bldg 80, 97-120 to Bldg 82, and 121-144 to Bldg 3.
61 | B33_Assessment | B61-R1 | All | Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | Large multi-room scope with active demarc/server equipment.
61 | B33_Assessment | B61-R2 | B13H-A / 124 / 226 | Hazardous material abatement plans exist for first and second levels | High | Medium | 6 | Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation | GC / IH / COR | Closed | Drawing index includes 61H-101 and 61H-102 hazardous material abatement plans.
61 | B33_Assessment | B61-R3 | 137 / 137A | Existing server/demarc equipment may remain active during cutover | Critical | Medium | 8 | Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path | OIT / Telecom | Closed | Existing APC/Fujitsu/rack/patch equipment shown in Room 137 inventory/rack elevations.
61 | B33_Assessment | B61-R4 | All TRs | Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR/server readiness.
61 | B33_Assessment | B61-R5 | All TRs | Panel source, UPS/PDU and rack receptacle coordination could delay energization | Critical | Medium | 8 | Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements | Electrical / GCC | Closed | Multiple telecom panelboards and PD panels shown.
61 | B61_Assessment | B61-R6 | All | Large cable tray scope creates coordination and firestop risk | High | Medium | 6 | Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 890 ft, first 499 ft, second 578 ft.
61 | B61_Assessment | B61-R7 | All | Telecom/fiber cutover could affect active hospital communications and server/demarc services | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | WAO counts and active ports are substantial across B13H-A, 124 and 226.
61 | B61_Assessment | B61-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope building with multiple divisions.
62 | B62_TR_Assessment | B62-R1 | All | Cooling redundancy / emergency power not verified | High | Medium | 6 | Confirm power path for cooling, controls, condensate pump | GCC / VA | Closed | 0
62 | B62_TR_Assessment | B62-R2 | All | Firestopping condition unknown | High | Medium | 6 | Survey penetrations and temporary/permanent firestop plan | GCC | Closed | 0
62 | B62_TR_Assessment | B62-R3 | All | Existing room conditions undocumented | Medium | High | 6 | Create photo record before construction begins | GCC | Closed | 0
62 | B62_TR_Assessment | B62-R4 | All | Condensate leak risk near IT equipment | High | Medium | 6 | Verify condensate routing and alarms | GCC / Contractor | Closed | 0
70 | B70_TR_Assessment | B70-R1 | All | Cooling emergency power / continuity not verified | High | Medium | 6 | Confirm power path for cooling, controls, BACnet adapter, and condensate pump | GCC / VA | Closed | 0
70 | B70_TR_Assessment | B70-R2 | All | 1-hour rated/smoke-rated TR envelope and penetrations not field verified | High | Medium | 6 | Survey walls, doors, sleeves, trays, firestop, and head-of-wall conditions | GCC | Closed | 0
70 | B70_TR_Assessment | B70-R3 | B27 | Existing basement service conditions may constrain routing and access | Medium | High | 6 | Document existing utilities, clearances, and phasing around active systems | GCC | Closed | 0
70 | B70_TR_Assessment | B70-R4 | All | Existing TR/service equipment transfer could affect active operations | High | Medium | 6 | Require phasing plan and maintain analog/low-voltage systems operational | GCC / Contractor | Closed | 0
70 | B70_TR_Assessment | B70-R5 | All | Condensate leak risk near IT equipment | High | Medium | 6 | Verify condensate routing, insulation, pump power, and alarms | GCC / Contractor | Closed | 0
78 | B70_TR_Assessment | B78-R1 | All | Existing conditions and active equipment across six TRs and existing telecom rooms not field verified | High | Medium | 6 | Perform detailed room-by-room existing condition survey with photos and active-service inventory | GCC / Contractor | Closed | B78/78A has six major TR areas and several existing transition rooms.
78 | B70_TR_Assessment | B78-R2 | Basement / Third | Hazardous material abatement plans exist for basement and third level | High | Medium | 6 | Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or MEP installation | GC / IH / COR | Closed | Drawing index includes 78_78AH-100 and 78_78AH-103.
78 | B70_TR_Assessment | B78-R3 | Existing rooms | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, OIT windows, rack inventory, temporary utilities and rollback plan | Telecom / OIT | Closed | Photo references include 15E, 1234, 353, 308A, 408A.
78 | B70_TR_Assessment | B78-R4 | All TRs | Dedicated cooling sequence, emergency power, condensate and alarms not verified | Critical | Medium | 8 | Confirm HVAC equipment serving each TR, emergency source, condensate, controls/BACnet and high-temp alarms | Mechanical / Electrical | Closed | Mechanical sheets are included for basement through fourth level.
78 | B70_TR_Assessment | B78-R5 | All TRs | Panel source, UPS/PDU and rack receptacle coordination could delay energization | Critical | Medium | 8 | Verify telecom panelboards, breakers, rack receptacles, UPS/PDU sources, SPDs, labels and LOTO requirements | Electrical / GCC | Closed | Electrical plans/schedules are extensive; confirm all panel IDs in field.
78 | B78_Assessment | B78-R6 | All | Large cable tray scope creates coordination and firestop risk | High | Medium | 6 | Verify 4,849 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 1,702 ft, first 959 ft, second 804 ft, third 695 ft, fourth 689 ft.
78 | B78_Assessment | B78-R7 | All | Telecom/fiber cutover could affect active hospital communications across B78 and B78A | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | Total scheduled ports exceed 1,300 across the primary schedules.
78 | B78_Assessment | B78-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope 102-sheet IFC package with multiple divisions.
80 | B78_Assessment | B80-R1 | All | Existing conditions for Room 102 and existing 127A/126 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B80 includes new TR plus existing telecom transition point.
80 | B78_Assessment | B80-R2 | 127A / 126 | Existing telecom equipment may remain active during transfer to Room 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing and rollback plan | Telecom / OIT | Closed | Existing rack elevation shows Cisco switches, legacy patch panels, Fiber LIU and APC floor UPS.
80 | B78_Assessment | B80-R3 | 102 / 127A | Room-number mismatch between Tel Closet 127A and photo/rack reference Room 126/127-A | High | Medium | 6 | Track both IDs in PMIS and confirm field room signage/owner mapping before punch list and turnover | GCC / VA / Designer | Closed | 80T-101 calls Tel Closet 127A; 80R-900 photo reference calls existing telecom room 126; 80T-604 lists room 126/127-A.
80 | B78_Assessment | B80-R4 | 102 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
80 | B78_Assessment | B80-R5 | 102 | B80-TR102A/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panel sources BUS-B80-MDP and BUS-B80-E1, breakers, receptacles, SPD, labels, load measurement and LOTO needs | Electrical / GCC | Closed | B80-TR102A/B panel schedules and one-line show normal/emergency source split.
80 | B80_Assessment | B80-R6 | All | 811 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | 80T-701 cable tray schedule: basement 122 ft, first level 688 ft, grand total 811 ft.
80 | B80_Assessment | B80-R7 | All | Telecom/fiber cutover could affect active hospital communications on first-level operations | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | RM102 supports 215 total ports including allowance and existing rack transfer.
80 | B80_Assessment | B80-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope 52-sheet IFC package with mechanical, electrical, FP and telecom work.
82 | B80_Assessment | B82-R1 | All | Existing conditions for new Room 102 TE and existing B01-A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B82 has a compact TE scope but still depends on field conditions and existing equipment transfer.
82 | B80_Assessment | B82-R2 | 102 / B01-A | Existing equipment in B01-A may remain active during transfer to new TE in 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 82T-101 keynotes require phasing plan and transfer of existing devices to new rack/enclosure.
82 | B80_Assessment | B82-R3 | 102 | Cover sheet says TE, but mechanical cooling is included for Room 102 | High | Medium | 6 | Confirm scope interpretation with VA/AE and ensure cooling is commissioned if it serves active TE equipment | GCC / VA / Designer | Closed | Unlike some TE buildings, B82 includes IU-1-01/CU-1-01 mechanical/electrical scope.
82 | B80_Assessment | B82-R4 | 102 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling appears included and must be verified before acceptance.
82 | B80_Assessment | B82-R5 | 102 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding, SPD and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs.
82 | B82_Assessment | B82-R6 | All | 278 feet of first-level cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | 82T-701 cable tray schedule lists first level estimated length of 278 ft.
82 | B82_Assessment | B82-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | Cover excludes fire protection; telecom notes require fire caulk and rated penetrations.
82 | B82_Assessment | B82-R8 | All | Commissioning/test documentation may be overlooked due to TE-only scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification, HVAC startup/controls and owner signoff | GC / Cx Manager | Closed | General notes still require testing, acceptance and documentation.
BCH | B82_Assessment | BCH-R1 | All | Existing conditions for Crescent House Room 107 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | BCH is off-site at 15 Veterans Way, Lowell and requires careful field verification.
BCH | B82_Assessment | BCH-R2 | 107 | Mechanical and fire protection are excluded despite telecom/electronics installation | High | Medium | 6 | Verify existing environmental and life-safety conditions support TE equipment; confirm no dedicated HVAC/FP requirement applies | GCC / VA / AE | Closed | Cover sheet explicitly excludes mechanical and fire protection.
BCH | B82_Assessment | BCH-R3 | 107 / 00 | Rack/elevation conflict: TE 12RU enclosure versus BCH Room 107 new telecom room elevation | High | Medium | 6 | Submit RFI/confirm with AE which elevation governs and map room/equipment in PMIS | Telecom / Designer | Closed | BCHT-604 includes both TE enclosure and BCH 45RU new telecom room/no existing elevations.
BCH | B82_Assessment | BCH-R4 | 107 | Active services and existing devices may require phasing/temporary service | Critical | Medium | 8 | Document active services, maintain existing service, use phasing plan, temporary utilities and OIT cutover windows | Telecom / OIT | Closed | General telecom notes require transfer/phasing and avoiding shutdowns.
BCH | B82_Assessment | BCH-R5 | 107 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | Electrical sheets included but no full mechanical/FP package.
BCH | BCH_Assessment | BCH-R6 | All | Cable tray, sleeve and pathway quantities not scheduled in a BCHT-701 sheet | High | Medium | 6 | Require coordination drawings showing route, supports, fill, penetrations, sleeves and cable counts | Telecom / GC | Closed | Drawing index does not list BCHT-701 telecom schedules.
BCH | BCH_Assessment | BCH-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch sleeves, rated penetrations, fire caulk, temporary firestopping and patching even without FP scope | GC / Firestop | Closed | Telecom plan notes still require fire caulk and rated penetration protection.
BCH | BCH_Assessment | BCH-R8 | All | Turnover documentation may be incomplete due to TE-only/off-site scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification and owner signoff | GC / Cx Manager | Closed | Commissioning/testing requirements still apply to impacted systems.
MCR | BCH_Assessment | MCR-R1 | All | MCR is a new standalone critical facility with 120-sheet multi-discipline scope | Critical | Medium | 8 | Use discipline-by-discipline pre-install checklist, coordination drawings, third-party inspections and commissioning tracker | GCC / VA / Cx | Closed | New MCR cannot depend on another project or funding source to be usable.
MCR | BCH_Assessment | MCR-R2 | Existing 107/137 | Existing MCR/server/core equipment transfer may interrupt hospital network operations | Critical | Medium | 8 | Require detailed OIT cutover plan, temporary fiber/umbilicals, rollback plan, VA activation windows and after-hours phasing | OIT / Telecom | Closed | Notes state MCR activation may need 3-6 months and WAO activation depends on fiber/core connections.
MCR | BCH_Assessment | MCR-R3 | MDA/HDA | A/B fiber path diversity and backbone commissioning not verified | Critical | Medium | 8 | Verify OSP/ISP Path A/B routing, no intermediate splices, test results, labeling and geographic diversity | Telecom / OIT | Closed | New fiber risers require A-side and B-side redundant paths to every TR.
MCR | BCH_Assessment | MCR-R4 | MCR / UPS | UPS-A/B, ATS/generator, panel source and PDU coordination could delay activation | Critical | Medium | 8 | Verify one-line, load banks, breaker settings, panel labels, generator/ATS tests, UPS start-up and A/B power mapping | Electrical / Cx | Closed | Electrical scope includes site electrical, enlarged MCR plans, one-lines and schedules.
MCR | BCH_Assessment | MCR-R5 | MCR | CRAC capacity, redundancy, condensate, BMS/FMS alarms and emergency power not verified | Critical | Medium | 8 | Confirm mechanical schedules, CRAC start-up, controls, alarm points, emergency source, environmental monitoring and hot/cold aisle performance | Mechanical / Cx | Closed | Telecom notes explicitly call for indoor computer room air conditioner CRAC units and BMS coordination.
MCR | MCR_Assessment | MCR-R6 | MCR | Clean-agent/preaction/fire alarm interface and room integrity acceptance risk | Critical | Medium | 8 | Track clean-agent calculations, room integrity test, release/abort stations, FA matrix, sprinkler/preaction tests and AHJ/third-party acceptance | FP / FA / Cx | Closed | MCR receives new fire alarm and clean-agent fire suppression system.
MCR | MCR_Assessment | MCR-R7 | MCR / Site | Civil/site/utility ductbank, drainage, grading and security envelope could affect substantial completion | High | Medium | 6 | Track civil utility plan, stormwater, grading, ductbank, site fiber conduit encasement, access and landscape/hardscape restoration | Civil / Site / GC | Closed | MCR package includes civil, structural and architectural site work.
MCR | MCR_Assessment | MCR-R8 | All | Commissioning/turnover package may be incomplete across all divisions | High | Medium | 6 | Maintain MCR-specific turnover matrix for electrical, mechanical, FP, FA, telecom, security, civil, structural and architectural systems | GC / Cx Manager | Closed | General notes require commissioning/recommissioning, third-party inspections and written reports.
SITE | MCR_Assessment | SITE-R1 | All | Existing utility locations are approximate and field conditions may vary from survey | Critical | High | 9 | Complete utility locate, GPR review, potholing/hand-digging at crossings and VA utility coordination before excavation | GC / Civil / VA | Closed | Multiple sheets repeat that survey conditions may vary and utility location service is required prior to excavation.
SITE | MCR_Assessment | SITE-R2 | All | A/B fiber path separation may not be maintained through common ductbank or congested areas | Critical | Medium | 8 | Verify separate conduits, route diversity, THH labels, T-601 path counts and as-built documentation | Telecom / OIT | Closed | Legend allows A+B in common ductbank but separate conduits; redundancy must be validated.
SITE | MCR_Assessment | SITE-R3 | All | Concrete ductbank could be backfilled before inspection | High | Medium | 6 | Establish inspection hold point; trench remains open until concrete duct inspection and photos are accepted | GC / QA / COR | Closed | Site notes state trench to remain open until inspection of concrete duct.
SITE | MCR_Assessment | SITE-R4 | MCR / Provider | WAN/provider fiber and MCR activation sequence could delay campus cutover | Critical | Medium | 8 | Coordinate Century Link/service provider, temporary fiber, provider extension, MCR readiness and OIT activation plan | OIT / Telecom | Closed | T-601 references WAN fiber, temporary fiber and provider extension.
SITE | MCR_Assessment | SITE-R5 | Roads / Parking / Pedestrian Areas | Trenching/restoration may disrupt accessible parking, fire lanes, public access and campus traffic | High | Medium | 6 | Submit traffic/pedestrian/staging plan, maintain fire lanes/hydrants and restore surfaces to match existing | GC / Site | Closed | General notes require coordination with owner and protection of accessible parking/public access.
SITE | SITE_Assesment | SITE-R6 | All Building Tie-ins | Building entry penetrations/firestopping may not align with building PMIS packages | High | Medium | 6 | Cross-check every site tie-in against building assessment, T-101 continuation sheets and firestop photos | Telecom / Firestop / QA | Closed | Every building continuation references building T-101 and T-601.
SITE | SITE_Assesment | SITE-R7 | Civil Restoration | Asphalt/concrete/landscape restoration quantities and limits may be underestimated | Medium | Medium | 4 | Verify trench patch details, tie bars, concrete/asphalt specs, landscape protection and final surface restoration photo log | GC / Civil | Closed | T-501 includes trenching/restoration details and concrete requirements.
SITE | SITE_Assesment | SITE-R8 | Commissioning / Turnover | Fiber testing, labels, as-builts and site utility commissioning may be incomplete | High | Medium | 6 | Track OTDR/power meter tests, conduit as-builts, THH labels, route photos, redlines, third-party inspections and VA/OIT acceptance | GC / Cx / OIT | Closed | Commissioning and third-party inspection requirements apply to site utilities and communications.
B01_Assessment
MAPPED OPEN QUESTIONS — FORMULA-FED FROM BUILDING SHEETS | B01_Assessment
Building | B01_Assessment | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
01 | B01_Assessment | B01-Q1 | Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
01 | B01_Assessment | B01-Q2 | What active services are currently fed from existing Rooms B02, 138 and 282? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
01 | B01_Assessment | B01-Q3 | What equipment from existing racks transfers to new Room 107 versus remains/decommissions? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0
01 | B01_Assessment | B01-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
01 | B01_Assessment | B01-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
01 | B01_Assessment | B01-Q6 | Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
01 | B01_Assessment | B01-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
01 | B01_Assessment | B01-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
02 | B01_Assessment | B02-Q1 | Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
02 | B01_Assessment | B02-Q2 | What active services are currently fed from existing Rooms B-06, 141 and 236? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
02 | B01_Assessment | B02-Q3 | What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0
02 | B01_Assessment | B02-Q4 | Which IU/CU pair serves each TR and are they on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
02 | B01_Assessment | B02-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
02 | B02_Assessment | B02-Q6 | Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
02 | B02_Assessment | B02-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
02 | B02_Assessment | B02-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
03 | B02_Assessment | B03-Q1 | Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
03 | B02_Assessment | B03-Q2 | What active services are currently fed from existing Room 107 and DMARC Room 101C? | OIT / Contractor / Provider | Closed | 0 | 0 | Potential communications/provider outage | 0 | 0 | 0
03 | B02_Assessment | B03-Q3 | What existing equipment transfers to new Room 101E versus remains/decommissions? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0
03 | B02_Assessment | B03-Q4 | Which IU/CU pair serves Room 101E and is it on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
03 | B02_Assessment | B03-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
03 | B03_Assessment | B03-Q6 | Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
03 | B03_Assessment | B03-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
03 | B03_Assessment | B03-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
04 | B03_Assessment | B04-Q1 | Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? | VA / OIT / Designer | Closed | 0 | 0 | Incomplete room inventory / missed scope | 0 | 0 | 0
04 | B03_Assessment | B04-Q2 | Are B05, 141, and 244A cooling systems on emergency/backup power? | VA / Electrical / Mechanical | Closed | 0 | 0 | Cooling continuity not confirmed | 0 | 0 | 0
04 | B03_Assessment | B04-Q3 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
04 | B03_Assessment | B04-Q4 | What is the approved migration and cutover sequence for active Building 04 services? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
04 | B03_Assessment | B04-Q5 | Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? | GC / COR | Closed | 0 | 0 | Work stoppage or exposure risk | 0 | 0 | 0
04 | B04_Assessment | B04-Q6 | Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? | Electrical / Designer | Closed | 0 | 0 | Electrical delay or overload risk | 0 | 0 | 0
04 | B04_Assessment | B04-Q7 | Are all rated wall/floor penetrations and speed sleeves identified and firestopped? | GC / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
04 | B04_Assessment | B04-Q8 | Which third-party tests, commissioning forms, and acceptance documents are required before VA turnover? | GC / Cx Manager | Closed | 0 | 0 | Incomplete turnover package | 0 | 0 | 0
05 | B04_Assessment | B05-Q1 | Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could be wrong | 0 | 0 | 0
05 | B04_Assessment | B05-Q2 | What active services are currently fed from the existing 153-A TE/legacy patch panels? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
05 | B04_Assessment | B05-Q3 | What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? | OIT / Contractor | Closed | 0 | 0 | Cutover risk | 0 | 0 | 0
05 | B04_Assessment | B05-Q4 | Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? | Electrical / Designer | Closed | 0 | 0 | Power source cannot be verified | 0 | 0 | 0
05 | B05_Assessment | B05-Q5 | Is emergency/backup power required or provided for the TE UPS/PDU source? | VA / Electrical | Closed | 0 | 0 | Continuity requirement unclear | 0 | 0 | 0
05 | B05_Assessment | B05-Q6 | Are firestopping locations and surface raceway/conduit routes shown and coordinated? | GC / Designer | Closed | 0 | 0 | Rated assembly/firestop risk | 0 | 0 | 0
05 | B05_Assessment | B05-Q7 | Does Room 150 or existing Room 153-A require PACS/CCTV modifications, or is existing security adequate? | Security / VA | Closed | 0 | 0 | Security acceptance risk | 0 | 0 | 0
06 | B05_Assessment | B06-Q1 | Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
06 | B05_Assessment | B06-Q2 | What active services are fed from existing B-01 and Room 178 legacy equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
06 | B05_Assessment | B06-Q3 | What is the approved cutover sequence for B-01, 178 and 233? | OIT / Contractor | Closed | 0 | 0 | Cutover risk | 0 | 0 | 0
06 | B05_Assessment | B06-Q4 | Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
06 | B05_Assessment | B06-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
06 | B06_Assessment | B06-Q6 | Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
06 | B06_Assessment | B06-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
06 | B06_Assessment | B06-Q8 | Which commissioning/third-party tests must be complete before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
07 | B06_Assessment | B07-Q1 | Confirm final TR scope: B-18 basement and 228A second floor only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
07 | B06_Assessment | B07-Q2 | Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? | Mechanical / Designer | Closed | 0 | 0 | Cooling scope unclear | 0 | 0 | 0
07 | B06_Assessment | B07-Q3 | Are cooling units and controls on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity not confirmed | 0 | 0 | 0
07 | B06_Assessment | B07-Q4 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
07 | B06_Assessment | B07-Q5 | What active services are currently fed from B-18 and/or existing pathways serving 228A? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
07 | B07_Assessment | B07-Q6 | Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
07 | B07_Assessment | B07-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
07 | B07_Assessment | B07-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
08 | B07_Assessment | B08-Q1 | Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory may miss scope | 0 | 0 | 0
08 | B07_Assessment | B08-Q2 | What active services are currently fed from existing B-15 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
08 | B07_Assessment | B08-Q3 | Is B12B truly a TE/equipment location or only a cabling pathway/service area? | VA / Designer / Contractor | Closed | 0 | 0 | Scope ambiguity | 0 | 0 | 0
08 | B07_Assessment | B08-Q4 | Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
08 | B07_Assessment | B08-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
08 | B08_Assessment | B08-Q6 | Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
08 | B08_Assessment | B08-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
08 | B08_Assessment | B08-Q8 | Which hazardous material/abatement steps apply to Level 2 floor penetrations and flooring removal? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
09 | B08_Assessment | B09-Q1 | Confirm final TR scope: B01 basement, 104B first level, and 206A second level? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory may miss scope | 0 | 0 | 0
09 | B08_Assessment | B09-Q2 | What active services are currently fed from B01 existing equipment/security/network devices? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
09 | B08_Assessment | B09-Q3 | What hazardous/abatement steps apply to B01, 104B and 206A work areas? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
09 | B08_Assessment | B09-Q4 | Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
09 | B08_Assessment | B09-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
09 | B09_Assessment | B09-Q6 | Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
09 | B09_Assessment | B09-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
09 | B09_Assessment | B09-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
10 | B09_Assessment | B10-Q1 | Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
10 | B09_Assessment | B10-Q2 | What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
10 | B09_Assessment | B10-Q3 | What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? | GC / IH / COR | Closed | 0 | 0 | Work delay/exposure risk | 0 | 0 | 0
10 | B09_Assessment | B10-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
10 | B09_Assessment | B10-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
10 | B10_Assessment | B10-Q6 | Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
10 | B10_Assessment | B10-Q7 | Are all attic wall/floor/ceiling penetrations, sleeves and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
10 | B10_Assessment | B10-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
12 | B10_Assessment | B12-Q1 | Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? | VA / OIT / Designer | Closed | 0 | 0 | Scope misunderstanding | 0 | 0 | 0
12 | B10_Assessment | B12-Q2 | What exact pathway does the Building 12 fiber take through basement, first and second levels? | Telecom Contractor / OIT | Closed | 0 | 0 | Fiber pull and access risk | 0 | 0 | 0
12 | B10_Assessment | B12-Q3 | Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? | OIT / Contractor | Closed | 0 | 0 | Termination and ownership unclear | 0 | 0 | 0
12 | B10_Assessment | B12-Q4 | Are existing conduits/cable trays available and below fill limits for the new fiber? | Telecom Contractor | Closed | 0 | 0 | Pathway capacity risk | 0 | 0 | 0
12 | B12_Assessment | B12-Q5 | Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? | GC / Firestop | Closed | 0 | 0 | Life safety/firestop risk | 0 | 0 | 0
12 | B12_Assessment | B12-Q6 | What is the approved cutover/testing/acceptance sequence for Building 12 fiber? | OIT / COR / Contractor | Closed | 0 | 0 | Possible outage or acceptance delay | 0 | 0 | 0
12 | B12_Assessment | B12-Q7 | Which fiber test reports, labels, route documentation and as-builts are required for closeout? | Telecom / GCC | Closed | 0 | 0 | Closeout documentation gap | 0 | 0 | 0
13 | B12_Assessment | B13-Q1 | Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
13 | B12_Assessment | B13-Q2 | What active services are currently fed from existing Tel Room 222 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
13 | B12_Assessment | B13-Q3 | What hazardous/abatement steps apply to first-level Room 124 work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
13 | B12_Assessment | B13-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
13 | B12_Assessment | B13-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
13 | B13_Assessment | B13-Q6 | Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
13 | B13_Assessment | B13-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
13 | B13_Assessment | B13-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
14 | B13_Assessment | B14-Q1 | Confirm final telecom scope: new Room 119 and existing basement B.01/B2 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
14 | B13_Assessment | B14-Q2 | What active services are currently fed from existing B.01/B2 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
14 | B13_Assessment | B14-Q3 | What hazardous/abatement steps apply to first-level Room 119 work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
14 | B13_Assessment | B14-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 119? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
14 | B13_Assessment | B14-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 119? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
14 | B14_Assessment | B14-Q6 | Are B14-TR119A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
14 | B14_Assessment | B14-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
14 | B14_Assessment | B14-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
15 | B14_Assessment | B15-Q1 | Confirm final telecom scope: new Room 124A and existing Rooms 222/B01 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
15 | B14_Assessment | B15-Q2 | Why does 15T-701 reference RM 109A while plans and electrical schedules identify Telecom Room 124A? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0
15 | B14_Assessment | B15-Q3 | What active services are currently fed from existing Room 222 and B01 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
15 | B14_Assessment | B15-Q4 | What hazardous/abatement steps apply to first-level Room 124A work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
15 | B14_Assessment | B15-Q5 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124A? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
15 | B15_Assessment | B15-Q6 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124A? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
15 | B15_Assessment | B15-Q7 | Are B15-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
15 | B15_Assessment | B15-Q8 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
16 | B15_Assessment | B16-Q1 | Confirm final telecom scope: new Room 015 and existing Room 014 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
16 | B15_Assessment | B16-Q2 | What active services are currently fed from existing Room 014 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
16 | B15_Assessment | B16-Q3 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 015? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
16 | B15_Assessment | B16-Q4 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 015? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
16 | B15_Assessment | B16-Q5 | Are B16-TR015A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
16 | B16_Assessment | B16-Q6 | Which existing panel/circuit breaker/feeder demolition and replacement affects Room 015 telecom power? | Electrical / GCC | Closed | 0 | 0 | Panel outage/cutover risk | 0 | 0 | 0
16 | B16_Assessment | B16-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
16 | B16_Assessment | B16-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
17 | B16_Assessment | B17-Q1 | Confirm final telecom scope: new Room 118, existing B35A, and Building 29 served from B17? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
17 | B16_Assessment | B17-Q2 | What active services are currently fed from existing B35A equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
17 | B16_Assessment | B17-Q3 | What exact Building 29 outlets/devices are served through TR17-118-1? | VA / OIT / Designer | Closed | 0 | 0 | Building 29 scope boundary unclear | 0 | 0 | 0
17 | B16_Assessment | B17-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 118? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
17 | B16_Assessment | B17-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 118? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
17 | B17_Assessment | B17-Q6 | Are B17-TR118A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
17 | B17_Assessment | B17-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
17 | B17_Assessment | B17-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
18 | B17_Assessment | B18-Q1 | Confirm final telecom scope: new Room 110 with existing 111B and 213 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
18 | B17_Assessment | B18-Q2 | Why does 18T-701 reference RM 111A while new rack/electrical plans identify Telecom Room 110? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0
18 | B17_Assessment | B18-Q3 | What active services are currently fed from existing 111B and 213 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
18 | B17_Assessment | B18-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 110? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
18 | B17_Assessment | B18-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 110? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
18 | B18_Assessment | B18-Q6 | Are B18-TR110A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
18 | B18_Assessment | B18-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
18 | B18_Assessment | B18-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
20 | B18_Assessment | B20-Q1 | Confirm final scope: new wall-mount TE enclosure in Office 1B and existing Tel/Data Closet 8A transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
20 | B18_Assessment | B20-Q2 | What active services are currently fed from existing 8A open TE cabinet and related equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
20 | B18_Assessment | B20-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Office 1B? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
20 | B18_Assessment | B20-Q4 | Is Office 1B HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0
20 | B18_Assessment | B20-Q5 | Are existing cameras/security devices in Building 20 protected and retained with no VMS/PACS changes? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
20 | B20_Assessment | B20-Q6 | Are all 459 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
20 | B20_Assessment | B20-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0
20 | B20_Assessment | B20-Q8 | Which test records and turnover documents are required for TE-only acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
21 | B20_Assessment | B21-Q1 | Confirm final scope: new TE enclosure at Room 100A/RM 104 and existing B21 B1.TR plus B19 B05TR transition? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
21 | B20_Assessment | B21-Q2 | Why does 21_19T-701 list RM 104 / TR01-104-1 while enlarged plan identifies Room 100A? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0
21 | B20_Assessment | B21-Q3 | What active services are currently fed from existing B21 B1.TR and B19 B05TR equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
21 | B20_Assessment | B21-Q4 | What exactly is meant by '19 serving 21' on the new TE enclosure elevation? | VA / OIT / Designer | Closed | 0 | 0 | Building 19/21 boundary unclear | 0 | 0 | 0
21 | B20_Assessment | B21-Q5 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in 100A? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
21 | B21_Assessment | B21-Q6 | Are all 659 ft of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
21 | B21_Assessment | B21-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0
21 | B21_Assessment | B21-Q8 | Which test records and turnover documents are required for TE-only acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
22 | B21_Assessment | B22-Q1 | Confirm final scope: new wall-mount TE enclosure in Break Room 102 and existing Room 103 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
22 | B21_Assessment | B22-Q2 | What active services are currently fed from existing Room 103 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
22 | B21_Assessment | B22-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
22 | B21_Assessment | B22-Q4 | Is Break Room 102 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0
22 | B21_Assessment | B22-Q5 | Are existing cameras/security devices in Building 22 protected and retained with no VMS/PACS changes? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
22 | B22_Assessment | B22-Q6 | Are all 139 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
22 | B22_Assessment | B22-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0
22 | B22_Assessment | B22-Q8 | What is the operational impact of Room 103 ports 1-24 to Building 19 ports 73-96? | VA / OIT / Designer | Closed | 0 | 0 | B19 dependency/cutover risk | 0 | 0 | 0
33 | B22_Assessment | B33-Q1 | Confirm final scope: new wall-mount TE enclosure in B23 and existing B17 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
33 | B22_Assessment | B33-Q2 | What active services are currently fed from existing B17 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
33 | B22_Assessment | B33-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in B23? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
33 | B22_Assessment | B33-Q4 | Is Office B23 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0
33 | B22_Assessment | B33-Q5 | Are existing cameras/security devices in Building 33 protected and retained with no VMS/PACS disruption? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
33 | B33_Assessment | B33-Q6 | Are all 102 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
33 | B33_Assessment | B33-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0
33 | B33_Assessment | B33-Q8 | What is the operational impact of B17 ports serving Buildings 3, 80 and 82? | VA / OIT / Designer | Closed | 0 | 0 | Cross-building dependency/cutover risk | 0 | 0 | 0
61 | B33_Assessment | B61-Q1 | Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
61 | B33_Assessment | B61-Q2 | What active services and circuits are currently housed in Room 137/137A? | OIT / Contractor | Closed | 0 | 0 | Potential outage/cutover risk | 0 | 0 | 0
61 | B33_Assessment | B61-Q3 | Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? | Electrical / Designer | Closed | 0 | 0 | Electrical PMIS mapping risk | 0 | 0 | 0
61 | B33_Assessment | B61-Q4 | Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
61 | B33_Assessment | B61-Q5 | Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
61 | B61_Assessment | B61-Q6 | Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
61 | B61_Assessment | B61-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and temporary firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
61 | B61_Assessment | B61-Q8 | Which third-party inspections, commissioning forms and OIT acceptance records are required before turnover? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
62 | B62_TR_Assessment | B62-Q1 | Are cooling units emergency powered? | VA / Designer | Closed | 0 | 0 | Cannot confirm continuity of operations | 0 | 0 | 0
62 | B62_TR_Assessment | B62-Q2 | Are future rack loads included in HVAC sizing? | Designer | Closed | 0 | 0 | Cooling may be undersized after expansion | 0 | 0 | 0
62 | B62_TR_Assessment | B62-Q3 | Is extinguisher location identified within 75 feet? | Contractor / COR | Closed | 0 | 0 | Life safety / acceptance risk | 0 | 0 | 0
62 | B62_TR_Assessment | B62-Q4 | Are all penetrations fully documented and firestopped? | Contractor / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q1 | Are cooling units and controls on emergency/backup power? | VA / Designer | Closed | 0 | 0 | Cannot confirm continuity of operations | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q2 | Are future rack loads included in HVAC sizing for B27, 125A, and 262A? | Designer | Closed | 0 | 0 | Cooling may be undersized after expansion | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q3 | Are extinguisher cabinet locations identified within 75 feet of each TR? | Contractor / COR | Closed | 0 | 0 | Acceptance / life safety risk | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q4 | Are all wall/floor penetrations and speed sleeves shown and firestopped? | Contractor / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q5 | What phasing is required to keep existing low-voltage/analog systems operational? | Contractor / OIT | Closed | 0 | 0 | Potential communications interruption | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q1 | Confirm final telecom room list and PMIS mapping: B30, B35, 1232, 227A, 342, 401 plus existing rooms 15E/1234/353/308A/408A? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q2 | What active services currently remain in each existing telecom room/photo reference location? | OIT / Contractor | Closed | 0 | 0 | Potential outage/cutover risk | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q3 | Are Room 1232 and existing Room 1234 separate rooms or naming/mapping references for the same telecom space? | VA / Designer / OIT | Closed | 0 | 0 | PMIS mapping risk | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q4 | Which dedicated cooling units serve each TR and are they on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q5 | Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
78 | B78_Assessment | B78-Q6 | Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
78 | B78_Assessment | B78-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and temporary firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
78 | B78_Assessment | B78-Q8 | Which third-party inspections, commissioning forms and OIT acceptance records are required before turnover? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
80 | B78_Assessment | B80-Q1 | Confirm final telecom scope: new Room 102 with existing 127A/126 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
80 | B78_Assessment | B80-Q2 | What active services are currently fed from existing Room 127A/126 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
80 | B78_Assessment | B80-Q3 | Are Room 127A and Room 126 the same telecom room, or separate locations? | VA / Designer / OIT | Closed | 0 | 0 | PMIS mapping and turnover risk | 0 | 0 | 0
80 | B78_Assessment | B80-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
80 | B78_Assessment | B80-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 102? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
80 | B80_Assessment | B80-Q6 | Are B80-TR102A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
80 | B80_Assessment | B80-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
80 | B80_Assessment | B80-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
82 | B80_Assessment | B82-Q1 | Confirm final scope: new 12RU wall-mount TE enclosure in Room 102 and existing B01-A transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
82 | B80_Assessment | B82-Q2 | What active services are currently fed from existing B01-A equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
82 | B80_Assessment | B82-Q3 | Is Room 102 officially a TE-only scope or a conditioned telecom room with mechanical support? | VA / AE / COR | Closed | 0 | 0 | Scope and commissioning responsibility unclear | 0 | 0 | 0
82 | B80_Assessment | B82-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
82 | B80_Assessment | B82-Q5 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
82 | B82_Assessment | B82-Q6 | Are all 278 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
82 | B82_Assessment | B82-Q7 | Are existing cameras/security devices protected and retained with no VMS/PACS disruption? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
82 | B82_Assessment | B82-Q8 | Which test records, HVAC startup records and turnover documents are required for TE acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q1 | Confirm final BCH scope: Room 107 TE enclosure only, or a new telecom room/rack buildout? | VA / AE / OIT | Closed | 0 | 0 | PMIS scope and acceptance criteria unclear | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q2 | Why does BCHT-604 show a T78 12RU TE enclosure and a separate BCH Crescent House Room 107 new telecom room elevation? | VA / Designer | Closed | 0 | 0 | Rack/equipment mapping conflict | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q3 | What active services currently serve Crescent House and where are existing terminations located? | OIT / Contractor | Closed | 0 | 0 | Cutover/outage risk | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q4 | What is the approved power source, receptacle type and circuit capacity for the new UPS/PDU? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q5 | Is existing HVAC/ambient condition acceptable for TE/network equipment since mechanical scope is excluded? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk | 0 | 0 | 0
BCH | BCH_Assessment | BCH-Q6 | Are cable tray route, sleeve locations, supports and firestopping details shown/field verified without a BCHT-701 schedule? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
BCH | BCH_Assessment | BCH-Q7 | Are camera/security devices required, protected and integrated into VMS for Room 107? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
BCH | BCH_Assessment | BCH-Q8 | Which test records and turnover documents are required for BCH TE/off-site acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
MCR | BCH_Assessment | MCR-Q1 | Confirm final room naming and PMIS mapping: MCR Room 107, Fiber Entrance Room 031, Existing 107/137 server/MCR references. | VA / OIT / Designer | Closed | 0 | 0 | Room inventory and turnover mapping could be wrong | 0 | 0 | 0
MCR | BCH_Assessment | MCR-Q2 | What existing core/server/rack equipment is being relocated from the existing MCR/server rooms, and what remains? | OIT / Contractor | Closed | 0 | 0 | Cutover and outage risk | 0 | 0 | 0
MCR | BCH_Assessment | MCR-Q3 | What is the approved MCR activation sequence and required VA/OIT hold points? | VA / OIT / COR | Closed | 0 | 0 | Schedule/cutover impact | 0 | 0 | General phasing notes mention 3-6 month MCR activation and split core operation.
MCR | BCH_Assessment | MCR-Q4 | Are UPS-A/B, generator/ATS and emergency power paths commissioned and mapped to each rack/PDU? | Electrical / Cx | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
MCR | BCH_Assessment | MCR-Q5 | Are CRAC units fully commissioned with BMS/FMS alarms, redundancy and emergency power? | Mechanical / Cx | Closed | 0 | 0 | Cooling continuity risk | 0 | 0 | 0
MCR | MCR_Assessment | MCR-Q6 | Are clean-agent/preaction/fire alarm systems fully designed, tested and accepted? | FP / FA / AHJ | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
MCR | MCR_Assessment | MCR-Q7 | Are redundant Path A/B fiber routes geographically diverse, tested, labeled and accepted? | Telecom / OIT | Closed | 0 | 0 | Backbone redundancy risk | 0 | 0 | 0
MCR | MCR_Assessment | MCR-Q8 | Which third-party inspections, commissioning reports and OIT validation records are required before turnover/activation? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q1 | Confirm final list of all site fiber buildings and whether Buildings 1-22, 33, 61, 62, 70, 78/78A, 80, 81, 82, Crescent House and MCR are included in one site backbone turnover package. | VA / OIT / Designer | Closed | 0 | 0 | Scope and turnover package mapping unclear | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q2 | Which THH/manhole numbers are new versus existing, and which require locking cover replacement only? | Telecom / Civil | Closed | 0 | 0 | Structure inventory and inspection scope unclear | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q3 | Are all A and B routes physically diverse enough and in separate conduit wherever common ductbank is used? | OIT / Designer | Closed | 0 | 0 | Redundancy risk | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q4 | What are the approved utility-locate/potholing requirements before excavation at each crossing? | GC / VA / Civil | Closed | 0 | 0 | Utility strike risk | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q5 | What inspection hold points are required for ductbank forms, conduit placement, concrete pour, pull string, mandrel and backfill? | QA / COR / Civil | Closed | 0 | 0 | QA acceptance risk | 0 | 0 | 0
SITE | SITE_Assesment | SITE-Q6 | Are directional boring alternatives allowed anywhere, or is all base-bid work trenching unless separately approved by Government? | VA / COR | Closed | 0 | 0 | Means/methods and cost/schedule risk | 0 | 0 | 0
SITE | SITE_Assesment | SITE-Q7 | What exact fiber test package is required for each path and building tie-in before connection to active operations? | OIT / Telecom / Cx | Closed | 0 | 0 | Acceptance/activation risk | 0 | 0 | 0
SITE | SITE_Assesment | SITE-Q8 | How will MCR/provider temporary fiber, new fiber and campus building activation be sequenced to limit shutdowns to one at a time? | OIT / GC / COR | Closed | 0 | 0 | Operational outage risk | 0 | 0 | 0
MAPPED ROOMS / TELECOM SPACES — FORMULA-FED FROM BUILDING SHEETS
Building | Sheet | Source Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
01 | B01_Assessment | 01 | 107 | First | New Telecom Room build area | Telecom Room | 1 | 1 | Verify | 01A-401 / 01E-101 / 01E-601 / 01E-701 / 01T-101 / 01T-604 / 01T-605 / 01T-701 | Primary Building 01 TR. Plans identify Room 107 as new TR with Rack ID TR01-107-1, one new 4-post rack plus future rack, 5kW UPS, future/zone PDU, network switches, 48-port Cat6A patch panels, 24-port Cat5e patch panel, Fiber LIU, panels B01-TR107A/B, IU-1-01/CU-1-01 cooling, camera 107-CAM-1, and 161 total ports with 10% allowance.
01 | B01_Assessment | 01 | B02 | Basement | Existing telecom room / racks | Existing telecom transition point | 3 | 0 | Verify | 01T-100 / 01T-604 / 01R-900 | Existing Basement Telecom Room B02 with two 2-post floor racks and one wall TE. Existing equipment includes open rack, UPS on floor, Tripp Lite Smart Pro UPS, Tera Max/Nokia/Baseband/IRU equipment, Corning LANscape, Cisco, and Ortronics 24-port patch panels. Protect active services and transfer devices as required.
01 | B01_Assessment | 01 | 138 | First | Existing telecom room / patch panels | Existing telecom transition point | 3 | 0 | Verify | 01T-101 / 01T-604 / 01R-900 | Existing First-Level Telecom Room 138 with existing patch panels, APC UPS floor, Cisco, Corning LANscape and Ortronics 24/48-port patch panels. Protect active services and verify migration to Room 107.
01 | B01_Assessment | 01 | 282 | Second | Existing telecom room / racks | Existing telecom transition point | 2 | 0 | Verify | 01T-101 / 01T-605 / 01R-900 | Existing Second-Level Telecom Room 282 with two 2-post floor racks, Cisco switches, cable managers, legacy Ortronics 24/48-port patch panels, Corning LANscape and APC 12-port equipment. Protect active services during Room 107 cutover.
02 | B02_Assessment | 02 | 141 | First | Existing first-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-401 / 02E-101 / 02E-401 / 02E-601 / 02E-701 / 02T-101 / 02T-401 / 02T-604 / 02T-701 | Primary first-level TR. Schedules identify RM141 with 211 WAO total, 215 active ports, 322 scheduled ports and 354 total ports with 10% allowance. Rack IDs TR01-141-01/02. Enlarged plan shows Room 141 new and demo scope, 174-CAM-01, existing patch panels/fire alarm cabinet relocated to RM141 and future rack space.
02 | B02_Assessment | 02 | 236 | Second | Existing second-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-401 / 02E-102 / 02E-402 / 02E-701 / 02T-102 / 02T-401 / 02T-604 / 02T-702 | Second-level TR. Schedules identify RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approximately 345 ports with 10% allowance. Rack IDs TR01-236-01/02. Enlarged plans show 236-CAM-01 and new/demolition work at Room 236 / existing Room 282.
02 | B02_Assessment | 02 | 342 | Third | Third-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-402 / 02E-103 / 02E-402 / 02E-701 / 02T-103 / 02T-401 / 02T-604 / 02T-703 | Third-level TR. Schedules identify RM342 with 274 WAO total, 96 active ports, 353 scheduled ports and 388 total ports with 10% allowance. Rack IDs TR01-342-01/02. Enlarged plans show 342-CAM-01, 342A-CK-A and new rack scope.
02 | B02_Assessment | 02 | B-06 | Basement | Existing telecom room / legacy rack equipment | Existing telecom transition point | 1 | 0 | Verify | 02T-100 / 02T-604 / 02R-900 | Existing Basement Telecom Room B-06 with legacy Ortronics 48-port patch panels. Photo reference identifies B-06 existing telecom room. Protect active services and verify transfer/abandonment scope.
02 | B02_Assessment | 02 | Existing 141 / 236 | First / Second | Existing telecom room equipment / transition points | Existing telecom transition points | 4 | 0 | Verify | 02T-604 / 02R-900 | Existing First-Level Telecom Room 141 and Second-Level Existing Telecom Room 236 shown in photo references/rack elevations. Existing devices and racks are to be protected or transferred per notes.
03 | B03_Assessment | 03 | 101E | First | New telecom room buildout / relocated TR function | Telecom Room | 2 | 1 | Verify | 03A-401 / 03E-101 / 03E-401 / 03E-601 / 03E-701 / 03T-101 / 03T-401 / 03T-604 / 03T-701 | Primary Building 03 TR. Schedules identify RM101E with 143 WAO total, 213 active ports, 187 scheduled ports, 206 total ports with 10% allowance, Rack IDs TR01-101E-1 and TR01-101E-2, 5kW UPS, Zone PDU, fiber LIU, Cat6A patch panels, and future rack/switch capacity.
03 | B03_Assessment | 03 | 107 | Basement | Existing telecom room / legacy rack equipment | Existing telecom transition point | 1 | 0 | Verify | 03T-100 / 03T-403 / 03T-604 / 03R-900 | Existing Basement Telecom Room 107. Rack elevation identifies Building 3 existing B3-LB-B13-TC-FIBER rack with UPS on floor, Cisco switch, legacy 48-port patch panels, and fiber LIU wall-mounted. 03T-403 provides Room 107 inventory list for reference.
03 | B03_Assessment | 03 | 101C | First | Existing DMARC / telecom room | Existing DMARC transition point | 1 | 0 | Verify | 03T-101 / 03T-401 / 03T-604 / 03R-900 | First-floor existing DMARC Room 101C / telecom room. Enlarged plan shows existing/removal patch panels, existing branch panel, telecom cabinet, 101C-CAM-01, 101C-CK-A, 101C-A/B/C/D and AP locations. Protect active DMARC/fiber until new service is operational.
03 | B03_Assessment | 03 | 108 / 107A / 101C related WAO areas | First | Work area outlets and WAP/camera locations | WAO recabling / device support | 0 | 0 | Verify | 03T-101 / 03T-701 | WAO schedule includes first-level outlets such as 108-A/B/C, 108-CK-A, 108-AP-A, 107A-AP-A, 101C-CAM-01, 101C-A/B/C/D and AP locations served from TR01-101E-1/2.
04 | B04_Assessment | 04 | B05 | Basement | Existing telecom / service area | TR | 2 | 0 | Verify | 04A-400 / 04T-604 / 04E-701 | Rack elevations show B05 with Rack 1 of 2 and Rack 2 of 2; new B04-TRB05A/B panels and NPA-TR feed shown.
04 | B04_Assessment | 04 | 141 | First | Existing room to be converted / upgraded | TR | 1 | 1 | Verify | 04A-401 / 04T-604 / 04E-701 | Architectural enlarged views identify Room 141; new 45-minute rated door/frame, 1-hour/smoke-rated envelope, open-to-deck TR, and future rack.
04 | B04_Assessment | 04 | 244A | Second | Existing or renovated telecom area | TR | 1 | 1 | Verify | 04T / 04E-701 | Panel schedule identifies B04-TR244A; room requires field verification of rack count, cooling, pathways, fire protection, and PACS/CCTV requirements.
05 | B05_Assessment | 05 | 150 | First | Telecom / equipment location | Telecom Enclosure (TE) | 1 | 0 | Verify | 05T-604 / 05T-401 / 05E-401 | New elevation identifies Room 150 with one 12RU Telecom Enclosure; includes APC UPS, PDUs, cable managers, 48-port patch panels, Cat6A patch panel, and Fiber LIU.
05 | B05_Assessment | 05 | 153-A | First | Existing wall-mounted TE / existing rack area | Existing equipment / transition point | 1 | 0 | Verify | 05T-604 | Existing elevation shows wall or wall-mount TE at Room 153-A with Cisco switches and multiple legacy 24-port patch panels; existing floor UPS shown.
06 | B06_Assessment | 06 | B-01 | Basement | Existing wall/wall-mount TE and floor UPS | Existing equipment / transition point | 1 | 0 | Verify | 06T-604 | Existing basement wall/wall-mount TE with Cisco switches, legacy Ortronics 48-port patch panels, and floor UPS.
06 | B06_Assessment | 06 | 178 | First | Existing telecom room / group therapy area adjacent | Telecom Room | 2 | 0 | Verify | 06A-401 / 06E-401 / 06T-604 / 06E-701 | Room 178 shown as 114 SF Telecom Room; existing 2-post racks and new B06-TR178A/B panel work with IU-1-01 cooling.
06 | B06_Assessment | 06 | 233 | Second | Data closet / patient toilet area conversion | Telecom Room | 1 | 1 | Verify | 06A-402 / 06E-401 / 06T-604 / 06E-701 | Room 233 shown as 119 SF Telecom Room/Data Closet; future rack elevation, B06-TR233A/B panels, and IU-2-01 cooling.
07 | B07_Assessment | 07 | B-18 | Basement | Existing office / telecom-service area | Telecom Room | 1 | 1 | Verify | 07A-400 / 07E-401 / 07T-604 / 07M-701 | Rack elevation shows B-18 as 1 of 1 + future, 4-post floor rack, UPS, future Zone PDU, network switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
07 | B07_Assessment | 07 | 228A | Second | Social worker shared / adjacent OPM storage and DOM MSA area | Telecom Room | 1 | 1 | Verify | 07A-401 / 07E-401 / 07T-604 / 07M-701 | Architectural enlarged view identifies Telecom Room 228A at 236 SF; includes fire-rated door/wall work, FEC requirement, exterior furring wall/window enclosure and temporary dust barrier.
08 | B08_Assessment | 08 | B-15 | Basement | Existing wall/wall-mounted TE and floor UPS | Existing equipment / transition point | 2 | 0 | Verify | 08T-604 | Existing rack elevation identifies Building 08 basement Room B-15 with wall/wall-mounted TE, legacy patch panels, legacy Fiber LIU, and floor UPS.
08 | B08_Assessment | 08 | B12B | Basement | Office / basement cabling area | Telecom enclosure / TE cabling service area | 1 | 0 | Verify | 08A-401 / 08E-701 / 08T-701 | Door schedule identifies B12B as Office with 45-minute door; telecom schedule and electrical schedule reference TE01-B12B-1 and TE receptacle Room B12B. Field verify actual TE/equipment scope.
08 | B08_Assessment | 08 | 2065A | Second | Existing copy/office/storage area converted | Telecom Room | 2 | 0 | Verify | 08A-401 / 08E-701 / 08T-604 / 08M-701 | Telecom Room 2065A, 127 SF; new rack elevation shows two 4-post floor racks, UPS, Zone PDU, network switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
09 | B09_Assessment | 09 | B01 | Basement | Storage / existing telecom equipment area | Telecom Room | 2 | 0 | Verify | 09A-400 / 09E-402 / 09T-604 / 09E-701 | Telecom Room B01, 200 SF; existing/new telecom equipment shown with panels B09-TRB01A/B and cooling circuits CU-0-1, CU-1-1, CU-2-1 in electrical schedule/enlarged plans.
09 | B09_Assessment | 09 | 104B | First | Interview room / existing area converted | Telecom Room | 2 | 0 | Verify | 09A-401 / 09E-401 / 09T-604 / 09E-701 | Telecom Room 104B, 85 SF; panels B09-TR104BA/B shown; first-level enlarged plans identify access control/security devices, IU-1-01, and TR receptacle/rack circuiting.
09 | B09_Assessment | 09 | 206A | Second | Nursing service / adjacent office area | Telecom Room | 2 | 0 | Verify | 09A-401 / 09E-401 / 09T-604 / 09E-701 | Telecom Room 206A, 120 SF; panels B09-TR206AA/B shown; second-level enlarged plans identify IU-2-01, TR circuits, security devices, and room layout adjacent to Nursing Service 206.
10 | B10_Assessment | 10 | 200A | Attic | Existing attic telecom/equipment area | Telecom Room | 2 | 1 | Verify | 10A-401 / 10E-401 / 10T-604 / 10M-701 | Primary Building 10 TR. Drawings identify attic-level Room 200A with existing wall-mounted rack/equipment, new telecom rack equipment, panels B10-TR200AA/AB, IU-1-01, CU-1-01, rack receptacles and future rack space.
10 | B10_Assessment | 10 | B24 | Basement | Existing electrical room - normal power | Electrical source / coordination room | 0 | 0 | Verify | 10E-401 / 10E-701 | Basement existing electrical room normal power referenced on electrical enlarged plan; coordinate B10-MDP/B10-L10-E feeders and load measurement.
10 | B10_Assessment | 10 | B25 | Basement | Existing electrical room - emergency power | Emergency electrical source / coordination room | 0 | 0 | Verify | 10E-401 / 10E-601 / 10E-701 | Basement existing electrical room emergency power referenced on electrical enlarged plan; coordinate ATS-B10-LSD, emergency source and TR equipment continuity.
12 | B12_Assessment | 12 | 00 / existing fiber path | B/1/2 | Existing building fiber pathway / pull-through route | Fiber-only pull-through scope | 0 | 0 | Verify | 12G-000 / 12T-100 / 12T-101 / 12T-604 | Cover sheet states Building 12 receives fiber only. Rack elevation sheet identifies Building 12 as existing rack elevation/fiber only with no rack mounting and no new TR buildout.
12 | B12_Assessment | 12 | Existing rack/demarc - field verify | Field verify | Existing service point / serving closet | Protect-in-place / fiber transition point | 0 | 0 | Verify | 12T-604 / 12T-601 / 12T-602 / 12T-603A/B | 12T-604 identifies building level B/1/2 and mounting type NONE/FIBER ONLY. Field verification required to document where fiber enters, passes through, and terminates.
13 | B13_Assessment | 13 | 124 | First | Telecom Room / new TR build area | Telecom Room | 2 | 1 | Verify | 13A-401 / 13E-401 / 13T-100 / 13T-701 | Primary Building 13 TR. Plans identify Telecom Room 124 at 119 SF, served by Rack ID TR01-124-1, panels B13-TR124AA/AB, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, and a future rack allowance.
13 | B13_Assessment | 13 | 222 | Second | Existing Tel Room / existing rack and patching area | Existing telecom transition point | 1 | 0 | Verify | 13T-100 / 13R-900 | Existing second-level Tel Room 222 shown with existing telco patch, plywood backboard, indoor AC unit, wall-mounted rack, patch panel, and security cabinet. Protect active services and verify what is transferred to Room 124.
14 | B14_Assessment | 14 | 119 | First | Telecom Room / new TR build area | Telecom Room | 1 | 1 | Verify | 14A-401 / 14E-100 / 14T-100 / 14T-604 / 14T-701 | Primary Building 14 TR. Plans identify Telecom Room 119 at 124 SF, served by Rack ID TR01-119-1, panels B14-TR119A/B, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, 56 feet of first-level cable tray, and a future rack allowance.
14 | B14_Assessment | 14 | B.01 | Basement | Existing Tel/F Panel room / telecom equipment area | Existing telecom transition point | 1 | 0 | Verify | 14T-100 / 14T-604 / 14R-900 | Existing basement Tel/F Panel B.01 shown at 165 SF with existing wall-mounted TE, patch panels, telco patch, plywood backboards, and legacy fiber/equipment. Protect active services and verify what transfers to Room 119.
14 | B14_Assessment | 14 | B2 | Basement | Existing telecom room reference | Existing telecom transition point | 1 | 0 | Verify | 14R-900 | Photo reference sheet identifies basement existing telecom room B2. Field verify whether B2 is same/related to B.01 or separate legacy telecom space.
15 | B15_Assessment | 15 | 124A | First | Office/room converted to Telecom Room | Telecom Room | 1 | 1 | Verify | 15A-401 / 15E-401 / 15T-100 / 15T-604 / 15T-701 | Primary Building 15 TR. Plans identify Telecom Room 124A at 121 SF, served by Rack ID TR15-109A-01, panels B15-TR124AA/AB, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, and a future rack allowance.
15 | B15_Assessment | 15 | 222 | Second | Existing Tel Room / wall-mounted rack and support equipment | Existing telecom transition point | 1 | 0 | Verify | 15T-100 / 15T-604 / 15R-900 | Existing second-level Tel Room 222 shown at 65 SF with existing/remain indoor AC unit, security cabinet, ground bar, plywood backboard, wall-mounted rack, existing Cisco switches, legacy patch panels, and floor UPS; protect active services and verify transfer to Room 124A.
15 | B15_Assessment | 15 | B01 | Basement | Existing telecom/crossover area | Existing telecom transition point | 1 | 0 | Verify | 15T-604 / 15R-900 | Rack elevations identify existing B-01 crossover wall/wall-mount TE with legacy 24-port patch panel. Photo reference identifies basement existing telecom room B01.
16 | B16_Assessment | 16 | 015 | Basement | Vacant / new telecom room build area | Telecom Room | 1 | 1 | Verify | 16A-400 / 16E-100 / 16T-100 / 16T-604 / 16T-701 | Primary Building 16 TR. Plans identify Telecom Room 015 at 79 SF, served by Rack ID TR01-015-A-1, panels B16-TR015A/B, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, 96 feet total cable tray, and future rack allowance.
16 | B16_Assessment | 16 | 014 | Basement | Existing telecom room / stair-adjacent legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 16T-100 / 16T-604 / 16R-900 | Existing basement Telecom Room 014 shown with wall-mounted rack, plywood backboard, patch panel, security cabinet, telco patch, existing floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU/wall; protect active services and verify transfer to Room 015.
17 | B17_Assessment | 17 | 118 | First | New telecom room build area | Telecom Room | 1 | 1 | Verify | 17_29A-401 / 17_29E-401 / 17_29T-100 / 17_29T-604 / 17_29T-701 | Primary Building 17 TR. Plans identify Telecom Room 118 at 157 SF, Rack ID TR17-118-1, panels B17-TR118A/B, 208V rack UPS/PDU equipment, IU-1-01/CU-1-01 cooling, 517 feet total cable tray, and future rack allowance. Rack elevation notes Room 118 serves Building 29.
17 | B17_Assessment | 17 | B35A | Basement | Existing telecom closet / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 17_29T-100 / 17_29T-604 / 17_29R-900 | Existing basement Telecom Closet B35A shown at 12 SF with wall-mounted TE, patch panel, security cabinet, plywood backboard, indoor AC unit, floor UPS, Cisco switches, legacy Ortronics 24/48-port patch panels and SERTEX utility service ports. Protect active services and verify transfer to Room 118.
17 | B17_Assessment | 29 | Building 29 path | First / served from B17 | Building 29 service extension | Served from B17 TR 118 | 0 | 0 | Verify | 17_29T-100 / 17_29T-604 / 17_29T-701 | Building 29 is shown served from B17, with path to B29 via 4-inch PVC and fiber extending from Building 17 to Building 29. Field verify pathway, service boundary, and active outlets included in TR17-118-1 schedule.
18 | B18_Assessment | 18 | 110 | First | New telecom room build area | Telecom Room | 1 | 1 | Verify | 18A-401 / 18E-101 / 18T-100 / 18T-401 / 18T-604 / 18T-701 | Primary Building 18 TR. Plans identify Telecom Room 110 at 168 SF, Rack ID TR01-111A-1, panels B18-TR110A/B, 208V rack UPS/PDU equipment, IU-1-01/CU-1-01 cooling, 315 feet total cable tray, and future rack allowance. Room 110 is the new rack room even though the schedule labels RM 111A.
18 | B18_Assessment | 18 | 111B | First | Existing TE / stair-adjacent legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 18T-401 / 18T-604 / 18R-900 | Existing first-level TE 111B shown at 13 SF with wall-mounted rack, plywood backboard, patch panel, security cabinet, existing floor UPS, and 5RU fiber optic housing. Protect active services and verify transfer to Room 110.
18 | B18_Assessment | 18 | 213 | Second | Existing telecom closet / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 18T-401 / 18T-604 / 18R-900 | Existing second-level Closet 213 shown at 8 SF with wall-mounted rack, plywood backboard, patch panel, security cabinet, APC floor UPS, SERTEX utility service ports, Cisco switch and legacy Ortronics patch panels. Protect active services and verify transfer to Room 110.
20 | B20_Assessment | 20 | 1B | First | Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 20T-101 / 20T-701 / 20E-101 / 20E-601 | Primary Building 20 TE. Plans identify Office 1B at 110 SF with new wall-mount telecom enclosure Rack ID TE01-1B-1, 12RU enclosure, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and 33 total ports with 10% allowance.
20 | B20_Assessment | 20 | 8A | First | Existing Tel/Data Closet / open TE cabinet | Existing telecom transition point | 2 | 0 | Verify | 20T-101 / 20T-701 / 20R-900 | Existing Tel/Data Closet 8A at 17 SF with existing open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy Ortronics 48-port patch panel, floor UPS and Fiber LIU. Protect active services and transfer to Office 1B TE.
21 | B21_Assessment | 21 | 100A | First | M&O Foreman Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 21_19T-101 / 21_19T-604 / 21_19T-701 / 21_19E-101 | Primary Building 21/B19 TE. Plans identify M&O Foreman Office 100A at 202 SF with new 12RU telecom enclosure, shown as 19 serving 21, Room 100-A, and schedule Rack ID TR01-104-1 / RM 104. Includes APC UPS, two PDUs, network switches B20 and B19, 48-port Cat6A patch panel, Fiber LIU, and 131 total ports with 10% allowance.
21 | B21_Assessment | 21 | B1.TR | Basement | Existing telecom room / wall-mount TE | Existing telecom transition point | 1 | 0 | Verify | 21_19T-100 / 21_19T-604 | Existing Building 21 basement B1.TR shown with legacy Ortronics 24/48-port patch panels, UPS on ground, Cisco switch, multiple legacy 24-port patch panels, Fiber LIU, and APC floor UPS. Protect active services and verify transfer/cutover to new TE.
21 | B21_Assessment | 19 | B05TR | Basement / First | Existing telecom room / wall-mount TE | Existing telecom transition point serving B19/B21 | 2 | 0 | Verify | 21_19T-100 / 21_19T-604 / 21_19R-900 | Existing Building 19 B05TR shown with basement and first-level existing elevations, legacy Ortronics patch panels, Cisco switch, Fiber LIU, APC floor UPS, and photo reference for basement B05. New enclosure is marked '19 serving 21'.
22 | B22_Assessment | 22 | 102 | First | Break Room / new TE location | Telecom Enclosure | 1 | 0 | Verify | 22T-101 / 22T-701 / 22E-101 / 22E-701 | Primary Building 22 TE. Plans identify Break Room 102 at 358 SF with new 12RU telecom enclosure Rack ID TR01-102-1, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and 8 total ports with 10% allowance.
22 | B22_Assessment | 22 | 103 | First | Existing wall/wall-mount TE / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 22T-101 / 22T-701 / 22R-900 | Existing Room 103 first-level wall/wall-mount TE shown with APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall, and ports 1-24 to Building 19 ports 73-96. Protect active services and transfer to Room 102 TE.
33 | B33_Assessment | 33 | B23 | Basement | EEO Manager Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 33T-100 / 33T-604 / 33T-701 / 33E-100 / 33E-701 | Primary Building 33 TE. Plans identify EEO Manager Office B23 at 175 SF with new 12RU telecom enclosure Rack ID TE01-B23-1, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, 55 WAO total, and 97 total ports with 10% allowance.
33 | B33_Assessment | 33 | B17 | Basement / First photo reference | Existing Tel Closet / open TE cabinet and legacy equipment | Existing telecom transition point | 2 | 0 | Verify | 33T-100 / 33T-604 / 33R-900 | Existing Tel Closet B17 shown at 13 SF with existing open TE cabinet, network door controller, indoor AC unit, plywood backboard, keypad, patch panel, ground bar, equipment box, Cisco switches, legacy patch panels, Fiber LIU, SERTEX utility service, and UPS on floor. Protect active services and verify transfer to Room B23 TE.
61 | B61_Assessment | 61 | B13H-A | Basement | Basement telecom / support area | Telecom Room | 1 | 1 | Pass | 61A-400 / 61E-401 / 61T-100 / 61T-401 / 61T-604 / 61T-701 | Basement TR identified as RM B13H-A with Rack ID TR01-B13H-A-1. Schedules identify 88 WAO total, 74 active ports, 129 scheduled ports, 142 ports with 10% allowance. Electrical panels include B61-TRB13A/B. Mechanical cooling includes IU-0-01/CU-0-01.
61 | B61_Assessment | 61 | 124 | First | First-level telecom area | Telecom Room | 1 | 1 | Pass | 61A-400 / 61E-402 / 61T-101 / 61T-401 / 61T-604 / 61T-701 | First-level TR identified as Room 124 / Rack ID TR01-124-1. Electrical panels include B61-TR124A/B. Mechanical cooling includes IU-1-01/CU-1-01. Verify room naming against electrical schedule references that also call out RM137B rack receptacles.
61 | B61_Assessment | 61 | 226 | Second | Second-level telecom area | Telecom Room | 1 | 1 | Pass | 61A-401 / 61E-402 / 61T-102 / 61T-401 / 61T-605 / 61T-702 | Second-level TR identified as Room 226 / Rack ID TR01-226-1. Schedules identify 109 WAO total, 126 active ports, 156 scheduled ports, 172 ports with 10% allowance. Electrical panels include B61-TR226A/B. Mechanical cooling includes IU-2-01/CU-2-01.
61 | B61_Assessment | 61 | 137 / 137A | First | Existing server/demarc/telecom equipment rooms | Existing demarc / server transition point | 11 | 0 | Pass | 61T-402 / 61T-606 / 61T-607 / 61R-900 | Existing Room 137/137A rack inventory and demarc/server equipment include existing 4-post racks, PACS/equipment racks, APC UPS/PDU equipment, Fujitsu FLM equipment, wall-mounted patch panels, and local elevations. Protect active services and verify what remains, transfers, or is modified.
62 | B62_TR_Assessment | 62 | B24A | Basement | Restroom / Storage | TR | 1 | 1 | Verify | B62 IFC | 0
62 | B62_TR_Assessment | 62 | 125 | First | Medication Room | TR | 1 | 1 | Verify | B62 IFC | 0
62 | B62_TR_Assessment | 62 | 225 | Second | Office | TR | 1 | 1 | Verify | B62 IFC | 0
70 | B70_TR_Assessment | 70 | B27 | Basement | Telecom Room / existing service area | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room B27; rack elevation references B-27 with 1 rack + future.
70 | B70_TR_Assessment | 70 | 125A | First | Telecom Room / existing or renovated space | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room 125A; rack elevation references 125-A with 1 rack + future.
70 | B70_TR_Assessment | 70 | 262A | Second | Telecom Room / existing or renovated space | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room 262A; rack elevation references 262-A with 1 rack + future.
78 | B70_TR_Assessment | 78/78A | B30 | Basement | Basement telecom area / existing rack transfer | Telecom Room | 2 | 1 | Verify | 78_78AA-400 / 78_78AE-401 / 78_78AT-100 / 78_78AT-604 / 78_78AT-701 | Basement primary TR. Schedule identifies RM B30 with 210 WAO total, 23 active ports, 311 scheduled ports, 342 total ports with 10% allowance. Rack IDs include TR01-B30-1 and TR01-B30-2.
78 | B70_TR_Assessment | 78/78A | B35 | Basement | Basement telecom area / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AT-100 / 78_78AT-605 / 78_78AT-702 | Basement TR/closet. Schedule identifies RM B35 with 53 WAO total, 23 active ports, 64 scheduled ports, 70 total ports with 10% allowance. Verify relationship to existing basement telecom room 15E photo reference.
78 | B70_TR_Assessment | 78/78A | 1232 | First | First-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-401 / 78_78AE-402 / 78_78AT-101 / 78_78AT-606 / 78_78AT-702/703 | First-level TR. Schedule identifies RM 1232 with 301 WAO total, 388 active ports, 404 scheduled ports, 444 total ports with 10% allowance. Existing photo references show first-level existing telecom room 1234; verify room-name mapping.
78 | B70_TR_Assessment | 78/78A | 227A | Second | Second-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-401 / 78_78AE-402 / 78_78AT-102 / 78_78AT-606 / 78_78AT-703/704 | Second-level TR. Schedule identifies RM 227A with 256 WAO total, 153 active ports, 348 scheduled ports, 383 total ports with 10% allowance. Existing photo references show second-level existing telecom room 1234; verify field room ID.
78 | B78_Assessment | 78/78A | 342 | Third | Third-level telecom room / existing rack transfer | Telecom Room | 2 | 1 | Verify | 78_78AA-402 / 78_78AE-403 / 78_78AT-103 / 78_78AT-607 / 78_78AT-704 | Third-level TR. Schedule identifies RM 342 with 158 WAO total, 163 active ports, 289 scheduled ports, 318 total ports with 10% allowance. Rack IDs include TR01-342-1 and TR01-342-2.
78 | B78_Assessment | 78/78A | 401 | Fourth | Fourth-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-402 / 78_78AE-404 / 78_78AT-104 / 78_78AT-607 / 78_78AT-705 | Fourth-level TR. Schedule identifies RM 401 with 89 WAO total, 65 active ports, 123 scheduled ports, 135 total ports with 10% allowance.
78 | B78_Assessment | 78/78A | 15E / 1234 / 353 / 308A / 408A | Existing levels | Existing telecom rooms / photo references | Existing telecom transition points | 5 | 0 | Verify | 78_78AR-900 / 901 / 902 / 903 | Photo references identify existing telecom rooms: basement 15E, first-level 1234, second-level 1234, third-level 353, fourth-level 308A and 408A. Protect active equipment and verify transfer/abandonment scope.
80 | B80_Assessment | 80 | 102 | First | Telecom Room / new TR build area | Telecom Room | 1 | 1 | Verify | 80A-401 / 80E-101 / 80E-401 / 80T-101 / 80T-604 / 80T-701 | Primary Building 80 TR. Plans identify Telecom Room 102 at 140 SF, new Rack ID TR01-102-1 plus future rack, panels B80-TR102A/B, 5kW 208V UPS/PDU rack power, IU-1-01/CU-1-01 dedicated cooling, camera 102-CAM-1, and 215 total ports with 10% allowance.
80 | B80_Assessment | 80 | 127A / 126 | First | Existing Tel Closet / existing telecom room photo reference | Existing telecom transition point | 1 | 0 | Verify | 80T-101 / 80T-604 / 80R-900 | Existing Tel Closet 127A shown at 9 SF with existing plywood backboard, ground bar, patch panel, equipment box and two-post TR. Rack elevation/photo reference identify existing room 126/127-A with existing wall/wall-mount TE, Cisco switches, legacy optical Fiber LIU, multiple legacy Ortronics patch panels, Cat5e patch panel and APC floor UPS. Verify room-number mapping and active services.
82 | B82_Assessment | 82 | 102 | First | Telecom Room / new TE location | Telecom Enclosure | 1 | 0 | Verify | 82A-401 / 82M-101 / 82E-101 / 82T-101 / 82T-604 / 82T-701 | Primary Building 82 TE. Plans identify Telecom Room 102 at 86 SF with new 12RU telecom enclosure, Rack ID TR01-102-01, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, IU-1-01/CU-1-01 cooling, and 40 total ports with 10% allowance.
82 | B82_Assessment | 82 | B01-A | First | Existing telecom room / wall rack and patch panels | Existing telecom transition point | 1 | 0 | Verify | 82T-101 / 82T-604 / 82R-900 | Existing first-level telecom room B01-A shown with existing wall rack, Cisco switches, cable management, Ortronics 24-port patch panels, APC floor UPS, and photo reference. Protect active services and verify transfer to Room 102 TE.
BCH | B82_Assessment | BCH | 107 | First | Existing Crescent House room area / telecom work area | Telecom Enclosure / Telecom Room | 1 | 0 | Verify | BCHGA-401 / BCHE-101 / BCHT-101 / BCHT-604 | Primary BCH telecom location. Architectural/electrical/telecom plans reference first-level Room 107. BCHT-101 enlarged plan identifies RM 107 new telecom work. BCHT-604 shows BCH Crescent House Room 107 as new telecom room / no existing elevations.
BCH | B82_Assessment | BCH | 00 / 107 | First | Rack/elevation reference location | Telecom Enclosure | 1 | 0 | Verify | BCHT-604 | Rack elevation shows 12RU telecom enclosure with APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and first-level mounting. Also includes separate BCH Crescent House Room 107 / new telecom room elevation; field confirm correct configuration.
MCR | B82_Assessment | MCR | 107 / MCR | Ground | New Main Computer Room / MCR building | Main Computer Room | 12 | 0 | Verify | MCRA-101 / MCRT-100 / MCRT-101 / MCRT-401 / MCRT-607-609 / MCRT-701 | Primary new MCR space. Telecom plans show MDA-A1/A2/A3, MDA-B1/B2/B3, HDA-A, HDA-B, UPS-A and UPS-B. Rack elevations identify MDA A/B racks, HDA A/B server cabinets, existing server cabinet transfer references, 10 WAO total and 359 ft cable tray.
MCR | B82_Assessment | MCR | 031 / Fiber Entrance Room 1 | Ground | Fiber entrance / telecom pathway space | Fiber Entrance / support room | 1 | 0 | Verify | MCRT-401 / MCRT-701 | MCRT-701 schedule is titled Data Device and Circuit Schedule - Fiber Entrance Room 1 and identifies Rack ID TR01-031-1, four data outlets 31-A/B/C/D and security camera/data devices 07-CAM-03/04/07/08/11.
MCR | B82_Assessment | MCR | MDA-A1/A2/A3 | Ground | New MDA row A | Main Distribution Area A | 3 | 0 | Verify | MCRT-607 | New MDA A racks: MDA-A-1, MDA-A-2, MDA-A-3. MDA A-2 includes 1RU LIU for hybrid FOC to HDA and 48x Cat6A to HDA. MDA A-1/A-3 reserved for LAN elements/leaf/access or spine/aggregation.
MCR | B82_Assessment | MCR | MDA-B1/B2/B3 | Ground | New MDA row B | Main Distribution Area B | 3 | 0 | Verify | MCRT-607 | New MDA B racks: MDA-B-1, MDA-B-2, MDA-B-3. MDA B-2 includes 1RU LIU for hybrid FOC to HDA and 48x Cat6A to HDA. Supports redundant B-side backbone/distribution.
MCR | MCR_Assessment | MCR | HDA-A | Ground | New HDA A row | Horizontal Distribution Area A | 1 | 0 | Verify | MCRT-608 | HDA A-1 new server cabinet front/rear elevation, 48-port Cat6A patch panels, HD fiber LIUs, HD Cat6A patch panel to MDA-A2, and backbone side A/B LIU. Also includes existing B61 server cabinet transfer references.
MCR | MCR_Assessment | MCR | HDA-B | Ground | New HDA B row | Horizontal Distribution Area B | 1 | 0 | Verify | MCRT-609 | HDA B-1 new server cabinet front/rear elevation, 48-port Cat6A patch panels, HD fiber LIUs, HD Cat6A patch panel to MDA-B2, and duplicate existing B61 server cabinet transfer references.
MCR | MCR_Assessment | MCR | Existing 107 / 137 Server MCR | Existing / transition | Existing MCR/server/core equipment | Existing equipment transition point | 20 | 0 | Verify | MCRT-604 / MCRT-605 / MCRT-606 / MCRT-608 / MCRT-609 | Existing MCR elevations include Rows 1-3 and existing server cabinet B61 equipment, Cisco core, WAN aggregation, NetScout, Canoga Perkins, Cisco switches, legacy Ortronics patch panels, LIUs, APC/Chatsworth/HP PDUs and UPS equipment. Protect and phase transfer.
B01_Assessment
MAPPED PHOTO / DOCUMENTATION NEEDS — FORMULA-FED FROM BUILDING SHEETS | B01_Assessment
Building | B01_Assessment | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
01 | B01_Assessment | B01-P001 | 107 | Existing / New Condition | Room 107 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, fiber path A/B, cable tray and penetrations | 0 | Paul | 0 | B01-R1/B01-R3 | Closed | 0
01 | B01_Assessment | B01-P002 | B02 | Existing Equipment | Basement existing telecom room B02 racks, wall TE, Cisco/Nokia/Baseband/IRU/Corning/Ortronics equipment, UPS and cable entries | 0 | Paul | 0 | B01-R1/B01-R2 | Closed | 0
01 | B01_Assessment | B01-P003 | 138 | Existing Equipment | First-level existing telecom room 138 racks, patch panels, Cisco, Corning, APC UPS and active service labels | 0 | Paul | 0 | B01-R2/B01-R6 | Closed | 0
01 | B01_Assessment | B01-P004 | 282 | Existing Equipment | Second-level existing telecom room 282 racks, Cisco switches, Ortronics patch panels, cable managers and active service labels | 0 | Paul | 0 | B01-R2/B01-R6 | Closed | 0
01 | B01_Assessment | B01-P005 | 107 | HVAC | IU-1-01/CU-1-01, condensate pump/line, thermostat, BACnet adapter, disconnects, FMS alarm points and power source | 0 | Paul | 0 | B01-R3 | Closed | 0
01 | B01_Assessment | B01-P006 | 107 | Electrical | B01-TR107A/B panels, rack receptacles, breakers, SPD, PACS power supply, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B01-R4/B01-R7 | Closed | 0
01 | B01_Assessment | B01-P007 | All | Cable Tray / Firestop | Basement/first/second cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B01-R5 | Closed | 0
01 | B01_Assessment | B01-P008 | 107 / Existing Rooms | Telecom / Security | New rack/future rack, Fiber LIU, Cat6A, patch panels, labels/test records, 107-CAM-1, PACS and existing rack transfer work | 0 | Paul | 0 | B01-R6/B01-R8 | Closed | 0
02 | B01_Assessment | B02-P001 | 141 | Existing / New Condition | Room 141 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 174-CAM-01, penetrations and demo/relocation conditions | 0 | Paul | 0 | B02-R1/B02-R3 | Closed | 0
02 | B01_Assessment | B02-P002 | 236 | Existing / New Condition | Room 236 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 236-CAM-01, penetrations and existing transfer conditions | 0 | Paul | 0 | B02-R1/B02-R6 | Closed | 0
02 | B01_Assessment | B02-P003 | 342 | Existing / New Condition | Room 342 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 342-CAM-01, penetrations and 342A-CK-A | 0 | Paul | 0 | B02-R1/B02-R7 | Closed | 0
02 | B01_Assessment | B02-P004 | B-06 | Existing Equipment | Basement existing telecom room B-06 legacy rack/patch panels, active service labels and cable entries | 0 | Paul | 0 | B02-R2 | Closed | 0
02 | B01_Assessment | B02-P005 | Existing 141 / 236 | Existing Equipment | Existing first/second-level telecom rooms 141 and 236, existing patch panels, relocated/removed equipment and fire alarm cabinet conditions | 0 | Paul | 0 | B02-R2/B02-R6 | Closed | 0
02 | B02_Assessment | B02-P006 | All TRs | Electrical / HVAC | B02-TR141/236/342 A/B panels, rack receptacles, breakers, SPD, UPS/PDU, CU/IU equipment, condensate, disconnects and labels | 0 | Paul | 0 | B02-R3/B02-R4 | Closed | 0
02 | B02_Assessment | B02-P007 | All | Cable Tray / Firestop | Basement/first/second/third/fourth cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B02-R5 | Closed | 0
02 | B02_Assessment | B02-P008 | All TRs | Telecom / Security | Racks, Fiber LIU, Cat6A, patch panels, labels/test records, cameras, PACS and existing rack transfer work | 0 | Paul | 0 | B02-R6/B02-R8 | Closed | 0
03 | B02_Assessment | B03-P001 | 101E | Existing / New Condition | Room 101E walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, penetrations, PACS and final TR layout | 0 | Paul | 0 | B03-R1/B03-R3 | Closed | 0
03 | B02_Assessment | B03-P002 | 107 | Existing Equipment | Basement existing telecom room 107 rack, UPS on floor, Cisco switch, legacy patch panels, fiber LIU, active service labels and cable entries | 0 | Paul | 0 | B03-R1/B03-R2 | Closed | 0
03 | B02_Assessment | B03-P003 | 101C | Existing DMARC | First-floor existing DMARC Room 101C, patch panels, telecom cabinet, branch panel, provider/fiber equipment, 101C-CAM-01 and active service labels | 0 | Paul | 0 | B03-R2/B03-R6 | Closed | 0
03 | B02_Assessment | B03-P004 | 101E / 101C | Electrical / Security | B03-TR101CA/B panels, rack receptacles, breakers, SPD, UPS/PDU, access controller, CU-01, 101C-CAM-01 and labels | 0 | Paul | 0 | B03-R4/B03-R7 | Closed | 0
03 | B02_Assessment | B03-P005 | 101E | HVAC | IU/CU-01, condensate route, thermostat, BACnet adapter, disconnects, alarm points and emergency power source | 0 | Paul | 0 | B03-R3 | Closed | 0
03 | B03_Assessment | B03-P006 | All | Cable Tray / Firestop | Basement and first-level cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B03-R5 | Closed | 0
03 | B03_Assessment | B03-P007 | WAO Areas | Telecom Devices | Representative outlets/WAPs/Centrak/clock/camera locations including 108-A/B/C, 108-CK-A, 107A-AP-A, 101C-CAM-01 and related labels | 0 | Paul | 0 | B03-R6 | Closed | 0
03 | B03_Assessment | B03-P008 | 101E / Existing Rooms | Telecom Acceptance | New racks TR01-101E-1/2, Fiber LIU, Cat6A, patch panels, labels/test records and existing rack transfer work | 0 | Paul | 0 | B03-R6/B03-R8 | Closed | 0
04 | B03_Assessment | B04-P001 | B05 | Existing Condition | Basement TR B05 existing conditions, racks, utilities, penetrations, panels | 0 | Paul | 0 | B04-R1/B04-R2 | Closed | 0
04 | B03_Assessment | B04-P002 | 141 | Existing Condition | Room 141 existing conditions, door/walls/ceiling/window/floor conditions | 0 | Paul | 0 | B04-R3 | Closed | 0
04 | B03_Assessment | B04-P003 | 244A | Existing Condition | Room 244A TR existing condition and panel/rack area | 0 | Paul | 0 | B04-R1 | Closed | 0
04 | B03_Assessment | B04-P004 | All | Firestop | All floor/wall/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B04-R7 | Closed | 0
04 | B03_Assessment | B04-P005 | All | HVAC | Cooling units, condensate routing, controls, high-temp alarms | 0 | Paul | 0 | B04-R4 | Closed | 0
04 | B04_Assessment | B04-P006 | All | Electrical | Panels, breakers, UPS/PDU receptacles, SPD, grounding/bonding | 0 | Paul | 0 | B04-R5 | Closed | 0
04 | B04_Assessment | B04-P007 | All | Telecom | Racks, ladder tray, fiber, Cat6A, labels, LIU, cable managers | 0 | Paul | 0 | B04-R6 | Closed | 0
04 | B04_Assessment | B04-P008 | All | Security | PACS, card reader, electric strike, camera, motion sensor rough-in | 0 | Paul | 0 | B04-R3 | Closed | 0
05 | B04_Assessment | B05-P001 | 150 | Existing Condition | Room 150 wall/TE location, mounting surface, clearances, power, pathway | 0 | Paul | 0 | B05-R1/B05-R4 | Closed | 0
05 | B04_Assessment | B05-P002 | 153-A | Existing Condition | Existing wall/wall-mount TE, Cisco switches, legacy patch panels, floor UPS | 0 | Paul | 0 | B05-R2 | Closed | 0
05 | B04_Assessment | B05-P003 | All | Firestop | All new/reused penetrations and surface raceway/conduit routes | 0 | Paul | 0 | B05-R5 | Closed | 0
05 | B05_Assessment | B05-P004 | 150 | Electrical | UPS/PDU outlet, circuit label, panel source, grounding/bonding | 0 | Paul | 0 | B05-R4 | Closed | 0
05 | B05_Assessment | B05-P005 | All | Telecom | TE, patch panels, Fiber LIU, labels, testing records, as-built conditions | 0 | Paul | 0 | B05-R6 | Closed | 0
05 | B05_Assessment | B05-P006 | All | Security | Door/security/CCTV/PACS conditions at TE location | 0 | Paul | 0 | B05-R6 | Closed | 0
06 | B05_Assessment | B06-P001 | B-01 | Existing Condition | Existing basement wall/wall-mount TE, Cisco switches, legacy patch panels, floor UPS | 0 | Paul | 0 | B06-R1/B06-R2 | Closed | 0
06 | B05_Assessment | B06-P002 | 178 | Existing Condition | Room 178 TR, existing 2-post racks, panels, card reader/security, HVAC location | 0 | Paul | 0 | B06-R1/B06-R3 | Closed | 0
06 | B05_Assessment | B06-P003 | 233 | Existing Condition | Room 233/Data Closet, adjacent toilet/bath areas, walls/door/ceiling/penetrations | 0 | Paul | 0 | B06-R4 | Closed | 0
06 | B05_Assessment | B06-P004 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B06-R6 | Closed | 0
06 | B05_Assessment | B06-P005 | 178/233 | HVAC | IU/CU equipment, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm | 0 | Paul | 0 | B06-R5 | Closed | 0
06 | B06_Assessment | B06-P006 | All | Electrical | B06-NP-TR, B06-EP-TR, B06-TR178A/B, B06-TR233A/B, breakers, SPD, labels | 0 | Paul | 0 | B06-R3/B06-R6 | Closed | 0
06 | B06_Assessment | B06-P007 | All | Telecom | Racks, ladder tray, fiber, Cat6A, LIU, patch panels, labels, test records | 0 | Paul | 0 | B06-R7 | Closed | 0
06 | B06_Assessment | B06-P008 | All | Security | Card readers, electric strikes, door position, motion sensors, CCTV/PACS integration | 0 | Paul | 0 | B06-R4 | Closed | 0
07 | B06_Assessment | B07-P001 | B-18 | Existing Condition | Basement TR B-18 existing room, walls, ceiling, floor, utilities, penetrations and pathway | 0 | Paul | 0 | B07-R1/B07-R2 | Closed | 0
07 | B06_Assessment | B07-P002 | 228A | Existing Condition | Second-floor TR 228A, door/wall/furring/window conditions, adjacent spaces and pathway | 0 | Paul | 0 | B07-R1/B07-R3 | Closed | 0
07 | B06_Assessment | B07-P003 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B07-R7 | Closed | 0
07 | B06_Assessment | B07-P004 | B-18/228A | HVAC | IU/CU units, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B07-R4 | Closed | 0
07 | B07_Assessment | B07-P005 | All | Electrical | B07-TRB18A/B and B07-TR228A/B panels, breakers, SPD, rack receptacles and labels | 0 | Paul | 0 | B07-R5 | Closed | 0
07 | B07_Assessment | B07-P006 | All | Telecom | Racks, ladder tray, fiber, Cat6A, patch panels, LIU, labels and test records | 0 | Paul | 0 | B07-R6 | Closed | 0
07 | B07_Assessment | B07-P007 | All | Security | Card reader, electric strike, door position, CCTV/PACS and motion sensors | 0 | Paul | 0 | B07-R3 | Closed | 0
08 | B07_Assessment | B08-P001 | B-15 | Existing Condition | Existing basement TE, legacy patch panels, Fiber LIU, floor UPS and pathways | 0 | Paul | 0 | B08-R1/B08-R2 | Closed | 0
08 | B07_Assessment | B08-P002 | B12B | Existing Condition | Basement B12B office/TE location, door, pathways, receptacles, panel source and penetrations | 0 | Paul | 0 | B08-R3 | Closed | 0
08 | B07_Assessment | B08-P003 | 2065A | Existing Condition | Second-floor TR 2065A room, door/walls/ceiling/floor, exterior furring/window, penetrations | 0 | Paul | 0 | B08-R4 | Closed | 0
08 | B07_Assessment | B08-P004 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B08-R7 | Closed | 0
08 | B07_Assessment | B08-P005 | 2065A | HVAC | IU-2-01/CU-2-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power | 0 | Paul | 0 | B08-R5 | Closed | 0
08 | B08_Assessment | B08-P006 | All | Electrical | B08-TR2065AA/AB panels, breakers, SPD, rack receptacles, TE receptacle B12B and labels | 0 | Paul | 0 | B08-R6 | Closed | 0
08 | B08_Assessment | B08-P007 | All | Telecom | B-15 legacy equipment, B12B TE schedule, 2065A racks, fiber, Cat6A, patch panels, LIU, labels and test records | 0 | Paul | 0 | B08-R2/B08-R8 | Closed | 0
08 | B08_Assessment | B08-P008 | All | Security | Card reader, electric strike, door position, CCTV/PACS and motion sensors | 0 | Paul | 0 | B08-R4 | Closed | 0
09 | B08_Assessment | B09-P001 | B01 | Existing Condition | Basement TR B01 existing telecom/security/network equipment, storage conditions, panels, ceiling, walls and pathways | 0 | Paul | 0 | B09-R1/B09-R2 | Closed | 0
09 | B08_Assessment | B09-P002 | 104B | Existing Condition | First-level TR 104B, walls/door/ceiling/floor, security devices, IU-1-01 location and pathways | 0 | Paul | 0 | B09-R1/B09-R4 | Closed | 0
09 | B08_Assessment | B09-P003 | 206A | Existing Condition | Second-level TR 206A, walls/door/ceiling/floor, adjacent Nursing Service 206, IU-2-01 location and pathways | 0 | Paul | 0 | B09-R1/B09-R4 | Closed | 0
09 | B08_Assessment | B09-P004 | All | Hazardous Materials | Flooring, ceilings, pipe insulation, penetrations and abatement-related locations before disturbance | 0 | Paul | 0 | B09-R3 | Closed | 0
09 | B08_Assessment | B09-P005 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B09-R7 | Closed | 0
09 | B09_Assessment | B09-P006 | All | HVAC | IU/CU equipment, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B09-R5 | Closed | 0
09 | B09_Assessment | B09-P007 | All | Electrical | B09 TR panels, breakers, SPD, rack receptacles, access controllers, lighting and labels | 0 | Paul | 0 | B09-R6 | Closed | 0
09 | B09_Assessment | B09-P008 | All | Telecom/Security | Racks, fiber, Cat6A, LIU, patch panels, labeling/testing, cameras, access control and VMS/PACS integration | 0 | Paul | 0 | B09-R8 | Closed | 0
10 | B09_Assessment | B10-P001 | 200A | Existing Condition | Attic TR 200A existing rack/equipment, floor/deck, walls, access route, pathways and clearances | 0 | Paul | 0 | B10-R1/B10-R3 | Closed | 0
10 | B09_Assessment | B10-P002 | 200A | Hazardous Materials | Attic abatement-related materials, flooring/penetrations, ceiling/deck and disturbance areas | 0 | Paul | 0 | B10-R2 | Closed | 0
10 | B09_Assessment | B10-P003 | B24 | Electrical | Existing normal electrical room panels, B10-MDP/B10-L10-E, feeder route and working clearances | 0 | Paul | 0 | B10-R5 | Closed | 0
10 | B09_Assessment | B10-P004 | B25 | Electrical | Existing emergency electrical room, ATS-B10-LSD/emergency distribution and access constraints | 0 | Paul | 0 | B10-R5 | Closed | 0
10 | B09_Assessment | B10-P005 | 200A | Firestop | All attic wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B10-R6 | Closed | 0
10 | B10_Assessment | B10-P006 | 200A | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B10-R4 | Closed | 0
10 | B10_Assessment | B10-P007 | 200A | Telecom | Racks, UPS/PDU, fiber, Cat6A, patch panels, LIU, bonding, labels and test records | 0 | Paul | 0 | B10-R7 | Closed | 0
10 | B10_Assessment | B10-P008 | 200A | Security | Card reader, electric strike, door position, CCTV/PACS, motion sensor and VMS/PACS integration | 0 | Paul | 0 | B10-R8 | Closed | 0
12 | B12_Assessment | B12-P001 | Fiber path B/1/2 | Existing Condition | Existing conduit/cable tray/pathway from entry through basement/first/second levels | 0 | Paul | 0 | B12-R2 | Closed | 0
12 | B12_Assessment | B12-P002 | Existing rack/demarc - field verify | Existing Condition | Existing rack, demarc, serving closet or fiber termination/pass-through point | 0 | Paul | 0 | B12-R5 | Closed | 0
12 | B12_Assessment | B12-P003 | All | Firestop | All floor/wall/sleeve penetrations before pull, during work, and after permanent firestop | 0 | Paul | 0 | B12-R4 | Closed | 0
12 | B12_Assessment | B12-P004 | All | Telecom | Fiber reels, pull route, pull boxes, labels, slack loops, termination points and test records | 0 | Paul | 0 | B12-R3/B12-R6 | Closed | 0
12 | B12_Assessment | B12-P005 | All | Closeout | Fiber certification/OTDR screenshots, labeling, as-built route and VA/OIT acceptance evidence | 0 | Paul | 0 | B12-R6 | Closed | 0
13 | B12_Assessment | B13-P001 | 124 | Existing Condition | Room 124 walls, ceiling/deck, floor, door, adjacent Telehealth 124A/109, rack location, pathways and penetrations | 0 | Paul | 0 | B13-R1/B13-R6 | Closed | 0
13 | B12_Assessment | B13-P002 | 222 | Existing Condition | Existing Tel Room 222 wall rack, telco patch, plywood backboard, AC unit, patch panel and security cabinet | 0 | Paul | 0 | B13-R1/B13-R3 | Closed | 0
13 | B12_Assessment | B13-P003 | 124 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B13-R2 | Closed | 0
13 | B12_Assessment | B13-P004 | 124 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B13-R6 | Closed | 0
13 | B12_Assessment | B13-P005 | 124 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B13-R4 | Closed | 0
13 | B13_Assessment | B13-P006 | 124 | Electrical | B13-TR124AA/AB panels, rack receptacles, breakers, SPD, access controller, lighting and labels | 0 | Paul | 0 | B13-R5 | Closed | 0
13 | B13_Assessment | B13-P007 | 124/222 | Telecom | New racks, fiber path A/B, Cat6A, patch panels, LIU, labels/test records and existing Room 222 transfer work | 0 | Paul | 0 | B13-R7 | Closed | 0
13 | B13_Assessment | B13-P008 | 124/222 | Security | 124-CAM-01, card reader, electric strike, door position, motion sensor, existing security cabinet and VMS/PACS integration | 0 | Paul | 0 | B13-R8 | Closed | 0
14 | B13_Assessment | B14-P001 | 119 | Existing Condition | Room 119 walls, ceiling/deck, floor, door, adjacent conference/restroom/office spaces, rack location, pathways and penetrations | 0 | Paul | 0 | B14-R1/B14-R6 | Closed | 0
14 | B13_Assessment | B14-P002 | B.01 | Existing Condition | Existing basement Tel/F Panel B.01, wall-mounted TE, patch panels, telco patch, plywood backboards, legacy Fiber LIU and pathways | 0 | Paul | 0 | B14-R1/B14-R3 | Closed | 0
14 | B13_Assessment | B14-P003 | B2 | Existing Condition | Existing basement telecom room B2 photo reference, equipment, pathways, power and protection-in-place needs | 0 | Paul | 0 | B14-R1/B14-R3 | Closed | 0
14 | B13_Assessment | B14-P004 | 119 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B14-R2 | Closed | 0
14 | B13_Assessment | B14-P005 | 119 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B14-R6 | Closed | 0
14 | B14_Assessment | B14-P006 | 119 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B14-R4 | Closed | 0
14 | B14_Assessment | B14-P007 | 119 | Electrical | B14-TR119A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B14-R5 | Closed | 0
14 | B14_Assessment | B14-P008 | 119/B.01 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 119-CAM-01 and existing B.01/B2 transfer work | 0 | Paul | 0 | B14-R7/B14-R8 | Closed | 0
15 | B14_Assessment | B15-P001 | 124A | Existing Condition | Room 124A walls, ceiling/deck, floor, door, adjacent Office 124/Office 109/HAC 123, rack location, pathways and penetrations | 0 | Paul | 0 | B15-R1/B15-R6 | Closed | 0
15 | B14_Assessment | B15-P002 | 222 | Existing Condition | Existing Tel Room 222 wall rack, Cisco switches, legacy patch panels, indoor AC unit, security cabinet, ground bar, plywood backboard and floor UPS | 0 | Paul | 0 | B15-R1/B15-R3 | Closed | 0
15 | B14_Assessment | B15-P003 | B01 | Existing Condition | Existing basement telecom/crossover B01, legacy 24-port patch panel, pathway, power and protection-in-place needs | 0 | Paul | 0 | B15-R1/B15-R3 | Closed | 0
15 | B14_Assessment | B15-P004 | 124A | Hazardous Materials | First-level abatement-related materials, lead-based paint/door frames, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B15-R2 | Closed | 0
15 | B14_Assessment | B15-P005 | 124A | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B15-R6 | Closed | 0
15 | B15_Assessment | B15-P006 | 124A | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B15-R4 | Closed | 0
15 | B15_Assessment | B15-P007 | 124A | Electrical | B15-TR124AA/AB panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B15-R5 | Closed | 0
15 | B15_Assessment | B15-P008 | 124A/222/B01 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 124A-CAM-1 and existing 222/B01 transfer work | 0 | Paul | 0 | B15-R7/B15-R8 | Closed | 0
16 | B15_Assessment | B16-P001 | 015 | Existing Condition | Room 015 walls, ceiling/deck, floor, door, adjacent Vacant 011/012/013, Stair 014, Water Heater 010, rack location, pathways and penetrations | 0 | Paul | 0 | B16-R1/B16-R3 | Closed | 0
16 | B15_Assessment | B16-P002 | 014 | Existing Condition | Existing Telecom Room 014 wall rack/TE, Cisco switch, legacy 12-port patch panel, Fiber LIU, floor UPS, plywood backboard and security cabinet | 0 | Paul | 0 | B16-R1/B16-R2 | Closed | 0
16 | B15_Assessment | B16-P003 | 015 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B16-R6 | Closed | 0
16 | B15_Assessment | B16-P004 | 015 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B16-R4 | Closed | 0
16 | B15_Assessment | B16-P005 | 015 | Electrical | B16-TR015A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B16-R5 | Closed | 0
16 | B16_Assessment | B16-P006 | 015/014 | Telecom | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records and existing Room 014 transfer work | 0 | Paul | 0 | B16-R7 | Closed | 0
16 | B16_Assessment | B16-P007 | 015/014 | Security | 015-CAM-1, card reader, electric strike, door position, motion sensor, existing security cabinet and VMS/PACS integration | 0 | Paul | 0 | B16-R8 | Closed | 0
16 | B16_Assessment | B16-P008 | All | Cable Tray / Pathway | Basement and first-level cable tray/pathway route, supports, fill, firestopping and seismic bracing | 0 | Paul | 0 | B16-R3/B16-R7 | Closed | 0
17 | B16_Assessment | B17-P001 | 118 | Existing Condition | Room 118 walls, ceiling/deck, floor, door, adjacent Lab/Freezer/Research/Corridor areas, rack location, pathways and penetrations | 0 | Paul | 0 | B17-R1/B17-R2 | Closed | 0
17 | B16_Assessment | B17-P002 | B35A | Existing Condition | Existing Telecom Closet B35A wall TE, SERTEX service ports, legacy patch panels, Cisco switches, security cabinet, plywood backboard, indoor AC and floor UPS | 0 | Paul | 0 | B17-R1/B17-R3 | Closed | 0
17 | B16_Assessment | B17-P003 | B29 Path | Pathway | Path to B29 4-inch PVC, fiber route, penetrations, handoff points and labeling | 0 | Paul | 0 | B17-R6/B17-R7 | Closed | 0
17 | B16_Assessment | B17-P004 | 118 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B17-R2 | Closed | 0
17 | B16_Assessment | B17-P005 | 118/B29 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop, including B29 pathway | 0 | Paul | 0 | B17-R6 | Closed | 0
17 | B17_Assessment | B17-P006 | 118 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B17-R4 | Closed | 0
17 | B17_Assessment | B17-P007 | 118 | Electrical | B17-TR118A/B panels, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B17-R5 | Closed | 0
17 | B17_Assessment | B17-P008 | 118/B35A/B29 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 118-CAM-01 and existing B35A transfer work | 0 | Paul | 0 | B17-R7/B17-R8 | Closed | 0
18 | B17_Assessment | B18-P001 | 110 | Existing Condition | Room 110 walls, ceiling/deck, floor, door, adjacent Corridor 121/Stair 122/Office 112, rack location, pathways and penetrations | 0 | Paul | 0 | B18-R1/B18-R2 | Closed | 0
18 | B17_Assessment | B18-P002 | 111B | Existing Condition | Existing TE 111B wall rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber housing | 0 | Paul | 0 | B18-R1/B18-R3 | Closed | 0
18 | B17_Assessment | B18-P003 | 213 | Existing Condition | Existing Closet 213 wall rack/TE, SERTEX service ports, Cisco switch, legacy Ortronics patch panels, security cabinet, plywood backboard and APC floor UPS | 0 | Paul | 0 | B18-R1/B18-R3 | Closed | 0
18 | B17_Assessment | B18-P004 | 110 | Hazardous Materials | First-level abatement/lead-paint areas, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B18-R2 | Closed | 0
18 | B17_Assessment | B18-P005 | 110 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B18-R6 | Closed | 0
18 | B18_Assessment | B18-P006 | 110 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B18-R4 | Closed | 0
18 | B18_Assessment | B18-P007 | 110 | Electrical | B18-TR110A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B18-R5 | Closed | 0
18 | B18_Assessment | B18-P008 | 110/111B/213 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 111A-CAM-01 and existing 111B/213 transfer work | 0 | Paul | 0 | B18-R7/B18-R8 | Closed | 0
20 | B18_Assessment | B20-P001 | 1B | Existing Condition | Office 1B wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B20-R1/B20-R3 | Closed | 0
20 | B18_Assessment | B20-P002 | 8A | Existing Condition | Existing Tel/Data Closet 8A open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard and cable entries | 0 | Paul | 0 | B20-R1/B20-R2 | Closed | 0
20 | B18_Assessment | B20-P003 | 8A | Existing Equipment | BIX blocks, Cisco switch, legacy Ortronics 48-port patch panel, UPS on ground and Fiber LIU on wall | 0 | Paul | 0 | B20-R2/B20-R5 | Closed | 0
20 | B18_Assessment | B20-P004 | 1B/8A | Pathway | 459 ft Level 1 cable tray route, sleeves, wall penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B20-R6/B20-R7 | Closed | 0
20 | B18_Assessment | B20-P005 | 1B | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and disconnect/access | 0 | Paul | 0 | B20-R5 | Closed | 0
20 | B20_Assessment | B20-P006 | 1B/8A | Telecom | TE01-1B-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B20-R2/B20-R8 | Closed | 0
20 | B20_Assessment | B20-P007 | All | Firestop | 4-inch speed sleeve, wall penetrations and fire caulk before/after photos | 0 | Paul | 0 | B20-R7 | Closed | 0
20 | B20_Assessment | B20-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B20-R8 | Closed | 0
21 | B20_Assessment | B21-P001 | 100A | Existing Condition | M&O Foreman Office 100A wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B21-R1/B21-R3 | Closed | 0
21 | B20_Assessment | B21-P002 | B1.TR | Existing Condition | Existing B21 basement B1.TR wall TE, legacy patch panels, Cisco switch, Fiber LIU, UPS on ground and cable entries | 0 | Paul | 0 | B21-R1/B21-R2 | Closed | 0
21 | B20_Assessment | B21-P003 | B05TR | Existing Condition | Existing B19 B05TR basement and first-level TE/equipment, APC floor UPS, Cisco switch, patch panels, Fiber LIU and pathways | 0 | Paul | 0 | B21-R1/B21-R4 | Closed | 0
21 | B20_Assessment | B21-P004 | 100A/B05TR/B1.TR | Pathway | 659 ft cable tray route, sleeves, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B21-R6/B21-R7 | Closed | 0
21 | B20_Assessment | B21-P005 | 100A | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B21-R5 | Closed | 0
21 | B21_Assessment | B21-P006 | 100A/B1.TR/B05TR | Telecom | TR01-104-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B21-R2/B21-R8 | Closed | 0
21 | B21_Assessment | B21-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B21-R7 | Closed | 0
21 | B21_Assessment | B21-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B21-R8 | Closed | 0
22 | B21_Assessment | B22-P001 | 102 | Existing Condition | Break Room 102 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B22-R1/B22-R3 | Closed | 0
22 | B21_Assessment | B22-P002 | 103 | Existing Condition | Existing Room 103 wall/wall-mount TE, APC UPS, Cisco switch, SERTEX utility service, legacy patch panel, Fiber LIU and cable entries | 0 | Paul | 0 | B22-R1/B22-R2 | Closed | 0
22 | B21_Assessment | B22-P003 | 103 / B19 | Existing Equipment | Ports 1-24 to Building 19 ports 73-96, active service labeling, utility service and handoff condition | 0 | Paul | 0 | B22-R8 | Closed | 0
22 | B21_Assessment | B22-P004 | 102/103 | Pathway | 139 ft first-floor cable tray route, sleeves, wall penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B22-R6/B22-R7 | Closed | 0
22 | B21_Assessment | B22-P005 | 102 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B22-R5 | Closed | 0
22 | B22_Assessment | B22-P006 | 102/103 | Telecom | TR01-102-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B22-R2/B22-R8 | Closed | 0
22 | B22_Assessment | B22-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B22-R7 | Closed | 0
22 | B22_Assessment | B22-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B22-R8 | Closed | 0
33 | B22_Assessment | B33-P001 | B23 | Existing Condition | EEO Manager Office B23 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B33-R1/B33-R3 | Closed | 0
33 | B22_Assessment | B33-P002 | B17 | Existing Condition | Existing Tel Closet B17 open TE cabinet, network door controller, indoor AC unit, plywood backboard, keypad, patch panel, ground bar and equipment box | 0 | Paul | 0 | B33-R1/B33-R2 | Closed | 0
33 | B22_Assessment | B33-P003 | B17 | Existing Equipment | Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, Fiber LIU, UPS on floor and cross-building port labels | 0 | Paul | 0 | B33-R2/B33-R8 | Closed | 0
33 | B22_Assessment | B33-P004 | B23/B17 | Pathway | 102 ft basement cable tray route, 4-inch sleeve, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B33-R6/B33-R7 | Closed | 0
33 | B22_Assessment | B33-P005 | B23 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B33-R5 | Closed | 0
33 | B33_Assessment | B33-P006 | B23/B17 | Telecom | TE01-B23-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing B17 equipment transfer | 0 | Paul | 0 | B33-R2/B33-R8 | Closed | 0
33 | B33_Assessment | B33-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B33-R7 | Closed | 0
33 | B33_Assessment | B33-P008 | B17/B23 | Security / Existing Devices | Existing cameras, network door controller, keypad and equipment box to remain/protect or be recabled | 0 | Paul | 0 | B33-R8 | Closed | 0
61 | B33_Assessment | B61-P001 | B13H-A | Existing Condition | Basement TR B13H-A walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B61-R1/B61-R2 | Closed | 0
61 | B33_Assessment | B61-P002 | 124 | Existing Condition | First-level TR 124 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B61-R1/B61-R4 | Closed | 0
61 | B33_Assessment | B61-P003 | 226 | Existing Condition | Second-level TR 226 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and riser penetrations | 0 | Paul | 0 | B61-R1/B61-R4 | Closed | 0
61 | B33_Assessment | B61-P004 | 137 / 137A | Existing Equipment | Existing server/demarc racks, APC UPS/PDU, Fujitsu equipment, patch panels, PACS/equipment racks and cable entries | 0 | Paul | 0 | B61-R3/B61-R7 | Closed | 0
61 | B33_Assessment | B61-P005 | All TRs | HVAC | IU/CU-0-01, IU/CU-1-01, IU/CU-2-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B61-R4 | Closed | 0
61 | B61_Assessment | B61-P006 | All TRs | Electrical | B61 telecom panels, PD panels, rack receptacles, UPS/PDU, breakers, SPDs, labels and grounding/bonding | 0 | Paul | 0 | B61-R5 | Closed | 0
61 | B61_Assessment | B61-P007 | All | Cable Tray / Firestop | Basement/first/second cable tray route, supports, seismic bracing, penetrations and before/after firestopping | 0 | Paul | 0 | B61-R6 | Closed | 0
61 | B61_Assessment | B61-P008 | All | Telecom / Security | Racks, Fiber LIU, Cat6A, patch panels, labels/test records, CCTV, PACS and existing equipment transfer work | 0 | Paul | 0 | B61-R7/B61-R8 | Closed | 0
62 | B62_TR_Assessment | B62-P001 | B24A | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0
62 | B62_TR_Assessment | B62-P002 | 125 | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0
62 | B62_TR_Assessment | B62-P003 | 225 | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0
62 | B62_TR_Assessment | B62-P004 | All | Firestop | Penetration/firestopping photo | 0 | Paul | 0 | B62-R2 | Closed | 0
70 | B70_TR_Assessment | B70-P001 | B27 | Existing Condition | Existing basement TR / utility condition | 0 | Paul | 0 | B70-R3 | Closed | 0
70 | B70_TR_Assessment | B70-P002 | 125A | Existing Condition | Existing first-floor TR condition | 0 | Paul | 0 | 0 | Closed | 0
70 | B70_TR_Assessment | B70-P003 | 262A | Existing Condition | Existing second-floor TR condition | 0 | Paul | 0 | 0 | Closed | 0
70 | B70_TR_Assessment | B70-P004 | All | Firestop | Penetration/firestopping photo | 0 | Paul | 0 | B70-R2 | Closed | 0
70 | B70_TR_Assessment | B70-P005 | All | HVAC | Cooling unit/condensate photo | 0 | Paul | 0 | B70-R1/B70-R5 | Closed | 0
78 | B70_TR_Assessment | B78-P001 | B30 | Existing Condition | Basement RM B30 walls, ceiling/deck, floor, door, racks/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B78-R1/B78-R6 | Closed | 0
78 | B70_TR_Assessment | B78-P002 | B35 | Existing Condition | Basement RM B35 and relationship to existing telecom room 15E; rack/equipment, pathway, power, HVAC and penetrations | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B70_TR_Assessment | B78-P003 | 1232 / 1234 | Existing Condition | First-level RM 1232/new TR and existing telecom room 1234 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B70_TR_Assessment | B78-P004 | 227A / 1234 | Existing Condition | Second-level RM 227A/new TR and existing telecom room 1234 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B70_TR_Assessment | B78-P005 | 342 / 353 | Existing Condition | Third-level RM 342/new TR and existing telecom room 353 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B78_Assessment | B78-P006 | 401 / 308A / 408A | Existing Condition | Fourth-level RM 401 and existing telecom rooms 308A/408A photo references, active equipment, cable paths and transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B78_Assessment | B78-P007 | All | Cable Tray / Firestop | Basement through fourth-level cable tray routes, supports, seismic bracing, penetrations and before/after firestopping | 0 | Paul | 0 | B78-R6 | Closed | 0
78 | B78_Assessment | B78-P008 | All | Telecom / Security / HVAC | Racks, Fiber LIU, Cat6A, patch panels, UPS/PDU, labels/test records, CCTV, PACS, HVAC units and existing transfer work | 0 | Paul | 0 | B78-R4/B78-R7/B78-R8 | Closed | 0
80 | B78_Assessment | B80-P001 | 102 | Existing Condition | Room 102 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, fiber path A/B, cable tray and penetrations | 0 | Paul | 0 | B80-R1/B80-R4 | Closed | 0
80 | B78_Assessment | B80-P002 | 127A / 126 | Existing Condition | Existing Tel Closet/telecom room with plywood backboard, ground bar, patch panel, equipment box, two-post rack/wall TE and cable entries | 0 | Paul | 0 | B80-R1/B80-R2 | Closed | 0
80 | B78_Assessment | B80-P003 | 127A / 126 | Existing Equipment | Cisco switches, legacy Fiber LIU, Ortronics patch panels, Cat5e patch panel, APC floor UPS and active service labels | 0 | Paul | 0 | B80-R2/B80-R3 | Closed | 0
80 | B78_Assessment | B80-P004 | 102 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B80-R4 | Closed | 0
80 | B78_Assessment | B80-P005 | 102 | Electrical | B80-TR102A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B80-R5 | Closed | 0
80 | B80_Assessment | B80-P006 | All | Cable Tray / Firestop | Basement and first-level cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B80-R6 | Closed | 0
80 | B80_Assessment | B80-P007 | 102 / 127A | Telecom | New rack/future rack, Fiber LIU, Cat6A, patch panels, labels/test records and existing rack transfer work | 0 | Paul | 0 | B80-R7 | Closed | 0
80 | B80_Assessment | B80-P008 | 102 | Security | 102-CAM-1, card reader, electric strike, door position, motion sensor, existing security devices and VMS/PACS integration | 0 | Paul | 0 | B80-R8 | Closed | 0
82 | B80_Assessment | B82-P001 | 102 | Existing Condition | Room 102 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B82-R1/B82-R3 | Closed | 0
82 | B80_Assessment | B82-P002 | B01-A | Existing Condition | Existing first-level telecom room B01-A wall rack, Cisco switches, cable management, Ortronics patch panels, APC floor UPS and cable entries | 0 | Paul | 0 | B82-R1/B82-R2 | Closed | 0
82 | B80_Assessment | B82-P003 | 102 / B01-A | Pathway | 278 ft first-level cable tray route, 4-inch sleeve, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B82-R6/B82-R7 | Closed | 0
82 | B80_Assessment | B82-P004 | 102 | HVAC | IU-1-01/CU-1-01, condensate pump/path, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B82-R4 | Closed | 0
82 | B80_Assessment | B82-P005 | 102 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, B82-MDP/B82-P-EMER connections, grounding/bonding, SPD, labels and access | 0 | Paul | 0 | B82-R5 | Closed | 0
82 | B82_Assessment | B82-P006 | 102 / B01-A | Telecom | TR01-102-01 enclosure, cross-connect/cutover cabling, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B82-R2/B82-R8 | Closed | 0
82 | B82_Assessment | B82-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B82-R7 | Closed | 0
82 | B82_Assessment | B82-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B82-R8 | Closed | 0
BCH | B82_Assessment | BCH-P001 | 107 | Existing Condition | Room 107 walls, ceiling, floor, wall backing, clearances, existing devices, power source, cable path, and proposed TE/rack location | 0 | Paul | 0 | BCH-R1/BCH-R3 | Closed | 0
BCH | B82_Assessment | BCH-P002 | 107 | Electrical | Panel/source, receptacles, UPS/PDU location, grounding/bonding bar, labels and access clearance | 0 | Paul | 0 | BCH-R5 | Closed | 0
BCH | B82_Assessment | BCH-P003 | 107 | Telecom | 12RU enclosure or rack location, Fiber LIU, patch panel, network switch, Cat6A terminations, labels and test records | 0 | Paul | 0 | BCH-R3/BCH-R8 | Closed | 0
BCH | B82_Assessment | BCH-P004 | 107 | Pathway | Cable tray route, 4-inch sleeves, wall/floor penetrations, support points and 40% fill concerns | 0 | Paul | 0 | BCH-R6/BCH-R7 | Closed | 0
BCH | B82_Assessment | BCH-P005 | 107 | Firestop | Rated penetrations, fire caulk and temporary/final firestopping before/after photos | 0 | Paul | 0 | BCH-R7 | Closed | 0
BCH | BCH_Assessment | BCH-P006 | 107 | HVAC / Existing Environment | Existing room cooling/ventilation and ambient condition for TE equipment | 0 | Paul | 0 | BCH-R2/BCH-R5 | Closed | 0
BCH | BCH_Assessment | BCH-P007 | 107 | Security / CCTV | Camera location, existing/security devices, VMS integration, access conditions and protection-in-place | 0 | Paul | 0 | BCH-R8 | Closed | 0
BCH | BCH_Assessment | BCH-P008 | All | Off-site Coordination | Site access, staging, ICRA/dust control, work area barriers and temporary service conditions | 0 | Paul | 0 | BCH-R1/BCH-R4 | Closed | 0
MCR | BCH_Assessment | MCR-P001 | MCR 107 | Existing / New Condition | Full room envelope, doors, rated walls, ceiling/roof, floors, row layout, UPS-A/B, MDA/HDA, access points and cameras | 0 | Paul | 0 | MCR-R1/MCR-R6 | Closed | 0
MCR | BCH_Assessment | MCR-P002 | 031 | Fiber Entrance | Fiber Entrance Room 1, outlet locations 31-A/B/C/D, rack/cabinet location, sleeve/firestop and service entrance pathways | 0 | Paul | 0 | MCR-R3 | Closed | 0
MCR | BCH_Assessment | MCR-P003 | MDA-A/B | Rack / Fiber | MDA-A1/A2/A3 and MDA-B1/B2/B3 rack fronts/rears, LIUs, hybrid FOC, Cat6A to HDA, grounding and cable management | 0 | Paul | 0 | MCR-R3/MCR-R4 | Closed | 0
MCR | BCH_Assessment | MCR-P004 | HDA-A/B | Rack / Server Cabinets | HDA-A1/HDA-B1 front/rear, patch panels, HD LIUs, cabinet blanking panels, server cabinet airflow and labels | 0 | Paul | 0 | MCR-R3/MCR-R5 | Closed | 0
MCR | BCH_Assessment | MCR-P005 | Existing 107/137 | Existing Equipment | Existing rows 1-3 and B61 server cabinet transfer equipment, Cisco core, WAN aggregation, NetScout, Canoga, Ortronics, LIUs, UPS/PDU labels | 0 | Paul | 0 | MCR-R2 | Closed | 0
MCR | MCR_Assessment | MCR-P006 | MCR / Electrical | Electrical / UPS | UPS-A/B, switchboards, panels, ATS, generator tie, PDUs, rack receptacles, grounding, SPDs and load measurement labels | 0 | Paul | 0 | MCR-R4 | Closed | 0
MCR | MCR_Assessment | MCR-P007 | MCR / Mechanical | HVAC / Controls | CRAC units, condensate, controls/BACnet/BMS/FMS points, alarms, environmental monitoring and emergency power source | 0 | Paul | 0 | MCR-R5 | Closed | 0
MCR | MCR_Assessment | MCR-P008 | MCR / Life Safety | Fire / Security | Clean-agent cylinders/piping/nozzles, preaction/sprinkler, fire alarm, release/abort devices, cameras 07-CAM series, PACS/controller and door hardware | 0 | Paul | 0 | MCR-R6/MCR-R8 | Closed | 0
SITE | MCR_Assessment | SITE-P001 | Overall Site | Existing Conditions | Campus-wide route photos before excavation, including pavement, sidewalks, landscaping, parking, fire lanes and building entry areas | 0 | 0 | 0 | SITE-R1/SITE-R5 | Closed | 0
SITE | MCR_Assessment | SITE-P002 | THH #1-#19 | Structures | Each handhole/manhole/pullbox location, cover, label, depth, drainage, conduit entry, and final installed condition | 0 | 0 | 0 | SITE-R2/SITE-R8 | Closed | 0
SITE | MCR_Assessment | SITE-P003 | Ductbank | Pre-pour Inspection | Conduit count, separation, supports/spacers, depth, utility crossings, warning tape, pull strings and concrete encasement before pour | 0 | 0 | 0 | SITE-R1/SITE-R3 | Closed | 0
SITE | MCR_Assessment | SITE-P004 | Utility Crossings | Existing Utilities | Potholing/hand-dig photos showing electric, storm, sanitary, water, gas/unknown utilities and clearance to new ductbank | 0 | 0 | 0 | SITE-R1 | Closed | 0
SITE | MCR_Assessment | SITE-P005 | Building Tie-ins | Penetrations / Firestop | Exterior entry points, wall/floor penetrations, sleeves, firestop, weatherproofing and interior continuation to building TR/TE | 0 | 0 | 0 | SITE-R6 | Closed | 0
SITE | SITE_Assesment | SITE-P006 | Fiber Pull / Testing | Telecom | Fiber reels, pull setup, mandrel/rope, splice/termination points, labels, OTDR/power meter screenshots and OIT acceptance | 0 | 0 | 0 | SITE-R8 | Closed | 0
SITE | SITE_Assesment | SITE-P007 | Restoration | Civil | Asphalt/concrete trench patches, sidewalk panels, landscaping, turf, drainage, curb/edge details and final cleanup | 0 | 0 | 0 | SITE-R5/SITE-R7 | Closed | 0
SITE | SITE_Assesment | SITE-P008 | MCR / Provider Entrance | Critical Cutover | Provider handoff, WAN fiber route, temporary fiber, Path A/B into MCR and activation/cutover coordination photos | 0 | 0 | 0 | SITE-R4/SITE-R8 | Closed | 0
MAPPED READINESS SCORES — FORMULA-FED FROM BUILDING SHEETS
Building | Sheet | Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
01 | B01_Assessment | 107 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Green | New first-level TR with 161 total ports including allowance, dedicated cooling, UPS/PDU, B01-TR107A/B panels, cable tray, PACS/CCTV and fire/life-safety scope.
01 | B01_Assessment | B02 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Green | Existing basement telecom transition point; protect active services until transfer/cutover complete.
01 | B01_Assessment | 138 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Green | Existing first-level telecom transition point; protect active services and verify final condition.
01 | B01_Assessment | 282 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Green | Existing second-level telecom transition point; protect active services and verify final condition.
02 | B02_Assessment | 141 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with 354 total ports including allowance, 2 rack IDs, B02-TR141A/B panels, high cable tray volume and existing room transfer scope.
02 | B02_Assessment | 236 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR with approx. 345 total ports including allowance, B02-TR236A/B panels, camera/PACS and existing transition scope.
02 | B02_Assessment | 342 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Third-level TR with 388 total ports including allowance, B02-TR342A/B panels, camera/security and high WAO count.
02 | B02_Assessment | B-06 / existing rooms | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing telecom transition points; protect active services until transfer/cutover complete.
03 | B03_Assessment | 101E | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Primary first-level TR with 206 total ports including allowance, two rack IDs, B03-TR101CA/B panels, CU-01, 961 ft cable tray and existing 107/101C transfer scope.
03 | B03_Assessment | 107 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom transition point; protect active services until transfer/cutover complete.
03 | B03_Assessment | 101C | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing first-floor DMARC/telecom transition point; protect provider/fiber/active services and verify final condition.
03 | B03_Assessment | WAO Areas | 50% | 50% | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement and first-level WAO/WAP/camera recabling served from Room 101E.
04 | B04_Assessment | B05 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Two-rack basement TR; full field verification required.
04 | B04_Assessment | 141 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-floor TR with rated wall/door and future rack.
04 | B04_Assessment | 244A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-floor TR/panel scope; verify rack/equipment locations.
05 | B05_Assessment | 150 | 50% | 50% | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New 12RU TE; field verification required.
05 | B05_Assessment | 153-A | 50% | 50% | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing TE/legacy equipment transition point.
06 | B06_Assessment | B-01 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing equipment transition point; protect active services.
06 | B06_Assessment | 178 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-floor TR with new cooling and electrical scope.
06 | B06_Assessment | 233 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-floor TR/Data Closet with rated construction and future rack scope.
07 | B07_Assessment | B-18 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR; field verification required.
07 | B07_Assessment | 228A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-floor TR; rated wall/door and cooling coordination required.
08 | B08_Assessment | B-15 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing equipment transition point; protect active services.
08 | B08_Assessment | B12B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement office/TE ambiguity requires field verification.
08 | B08_Assessment | 2065A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New second-floor TR with two racks, cooling, rated work and possible abatement.
09 | B09_Assessment | B01 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR with existing equipment and multiple panel/cooling dependencies.
09 | B09_Assessment | 104B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with security/access control, cooling and rated wall/door coordination.
09 | B09_Assessment | 206A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR adjacent to Nursing Service with cooling, electrical and fire/life-safety coordination.
10 | B10_Assessment | 200A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Attic TR with rack/equipment, cooling, electrical, fire/life-safety and abatement coordination.
10 | B10_Assessment | B24 | 50% | 50% | N/A | 0.5 | N/A | Verify | 0.5 | Partial / Yellow | Normal electrical source coordination only.
10 | B10_Assessment | B25 | 50% | 50% | N/A | 0.5 | N/A | Verify | 0.5 | Partial / Yellow | Emergency electrical source coordination only.
12 | B12_Assessment | Fiber path B/1/2 | 60% | 50% | N/A | N/A | 0.6 | Verify | 0.55 | Partial / Yellow | Fiber-only pathway and cutover must be field verified.
12 | B12_Assessment | Existing rack/demarc - field verify | 50% | 50% | N/A | N/A | 0.6 | Verify | 0.53 | Partial / Yellow | Existing service point/termination requires field confirmation.
13 | B13_Assessment | 124 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with two racks, future rack, 240V UPS, cooling, access control and fire/life-safety coordination.
13 | B13_Assessment | 222 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing second-level tel room and transition point; protect active services until cutover complete.
14 | B14_Assessment | 119 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 240V UPS, cooling, access control, cable tray and fire/life-safety coordination.
14 | B14_Assessment | B.01 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement tel/fiber panel room and transition point; protect active services until cutover complete.
14 | B14_Assessment | B2 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom room reference; field verify scope and active status.
15 | B15_Assessment | 124A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 240V UPS, heat-pump cooling, access control, cable tray and fire/life-safety coordination.
15 | B15_Assessment | 222 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing second-level tel room and transition point; protect active services until cutover complete.
15 | B15_Assessment | B01 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom/crossover room; field verify scope and active status.
16 | B16_Assessment | 015 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New basement TR with one rack plus future rack, 240V UPS, cooling, access control, cable tray and fire/life-safety coordination.
16 | B16_Assessment | 014 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom room and transition point; protect active services until cutover complete.
17 | B17_Assessment | 118 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 208V UPS, cooling, access control, 517 ft cable tray and B29 service coordination.
17 | B17_Assessment | B35A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom closet and transition point; protect active services until cutover complete.
17 | B17_Assessment | B29 Path | 50% | 50% | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Building 29 served from B17; verify pathway, fiber, labeling, test records and PMIS mapping.
18 | B18_Assessment | 110 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 208V UPS, cooling, access control, 315 ft cable tray and fire/life-safety coordination.
18 | B18_Assessment | 111B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing first-level TE and transition point; protect active services until cutover complete.
18 | B18_Assessment | 213 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing second-level telecom closet and transition point; protect active services until cutover complete.
20 | B20_Assessment | 1B | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level Office TE with 12RU wall enclosure, UPS/PDU, 459 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
20 | B20_Assessment | 8A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Tel/Data Closet and transition point; protect active services until cutover complete.
21 | B21_Assessment | 100A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TE with 12RU wall enclosure, UPS/PDU, 659 ft cable tray, fiber/copper cutover and B19/B21 room naming coordination.
21 | B21_Assessment | B1.TR | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Building 21 basement telecom transition point; protect active services until cutover complete.
21 | B21_Assessment | B05TR | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Building 19 telecom transition point tied into Building 21 scope; confirm shared service boundary.
22 | B22_Assessment | 102 | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level Break Room TE with 12RU wall enclosure, UPS/PDU, 139 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
22 | B22_Assessment | 103 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing wall/wall-mount TE and transition point; protect active services until cutover complete.
33 | B33_Assessment | B23 | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New basement office TE with 12RU wall enclosure, UPS/PDU, 102 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
33 | B33_Assessment | B17 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Tel Closet and transition point; protect active services until cutover complete.
61 | B61_Assessment | B13H-A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR with 142 total ports including allowance, dedicated cooling, UPS/PDU, cable tray and fire/life-safety scope.
61 | B61_Assessment | 124 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with dedicated cooling, UPS/PDU, cable tray and potential electrical room-name mapping issue.
61 | B61_Assessment | 226 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR with 172 total ports including allowance, dedicated cooling, UPS/PDU and riser/firestop coordination.
61 | B61_Assessment | 137 / 137A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing demarc/server room inventory; protect active services until cutover and acceptance complete.
62 | B62_TR_Assessment | B24A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
62 | B62_TR_Assessment | 125 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
62 | B62_TR_Assessment | 225 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
70 | B62_TR_Assessment | B27 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
70 | B62_TR_Assessment | 125A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
70 | B62_TR_Assessment | 262A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
70 | B62_TR_Assessment | SOURCE / DRAWING REVIEW NOTES | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Source package | 518-22-700.Bedford.EHRM.IFC.B70.20260316.pdf | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | TR locations identified | B27 basement, 125A first floor, 262A second floor based on architectural, fire protection, mechanical, and telecom drawing references. | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Fire protection basis | Building 70 is fully sprinklered. TRs require sprinkler modifications, fire alarm devices, extinguisher coverage within 75 feet, and firestopping at penetrations. | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | HVAC basis | New indoor units, condensate routing, thermostat, and BACnet adapter are noted for TR spaces; emergency power and operational continuity should be field verified. | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Telecom basis | TR rack elevations show 1 rack plus future rack at B-27, 125-A, and 262-A with UPS/PDU/cable management/grounding requirements. | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Based on the Building 70 IFC review, the telecom scope is very similar to Building 62, but Building 70 appears to have three TRs (B27, 125A, and 262A) instead of a single room. The project introduces new racks, UPS equipment, dedicated cooling, fire alarm modifications, sprinkler modifications, grounding, cable management, and access control while maintaining hospital operations. | Telecom Room Build | Not Started | 0 | 0 | 🟡 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Building 70 – Telecom Room Infrastructure Scope | UPS Installation | Not Started | 1 | 0 | 🟢 | -1 | 0 | 0 | 0
70 | B62_TR_Assessment | Existing Conditions Survey | Firestopping | Not Started | 1 | 0 | 🟢 | -1 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify existing conditions of TR-B27, TR-125A, and TR-262A. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Document existing racks, power, HVAC, fire protection, grounding, and pathway systems. | 13. OIT ACTIVATION READINESS | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Photograph all existing conditions. | Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref. | 0 | 0
70 | B62_TR_Assessment | Verify existing active services and identify systems requiring uninterrupted operation. | Telecom Room Complete | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify room dimensions and equipment clearances. | Rack Installed | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Architectural | UPS Operational | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Prepare rooms for new telecom infrastructure. | National OIT Approval | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Patch and repair walls, ceilings, and penetrations as required. | Local OIT Ready | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Maintain or restore all fire-rated assemblies. | Activation Scheduled | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify door hardware, access control, and room security. | OIT Readiness | 0% |  | 0 | Success: Required OIT activation prerequisites are complete or formally coordinated. | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Label rooms and equipment per VA standards. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Fire Protection | Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence | 0 | 0
70 | B62_TR_Assessment | Verify sprinkler coverage within each TR. | Cable Tray | Not Started | No | No | No | Pending | 0 | 0 | 0
70 | B62_TR_Assessment | Reconfigure sprinkler piping and heads where required. | Firestop System | Not Started | No | No | No | Pending | 0 | 0 | 0
70 | B62_TR_Assessment | Verify no obstructions to sprinkler discharge. | HVAC Equipment | Not Started | No | No | No | Pending | 0 | 0 | 0
70 | B62_TR_Assessment | Provide fire extinguisher cabinet and clean-agent or CO₂ extinguisher within 75 feet of each TR. | Electrical Equipment | Not Started | No | No | No | Pending | 0 | 0 | 0
70 | B62_TR_Assessment | Firestop all penetrations through rated assemblies. | Inspection Compliance | 0% | 0 | 0 | Success: Installed materials match approved submittals and deficiencies are documented. | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify compliance with NFPA 13 and VA Fire Protection Design Manual requirements. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Fire Alarm | Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause | 0 | 0
70 | B62_TR_Assessment | Verify smoke detection coverage. | Telecom | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0
70 | B62_TR_Assessment | Verify horn/strobe coverage. | Mechanical | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0
70 | B62_TR_Assessment | Coordinate relocation or addition of devices as required. | Firestop | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0
70 | B62_TR_Assessment | Verify monitoring and reporting through existing fire alarm systems. | Contractor Performance | 0% | 0 | 0 | Success: Actual production is on or above baseline, or delay cause is documented. | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Test and document final operation. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Mechanical / HVAC | Requirement | Status | Required | Complete | Score | Comments | Evidence Ref. | 0 | 0
70 | B62_TR_Assessment | Verify dedicated cooling units serving each telecom room. | QA/QC Complete | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify thermostat installation. | Deficiencies Closed | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify BACnet integration and controls. | OIT Ready | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify condensate routing and drainage. | Documentation Complete | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify emergency power requirements for cooling equipment. | Recommended for Acceptance | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify continuous cooling capability during hospital operations. | Acceptance Readiness | 0% | 0 | 0 | Success: Building is ready for turnover when all required gates are complete. | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Perform startup and commissioning. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Electrical | Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify new electrical distribution serving telecom equipment. | Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify dedicated panel assignments. | Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify UPS installation and ratings. | Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify rack power distribution units. | Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify emergency power source. | Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify grounding and bonding requirements. | Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify circuit identification and labeling. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Telecommunications | Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Install and/or verify new equipment racks. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Install vertical and horizontal cable management. | Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal | 0
70 | B62_TR_Assessment | Install grounding busbars. | Approved Submittals | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Install fiber termination shelves. | ICRA / PCRA | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Install patch panels. | QA/QC Reports | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Verify Cat6A and fiber terminations. | Firestopping | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Verify cable labeling. | Cable Tests | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Test and certify all copper and fiber cabling. | OIT Acceptance | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B70_TR_Assessment | Verify compliance with OIT standards. | Photos | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B70_TR_Assessment | Security | Requirement | What it Means | 0 | 0 | Verification | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify PACS access control for all TR doors. | ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. | 0 | 0 | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify card reader operation. | QA/QC Reports | Contractor quality inspections have been completed and documented. | 0 | 0 | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify door position monitoring. | Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. | 0 | 0 | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify camera coverage where required. | Cable Tests | All network, fiber, and communication cabling has passed required testing. | 0 | 0 | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify integration with existing VA security systems. | OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. | 0 | 0 | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Operational Risk Review | Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. | 0 | 0 | Walk the space and confirm all critical deficiencies have been corrected prior to turnover. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Identify systems requiring uninterrupted operation. | Open Gate Count | 800% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Develop cutover strategy. | Gate Completion | 0 / 8 Complete | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Review outage requirements with VA OIT. | Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Review shutdown requirements with facilities staff. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify no active services are removed before migration. | Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW") | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Commissioning & Acceptance | Recommended Payment | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | HVAC commissioning. | ☐ Full | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Electrical commissioning. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Telecom testing and certification. | ☐ Partial | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Fire alarm testing. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Fire protection testing. | ☐ Withhold | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Security testing. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Final owner acceptance walkthrough. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Turnover documentation. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Owner Risks Identified | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | High Risk | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | B70_TR_Assessment | B30 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR with 342 total ports including allowance, dedicated cooling, UPS/PDU and 1,702 ft basement cable tray scope.
78 | B70_TR_Assessment | B35 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR/closet with 70 total ports including allowance and active transition scope.
78 | B70_TR_Assessment | 1232 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with 444 total ports including allowance and high active port count.
78 | B70_TR_Assessment | 227A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR with 383 total ports including allowance and riser/firestop coordination.
78 | B78_Assessment | 342 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Third-level TR with 318 total ports including allowance and two-rack configuration.
78 | B78_Assessment | 401 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Fourth-level TR with 135 total ports including allowance and existing 308A/408A transition points.
78 | B78_Assessment | Existing rooms | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing telecom room inventory; protect active services until cutover and acceptance complete.
80 | B80_Assessment | 102 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with 215 total ports including allowance, dedicated cooling, UPS/PDU, cable tray, PACS/CCTV and fire/life-safety scope.
80 | B80_Assessment | 127A / 126 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing telecom transition point; protect active services until cutover complete and confirm room-number mapping.
82 | B82_Assessment | 102 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TE/telecom room with 12RU wall enclosure, UPS/PDU, dedicated cooling shown, 278 ft cable tray and 40 total ports including allowance.
82 | B82_Assessment | B01-A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing first-level telecom room and transition point; protect active services until cutover complete.
BCH | BCH_Assessment | 107 | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | BCH first-level Room 107 telecom scope; verify final TE versus telecom room configuration, power, pathway, firestopping and active service transition.
BCH | BCH_Assessment | 00 / 107 | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Rack/elevation reference requiring confirmation before turnover and PMIS import.
MCR | MCR_Assessment | 107 / MCR | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New critical MCR facility with full architectural/civil/structural/MEP/FP/telecom/security scope; not construction-ready until coordination and commissioning plan are verified.
MCR | MCR_Assessment | 031 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Fiber Entrance Room 1 schedule and camera/data points require field verification and firestop/pathway coordination.
MCR | MCR_Assessment | MDA-A/B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New main distribution rows; A/B fiber diversity and rack/PDU mapping are critical.
MCR | MCR_Assessment | HDA-A/B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New horizontal distribution/server cabinet rows; airflow, patching, labeling and redundancy must be validated.
MCR | MCR_Assessment | Existing 107/137 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing MCR/server equipment transition point; protect active service until final activation.
SITE | SITE_Assesment | Overall Site | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Campus-wide fiber backbone is not construction-ready until utility locates, path routing, inspection holds and phasing plan are confirmed.
SITE | SITE_Assesment | Path A/B Backbone | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Redundant A/B path separation, conduit counts and T-601 one-line coordination require field verification.
SITE | SITE_Assesment | THH / Manholes | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | THH #1-#19 and locking manholes/pullboxes need inventory, labels, photos and acceptance.
SITE | SITE_Assesment | Building Tie-ins | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Building T-101 continuation, penetration/firestop and fiber acceptance must match each building assessment.
SITE | SITE_Assesment | MCR / Provider Entrance | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Provider fiber, temporary fiber and new MCR activation sequence are critical path items.
B01_Assessment
MAPPED DISCIPLINE STATUS ITEMS — FORMULA-FED FROM BUILDING SHEETS | B01_Assessment
Building | B01_Assessment | Discipline | Room | Overall | Notes | Source Row
01 | B01_Assessment | Fire | 107 | Verify | Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems. | B01_Assessment!A24:J24
01 | B01_Assessment | Fire | B02 | Verify | Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | B01_Assessment!A25:J25
01 | B01_Assessment | Fire | 138 | Verify | Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes. | B01_Assessment!A26:J26
01 | B01_Assessment | Fire | 282 | Verify | Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place. | B01_Assessment!A27:J27
01 | B01_Assessment | HVAC | 107 | Verify | Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup. | B01_Assessment!A31:J31
01 | B01_Assessment | HVAC | B02 | Verify | Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration. | B01_Assessment!A32:J32
01 | B01_Assessment | HVAC | 138 | Verify | Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear. | B01_Assessment!A33:J33
01 | B01_Assessment | HVAC | 282 | Verify | Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating. | B01_Assessment!A34:J34
01 | B01_Assessment | Electrical | 107 | Verify | Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation. | B01_Assessment!A38:J38
01 | B01_Assessment | Electrical | B02 | Verify | Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements. | B01_Assessment!A39:J39
01 | B01_Assessment | Electrical | 138 | Verify | Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition. | B01_Assessment!A40:J40
01 | B01_Assessment | Electrical | 282 | Verify | Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope. | B01_Assessment!A41:J41
01 | B01_Assessment | Telecom | 107 | Verify | 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1. | B01_Assessment!A45:J45
01 | B01_Assessment | Telecom | B02 | Verify | Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan. | B01_Assessment!A46:J46
01 | B01_Assessment | Telecom | 138 | Verify | Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence. | B01_Assessment!A47:J47
01 | B01_Assessment | Telecom | 282 | Verify | Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway. | B01_Assessment!A48:J48
01 | B01_Assessment | Security | 107 | Verify | Electrical/telecom plans show new access control, power supply/battery backup for PACS, HDP12/FIPS-compliant PIV-ready card reader with PIN pad, and camera 107-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration and door hardware coordination. | B01_Assessment!A52:J52
01 | B01_Assessment | Security | B02 | Verify | Verify existing security/CCTV equipment and any retained cameras. Maintain camera angles where existing security cameras are recabled. | B01_Assessment!A53:J53
01 | B01_Assessment | Security | 138 | Verify | Verify existing security/access conditions and protection-in-place during rack transfer. | B01_Assessment!A54:J54
01 | B01_Assessment | Security | 282 | Verify | Verify second-level existing security/CCTV impacts during cabling and equipment transfer. | B01_Assessment!A55:J55
02 | B01_Assessment | Fire | 141 | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. | B02_Assessment!A25:J25
02 | B01_Assessment | Fire | 236 | Verify | Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping. | B02_Assessment!A26:J26
02 | B01_Assessment | Fire | 342 | Verify | Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping. | B02_Assessment!A27:J27
02 | B01_Assessment | Fire | B-06 / existing rooms | Verify | Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | B02_Assessment!A28:J28
02 | B01_Assessment | HVAC | 141 | Verify | Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms. | B02_Assessment!A32:J32
02 | B01_Assessment | HVAC | 236 | Verify | Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm. | B02_Assessment!A33:J33
02 | B01_Assessment | HVAC | 342 | Verify | Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration. | B02_Assessment!A34:J34
02 | B01_Assessment | HVAC | B-06 / existing rooms | Verify | Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete. | B02_Assessment!A35:J35
02 | B01_Assessment | Electrical | 141 | Verify | Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels. | B02_Assessment!A39:J39
02 | B01_Assessment | Electrical | 236 | Verify | Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping. | B02_Assessment!A40:J40
02 | B01_Assessment | Electrical | 342 | Verify | Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits. | B02_Assessment!A41:J41
02 | B01_Assessment | Electrical | B-06 / existing rooms | Verify | Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs. | B02_Assessment!A42:J42
02 | B01_Assessment | Telecom | 141 | Verify | 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray. | B02_Assessment!A46:J46
02 | B01_Assessment | Telecom | 236 | Verify | 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope. | B02_Assessment!A47:J47
02 | B01_Assessment | Telecom | 342 | Verify | 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count. | B02_Assessment!A48:J48
02 | B01_Assessment | Telecom | B-06 / existing rooms | Verify | Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover. | B02_Assessment!A49:J49
02 | B01_Assessment | Security | 141 | Verify | Plans show 174-CAM-01 associated with the first-level TR area and PACS/security requirements. Verify camera/VMS integration, access controller/power supply, CR/RX/DC/ES/MD and door hardware. | B02_Assessment!A53:J53
02 | B02_Assessment | Security | 236 | Verify | Plans show 236-CAM-01. Verify camera/VMS integration, access control, door hardware, motion/detection devices and power. | B02_Assessment!A54:J54
02 | B02_Assessment | Security | 342 | Verify | Plans show 342-CAM-01 and 342A-CK-A. Verify camera/VMS integration and access control/security rough-in. | B02_Assessment!A55:J55
02 | B02_Assessment | Security | B-06 / existing rooms | Verify | Maintain existing camera angles when re-cabling and protect existing PACS/equipment racks during transfer. | B02_Assessment!A56:J56
03 | B02_Assessment | Fire | 101E | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. | B03_Assessment!A24:J24
03 | B02_Assessment | Fire | 107 | Verify | Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse. | B03_Assessment!A25:J25
03 | B02_Assessment | Fire | 101C | Verify | Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer. | B03_Assessment!A26:J26
03 | B02_Assessment | Fire | WAO Areas | Verify | Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations. | B03_Assessment!A27:J27
03 | B02_Assessment | HVAC | 101E | Verify | Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm. | B03_Assessment!A31:J31
03 | B02_Assessment | HVAC | 107 | Verify | Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete. | B03_Assessment!A32:J32
03 | B02_Assessment | HVAC | 101C | Verify | Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains. | B03_Assessment!A33:J33
03 | B02_Assessment | HVAC | WAO Areas | N/A | No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements. | B03_Assessment!A34:J34
03 | B02_Assessment | Electrical | 101E | Verify | Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements. | B03_Assessment!A38:J38
03 | B02_Assessment | Electrical | 107 | Verify | Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements. | B03_Assessment!A39:J39
03 | B02_Assessment | Electrical | 101C | Verify | Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer. | B03_Assessment!A40:J40
03 | B02_Assessment | Electrical | WAO Areas | Verify | Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations. | B03_Assessment!A41:J41
03 | B02_Assessment | Telecom | 101E | Verify | 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2. | B03_Assessment!A45:J45
03 | B02_Assessment | Telecom | 107 | Verify | Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover. | B03_Assessment!A46:J46
03 | B02_Assessment | Telecom | 101C | Verify | Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted. | B03_Assessment!A47:J47
03 | B02_Assessment | Telecom | WAO Areas | Verify | Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced. | B03_Assessment!A48:J48
03 | B02_Assessment | Security | 101E | Verify | Plans require PACS for TR doors and electrical details include access-controlled door rough-in. Verify access controller, power supply/battery backup, CR/RX/DC/ES/MD devices, reader, strike and door hardware coordination. | B03_Assessment!A52:J52
03 | B03_Assessment | Security | 101C | Verify | Enlarged plan and schedule identify 101C-CAM-01 and 101C-CK-A. Verify camera/VMS integration, existing camera angles and protection-in-place. | B03_Assessment!A53:J53
03 | B03_Assessment | Security | 107 | Verify | Verify existing security/CCTV/PACS impacts during basement telecom room transfer. | B03_Assessment!A54:J54
03 | B03_Assessment | Security | WAO Areas | Verify | Maintain existing camera angles when re-cabling; verify WAP/security/clock/Centrak devices are relabeled and tested. | B03_Assessment!A55:J55
04 | B03_Assessment | Fire | B05 | Verify | Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning. | B04_Assessment!A22:J22
04 | B03_Assessment | Fire | 141 | Verify | FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies. | B04_Assessment!A23:J23
04 | B03_Assessment | Fire | 244A | Verify | Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations. | B04_Assessment!A24:J24
04 | B03_Assessment | HVAC | B05 | Verify | Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up. | B04_Assessment!A28:J28
04 | B03_Assessment | HVAC | 141 | Verify | Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control. | B04_Assessment!A29:J29
04 | B03_Assessment | HVAC | 244A | Verify | Verify cooling unit, routing, condensate, controls, and emergency/backup power path. | B04_Assessment!A30:J30
04 | B03_Assessment | Electrical | B05 | Verify | Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits. | B04_Assessment!A34:J34
04 | B03_Assessment | Electrical | 141 | Verify | Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting. | B04_Assessment!A35:J35
04 | B03_Assessment | Electrical | 244A | Verify | Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source. | B04_Assessment!A36:J36
04 | B03_Assessment | Telecom | B05 | Verify | New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. | B04_Assessment!A40:J40
04 | B03_Assessment | Telecom | 141 | Verify | New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. | B04_Assessment!A41:J41
04 | B03_Assessment | Telecom | 244A | Verify | TR/panel identified; verify rack elevation and pathway details against 04T sheets. | B04_Assessment!A42:J42
04 | B04_Assessment | Security | B05 | Verify | Verify access-controlled TR door, camera, and VMS/PACS integration. | B04_Assessment!A46:J46
04 | B04_Assessment | Security | 141 | Verify | Architectural notes require door/access control coordination; verify card reader/electric strike rough-in. | B04_Assessment!A47:J47
04 | B04_Assessment | Security | 244A | Verify | Verify room security details and device integration with VA systems. | B04_Assessment!A48:J48
05 | B04_Assessment | Fire | 150 | Verify | Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts. | B05_Assessment!A20:J20
05 | B04_Assessment | Fire | 153-A | Verify | Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling. | B05_Assessment!A21:J21
05 | B04_Assessment | HVAC | 150 | N/A | Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling. | B05_Assessment!A25:J25
05 | B04_Assessment | HVAC | 153-A | N/A | Existing wall/wall-mount TE area; verify existing environmental conditions during field survey. | B05_Assessment!A26:J26
05 | B04_Assessment | Electrical | 150 | Verify | 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source. | B05_Assessment!A30:J30
05 | B04_Assessment | Electrical | 153-A | Verify | Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover. | B05_Assessment!A31:J31
05 | B04_Assessment | Telecom | 150 | Verify | New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU. | B05_Assessment!A35:J35
05 | B05_Assessment | Telecom | 153-A | Verify | Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records. | B05_Assessment!A36:J36
05 | B05_Assessment | Security | 150 | Verify | Project general scope includes CCTV and PACS for telecom spaces; verify whether TE location receives camera/access control or is served by existing room controls. | B05_Assessment!A40:J40
05 | B05_Assessment | Security | 153-A | Verify | Verify existing security protection and whether access-control work is needed for existing TE area. | B05_Assessment!A41:J41
06 | B05_Assessment | Fire | B-01 | Verify | Existing equipment area; verify no cabling penetrations are left unsealed. | B06_Assessment!A22:J22
06 | B05_Assessment | Fire | 178 | Verify | Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs. | B06_Assessment!A23:J23
06 | B05_Assessment | Fire | 233 | Verify | Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft. | B06_Assessment!A24:J24
06 | B05_Assessment | HVAC | B-01 | Verify | Verify basement equipment environmental condition and any heat/load issues during cutover. | B06_Assessment!A28:J28
06 | B05_Assessment | HVAC | 178 | Verify | Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route. | B06_Assessment!A29:J29
06 | B05_Assessment | HVAC | 233 | Verify | Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls. | B06_Assessment!A30:J30
06 | B05_Assessment | Electrical | B-01 | Verify | Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements. | B06_Assessment!A34:J34
06 | B05_Assessment | Electrical | 178 | Verify | Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation. | B06_Assessment!A35:J35
06 | B05_Assessment | Electrical | 233 | Verify | Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power. | B06_Assessment!A36:J36
06 | B05_Assessment | Telecom | B-01 | Verify | Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS. | B06_Assessment!A40:J40
06 | B05_Assessment | Telecom | 178 | Verify | Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification. | B06_Assessment!A41:J41
06 | B05_Assessment | Telecom | 233 | Verify | Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | B06_Assessment!A42:J42
06 | B06_Assessment | Security | B-01 | Verify | Verify existing basement access/security while protecting active equipment. | B06_Assessment!A46:J46
06 | B06_Assessment | Security | 178 | Verify | Electrical enlarged plan references existing card reader to remain/protect in place and new tri-tech motion sensor; verify PACS/CCTV integration. | B06_Assessment!A47:J47
06 | B06_Assessment | Security | 233 | Verify | Verify door hardware/access control, motion sensor, camera, and VA security integration. | B06_Assessment!A48:J48
07 | B06_Assessment | Fire | B-18 | Verify | Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination. | B07_Assessment!A20:J20
07 | B06_Assessment | Fire | 228A | Verify | Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications. | B07_Assessment!A21:J21
07 | B06_Assessment | HVAC | B-18 | Verify | Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm. | B07_Assessment!A25:J25
07 | B06_Assessment | HVAC | 228A | Verify | Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route. | B07_Assessment!A26:J26
07 | B06_Assessment | Electrical | B-18 | Verify | Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement. | B07_Assessment!A30:J30
07 | B06_Assessment | Electrical | 228A | Verify | Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels. | B07_Assessment!A31:J31
07 | B06_Assessment | Telecom | B-18 | Verify | 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU. | B07_Assessment!A35:J35
07 | B07_Assessment | Telecom | 228A | Verify | TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover. | B07_Assessment!A36:J36
07 | B07_Assessment | Security | B-18 | Verify | Verify access control, door hardware and CCTV/PACS integration for basement TR. | B07_Assessment!A40:J40
07 | B07_Assessment | Security | 228A | Verify | Architectural notes require access control hardware modifications at new rated door; verify card reader, electric strike, door position switch, motion sensor and camera. | B07_Assessment!A41:J41
08 | B07_Assessment | Fire | B-15 | Verify | Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected. | B08_Assessment!A22:J22
08 | B07_Assessment | Fire | B12B | Verify | Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers. | B08_Assessment!A23:J23
08 | B07_Assessment | Fire | 2065A | Verify | Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades. | B08_Assessment!A24:J24
08 | B07_Assessment | HVAC | B-15 | Verify | Verify existing environmental conditions and whether active legacy equipment remains during cutover. | B08_Assessment!A28:J28
08 | B07_Assessment | HVAC | B12B | Verify | Field verify whether TE equipment load requires cooling or if served by existing building HVAC. | B08_Assessment!A29:J29
08 | B07_Assessment | HVAC | 2065A | Verify | Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls. | B08_Assessment!A30:J30
08 | B07_Assessment | Electrical | B-15 | Verify | Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements. | B08_Assessment!A34:J34
08 | B07_Assessment | Electrical | B12B | Verify | Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel. | B08_Assessment!A35:J35
08 | B07_Assessment | Electrical | 2065A | Verify | Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope. | B08_Assessment!A36:J36
08 | B07_Assessment | Telecom | B-15 | Verify | Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS. | B08_Assessment!A40:J40
08 | B07_Assessment | Telecom | B12B | Verify | Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance. | B08_Assessment!A41:J41
08 | B07_Assessment | Telecom | 2065A | Verify | New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS. | B08_Assessment!A42:J42
08 | B08_Assessment | Security | B-15 | Verify | Verify existing basement access/security while protecting active equipment. | B08_Assessment!A46:J46
08 | B08_Assessment | Security | B12B | Verify | 45-minute door shown; verify access-control hardware applicability and whether TE is secured. | B08_Assessment!A47:J47
08 | B08_Assessment | Security | 2065A | Verify | Door schedule/hardware note requires coordination with electrical/access control; verify card reader, electric strike, door position, motion sensor, camera and VA integration. | B08_Assessment!A48:J48
09 | B08_Assessment | Fire | B01 | Verify | Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR. | B09_Assessment!A22:J22
09 | B08_Assessment | Fire | 104B | Verify | Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft. | B09_Assessment!A23:J23
09 | B08_Assessment | Fire | 206A | Verify | Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations. | B09_Assessment!A24:J24
09 | B08_Assessment | HVAC | B01 | Verify | Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms. | B09_Assessment!A28:J28
09 | B08_Assessment | HVAC | 104B | Verify | Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power. | B09_Assessment!A29:J29
09 | B08_Assessment | HVAC | 206A | Verify | Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power. | B09_Assessment!A30:J30
09 | B08_Assessment | Electrical | B01 | Verify | Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes. | B09_Assessment!A34:J34
09 | B08_Assessment | Electrical | 104B | Verify | Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits. | B09_Assessment!A35:J35
09 | B08_Assessment | Electrical | 206A | Verify | Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits. | B09_Assessment!A36:J36
09 | B08_Assessment | Telecom | B01 | Verify | Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover. | B09_Assessment!A40:J40
09 | B08_Assessment | Telecom | 104B | Verify | Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | B09_Assessment!A41:J41
09 | B08_Assessment | Telecom | 206A | Verify | Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | B09_Assessment!A42:J42
09 | B09_Assessment | Security | B01 | Verify | Enlarged plans show existing/new security boxes, network door controller, camera/security scope; verify PACS/CCTV integration and protection of active security systems. | B09_Assessment!A46:J46
09 | B09_Assessment | Security | 104B | Verify | First-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 104B camera designation; verify card reader, electric strike, door contact, motion and camera. | B09_Assessment!A47:J47
09 | B09_Assessment | Security | 206A | Verify | Second-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 206A camera designation; verify PACS/VMS integration and commissioning. | B09_Assessment!A48:J48
10 | B09_Assessment | Fire | 200A | Verify | Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping. | B10_Assessment!A22:J22
10 | B09_Assessment | Fire | B24 | Verify | Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place. | B10_Assessment!A23:J23
10 | B09_Assessment | Fire | B25 | Verify | Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment. | B10_Assessment!A24:J24
10 | B09_Assessment | HVAC | 200A | Verify | Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm. | B10_Assessment!A28:J28
10 | B09_Assessment | HVAC | B24 | N/A | No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work. | B10_Assessment!A29:J29
10 | B09_Assessment | HVAC | B25 | N/A | No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted. | B10_Assessment!A30:J30
10 | B09_Assessment | Electrical | 200A | Verify | Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels. | B10_Assessment!A34:J34
10 | B09_Assessment | Electrical | B24 | Verify | Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing. | B10_Assessment!A35:J35
10 | B09_Assessment | Electrical | B25 | Verify | Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required. | B10_Assessment!A36:J36
10 | B09_Assessment | Telecom | 200A | Verify | 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover. | B10_Assessment!A40:J40
10 | B09_Assessment | Telecom | B24 | Verify | Coordinate telecom power pathways through/source from basement electrical room if applicable. | B10_Assessment!A41:J41
10 | B09_Assessment | Telecom | B25 | Verify | Coordinate emergency source/backup power pathways for telecom equipment and cooling. | B10_Assessment!A42:J42
10 | B10_Assessment | Security | 200A | Verify | General scope requires PACS/CCTV for TR doors; verify door hardware, access controller, camera/VMS integration and any existing attic access/security constraints. | B10_Assessment!A46:J46
10 | B10_Assessment | Security | B24 | Verify | Verify security impact only if electrical source room access or devices are modified. | B10_Assessment!A47:J47
10 | B10_Assessment | Security | B25 | Verify | Verify emergency electrical room security impact if work requires access control changes. | B10_Assessment!A48:J48
12 | B10_Assessment | Fire | Fiber path B/1/2 | Verify | No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route. | B12_Assessment!A20:J20
12 | B10_Assessment | Fire | Existing rack/demarc - field verify | Verify | No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work. | B12_Assessment!A21:J21
12 | B10_Assessment | HVAC | Fiber path B/1/2 | N/A | No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment. | B12_Assessment!A25:J25
12 | B10_Assessment | HVAC | Existing rack/demarc - field verify | N/A | Field verify existing environmental conditions only if existing service point/equipment is accessed. | B12_Assessment!A26:J26
12 | B10_Assessment | Electrical | Fiber path B/1/2 | Verify | No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown. | B12_Assessment!A30:J30
12 | B10_Assessment | Electrical | Existing rack/demarc - field verify | Verify | Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling. | B12_Assessment!A31:J31
12 | B10_Assessment | Telecom | Fiber path B/1/2 | Verify | Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing. | B12_Assessment!A35:J35
12 | B12_Assessment | Telecom | Existing rack/demarc - field verify | Verify | 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only. | B12_Assessment!A36:J36
12 | B12_Assessment | Security | Fiber path B/1/2 | N/A / Verify | No new TR door or PACS/CCTV package shown for Building 12; verify security access only for work areas and existing equipment rooms. | B12_Assessment!A40:J40
12 | B12_Assessment | Security | Existing rack/demarc - field verify | N/A / Verify | Confirm access requirements to existing closet/demarc while protecting active operations. | B12_Assessment!A41:J41
13 | B12_Assessment | Fire | 124 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | B13_Assessment!A20:J20
13 | B12_Assessment | Fire | 222 | Verify | Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B13_Assessment!A21:J21
13 | B12_Assessment | HVAC | 124 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B13_Assessment!A25:J25
13 | B12_Assessment | HVAC | 222 | Verify | Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | B13_Assessment!A26:J26
13 | B12_Assessment | Electrical | 124 | Verify | Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements. | B13_Assessment!A30:J30
13 | B12_Assessment | Electrical | 222 | Verify | Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | B13_Assessment!A31:J31
13 | B12_Assessment | Telecom | 124 | Verify | 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B. | B13_Assessment!A35:J35
13 | B13_Assessment | Telecom | 222 | Verify | Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124. | B13_Assessment!A36:J36
13 | B13_Assessment | Security | 124 | Verify | Electrical enlarged plan shows security/access-control device callouts at Room 124 and 124-CAM-01 camera designation; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B13_Assessment!A40:J40
13 | B13_Assessment | Security | 222 | Verify | Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B13_Assessment!A41:J41
14 | B13_Assessment | Fire | 119 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | B14_Assessment!A22:J22
14 | B13_Assessment | Fire | B.01 | Verify | Existing basement tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B14_Assessment!A23:J23
14 | B13_Assessment | Fire | B2 | Verify | Existing basement telecom room; verify no unsealed penetrations remain after cable transfer or reuse. | B14_Assessment!A24:J24
14 | B13_Assessment | HVAC | 119 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 119 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B14_Assessment!A28:J28
14 | B13_Assessment | HVAC | B.01 | Verify | Existing Tel/F Panel room; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B14_Assessment!A29:J29
14 | B13_Assessment | HVAC | B2 | Verify | Existing telecom room reference; field verify cooling/ventilation and active equipment condition. | B14_Assessment!A30:J30
14 | B13_Assessment | Electrical | 119 | Verify | Electrical plan/schedules identify B14-TR119A/B, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and panel load measurement requirements. | B14_Assessment!A34:J34
14 | B13_Assessment | Electrical | B.01 | Verify | Existing basement wall-mounted TE/equipment area; verify power source, active equipment, UPS/PDU status, and transition requirements before disconnect or removal. | B14_Assessment!A35:J35
14 | B13_Assessment | Electrical | B2 | Verify | Existing telecom room photo reference; confirm power sources and any cutover requirements. | B14_Assessment!A36:J36
14 | B13_Assessment | Telecom | 119 | Verify | 14T-701 identifies Room 119 schedule: 44 WAO total, 29 active ports per survey, 76 total ports per schedule, and 84 total ports with 10% allowance. New Rack ID TR01-119-1 serves first and second level outlets with Fiber Path A/B. | B14_Assessment!A40:J40
14 | B13_Assessment | Telecom | B.01 | Verify | Existing Room B.01 equipment includes wall-mounted TE, Cisco switch/legacy patch panel, telco patch, plywood backboards, and legacy Fiber LIU; verify active services and transfer plan to Room 119. | B14_Assessment!A41:J41
14 | B13_Assessment | Telecom | B2 | Verify | Existing basement telecom room B2 is identified by photo reference; verify active devices, routing, and relation to B.01. | B14_Assessment!A42:J42
14 | B14_Assessment | Security | 119 | Verify | Telecom/electrical plans show 119-CAM-01 and security/access-control scope for Room 119; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B14_Assessment!A46:J46
14 | B14_Assessment | Security | B.01 | Verify | Verify whether existing security equipment remains, is relocated, or requires temporary protection during cutover. | B14_Assessment!A47:J47
14 | B14_Assessment | Security | B2 | Verify | Verify security/access conditions and whether any legacy security equipment is present. | B14_Assessment!A48:J48
15 | B14_Assessment | Fire | 124A | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | B15_Assessment!A22:J22
15 | B14_Assessment | Fire | 222 | Verify | Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B15_Assessment!A23:J23
15 | B14_Assessment | Fire | B01 | Verify | Existing basement telecom/crossover room; verify no unsealed penetrations remain after cable transfer or reuse. | B15_Assessment!A24:J24
15 | B14_Assessment | HVAC | 124A | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 124A and CU-1-01 outdoor heat-pump/A/C unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B15_Assessment!A28:J28
15 | B14_Assessment | HVAC | 222 | Verify | Existing Tel Room 222 is shown with existing/remain indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | B15_Assessment!A29:J29
15 | B14_Assessment | HVAC | B01 | Verify | Existing basement telecom/crossover space; verify environmental conditions and whether active equipment remains during cutover. | B15_Assessment!A30:J30
15 | B14_Assessment | Electrical | 124A | Verify | Electrical enlarged plans and schedules identify B15-TR124AA/AB, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and 30-day load measurement requirements. | B15_Assessment!A34:J34
15 | B14_Assessment | Electrical | 222 | Verify | Existing rack/equipment area; verify power source, active equipment, APC floor UPS status, and transition requirements before disconnect or removal. | B15_Assessment!A35:J35
15 | B14_Assessment | Electrical | B01 | Verify | Existing B-01 crossover; verify power sources and cutover needs for legacy patch panel/crossover. | B15_Assessment!A36:J36
15 | B14_Assessment | Telecom | 124A | Verify | 15T-701 identifies Room 109A schedule but field plan/electrical room callouts identify Telecom Room 124A; schedule has 62 WAO total, 76 active ports per survey, 101 total ports per schedule, and 111 total ports with 10% allowance. New Rack ID TR15-109A-01 serves basement, first and second level outlets. | B15_Assessment!A40:J40
15 | B14_Assessment | Telecom | 222 | Verify | Existing Room 222 equipment includes wall/wall-mounted TE, Cisco switches, legacy 48-port patch panels, ground bar, plywood backboard, security cabinet, and floor UPS; verify active services and transfer plan to Room 124A. | B15_Assessment!A41:J41
15 | B14_Assessment | Telecom | B01 | Verify | Existing B-01 crossover includes legacy 24-port patch panel; verify active devices, routing, and relation to Room 222 and Room 124A. | B15_Assessment!A42:J42
15 | B15_Assessment | Security | 124A | Verify | Telecom/electrical plans show 124A-CAM-1 and security/access-control scope for Room 124A; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B15_Assessment!A46:J46
15 | B15_Assessment | Security | 222 | Verify | Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B15_Assessment!A47:J47
15 | B15_Assessment | Security | B01 | Verify | Verify security/access conditions and whether any legacy security equipment is present. | B15_Assessment!A48:J48
16 | B15_Assessment | Fire | 015 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | B16_Assessment!A20:J20
16 | B15_Assessment | Fire | 014 | Verify | Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B16_Assessment!A21:J21
16 | B15_Assessment | HVAC | 015 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 015 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B16_Assessment!A25:J25
16 | B15_Assessment | HVAC | 014 | Verify | Existing Telecom Room 014; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B16_Assessment!A26:J26
16 | B15_Assessment | Electrical | 015 | Verify | Electrical plans/schedules identify B16-TR015A/B, 240V rack UPS requirements, rack receptacles, TR receptacles, lighting, access controller, CU-1-01, SPD requirements, existing panel demolition/replacement, and 30-day load measurement requirements. | B16_Assessment!A30:J30
16 | B15_Assessment | Electrical | 014 | Verify | Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | B16_Assessment!A31:J31
16 | B15_Assessment | Telecom | 015 | Verify | 16T-701 identifies Room 015-A schedule: 25 WAO total, 25 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. New Rack ID TR01-015-A-1 serves basement, first, second and attic level outlets. | B16_Assessment!A35:J35
16 | B16_Assessment | Telecom | 014 | Verify | Existing Room 014 equipment includes wall/TE rack, floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU; verify active services and transfer plan to Room 015. | B16_Assessment!A36:J36
16 | B16_Assessment | Security | 015 | Verify | Telecom/electrical plans show 015-CAM-1 and security/access-control scope for Room 015; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B16_Assessment!A40:J40
16 | B16_Assessment | Security | 014 | Verify | Existing security cabinet shown in Room 014; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B16_Assessment!A41:J41
17 | B16_Assessment | Fire | 118 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | B17_Assessment!A22:J22
17 | B16_Assessment | Fire | B35A | Verify | Existing telecom closet; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B17_Assessment!A23:J23
17 | B16_Assessment | Fire | B29 Path | Verify | Verify firestopping at pathway penetrations between Building 17 and Building 29 and any rated floor/wall assemblies. | B17_Assessment!A24:J24
17 | B16_Assessment | HVAC | 118 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 118 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B17_Assessment!A28:J28
17 | B16_Assessment | HVAC | B35A | Verify | Existing B35A is shown with existing indoor AC unit; verify whether it remains active, is abandoned, or needs temporary protection during cutover. | B17_Assessment!A29:J29
17 | B16_Assessment | HVAC | B29 Path | N/A | No dedicated cooling expected for pathway; verify any equipment cabinets or active service locations in Building 29 if applicable. | B17_Assessment!A30:J30
17 | B16_Assessment | Electrical | 118 | Verify | Electrical plans/schedules identify B17-TR118A fed from BUS-B17-NPB1-R and B17-TR118B fed from BUS-B17-EQDP, with TR RM118 rack receptacles, 208V UPS/PDU equipment, CU-1-01, SPD requirements, and 30-day load measurement requirements. | B17_Assessment!A34:J34
17 | B16_Assessment | Electrical | B35A | Verify | Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. | B17_Assessment!A35:J35
17 | B16_Assessment | Electrical | B29 Path | Verify | Verify whether any Building 29 equipment or extension path requires power, grounding, bonding, or labeling tied back to B17 TR 118. | B17_Assessment!A36:J36
17 | B16_Assessment | Telecom | 118 | Verify | 17_29T-701 identifies Room 118 schedule: 113 WAO total, 67 active ports per survey, 154 total ports per schedule, and 169 total ports with 10% allowance. Rack ID TR17-118-1 serves basement, first, second-level outlets and Building 29 path. | B17_Assessment!A40:J40
17 | B16_Assessment | Telecom | B35A | Verify | Existing Room B35A equipment includes SERTEX utility service ports, legacy Ortronics patch panels, Cisco switches, wall-mounted TE, Fiber/legacy equipment, security cabinet, and floor UPS; verify active services and transfer plan to Room 118. | B17_Assessment!A41:J41
17 | B16_Assessment | Telecom | B29 Path | Verify | Building 29 is shown served from B17; verify fiber from Building 17 to Building 29, path to B29 4-inch PVC, outlet labels, test records and as-builts. | B17_Assessment!A42:J42
17 | B17_Assessment | Security | 118 | Verify | Telecom/electrical plans show 118-CAM-01 and security/access-control scope for Room 118; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B17_Assessment!A46:J46
17 | B17_Assessment | Security | B35A | Verify | Existing security cabinet shown in B35A; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B17_Assessment!A47:J47
17 | B17_Assessment | Security | B29 Path | Verify | Verify Building 29 pathway and any security scope tied into B17 TR 118/VMS/PACS. | B17_Assessment!A48:J48
18 | B17_Assessment | Fire | 110 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | B18_Assessment!A22:J22
18 | B17_Assessment | Fire | 111B | Verify | Existing TE room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | B18_Assessment!A23:J23
18 | B17_Assessment | Fire | 213 | Verify | Existing second-level closet; verify protection-in-place and firestopping after transfer or abandonment. | B18_Assessment!A24:J24
18 | B17_Assessment | HVAC | 110 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 110 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B18_Assessment!A28:J28
18 | B17_Assessment | HVAC | 111B | Verify | Existing TE 111B; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B18_Assessment!A29:J29
18 | B17_Assessment | HVAC | 213 | Verify | Existing Closet 213; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B18_Assessment!A30:J30
18 | B17_Assessment | Electrical | 110 | Verify | Electrical plans/schedules identify B18-TR110A/B, 208V rack UPS requirements, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and telecom panelboard schedule requirements. | B18_Assessment!A34:J34
18 | B17_Assessment | Electrical | 111B | Verify | Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. | B18_Assessment!A35:J35
18 | B17_Assessment | Electrical | 213 | Verify | Existing rack/equipment area; verify active equipment, APC UPS status, source circuits, SERTEX utility service and transfer requirements before disconnect/removal. | B18_Assessment!A36:J36
18 | B17_Assessment | Telecom | 110 | Verify | 18T-701 identifies RM 111A schedule: 86 WAO total, 61 active ports per survey, 122 ports per schedule, and 134 total ports with 10% allowance. New rack elevation is Room 110, 1 rack plus future, with UPS, Future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | B18_Assessment!A40:J40
18 | B17_Assessment | Telecom | 111B | Verify | Existing Room 111B equipment includes wall-mounted rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber optic housing; verify active services and transfer plan to Room 110. | B18_Assessment!A41:J41
18 | B17_Assessment | Telecom | 213 | Verify | Existing Room 213 equipment includes SERTEX utility service ports, Cisco switch, multiple legacy Ortronics patch panels, wall/wall-mount TE and APC floor UPS; verify active services and transfer plan to Room 110. | B18_Assessment!A42:J42
18 | B18_Assessment | Security | 110 | Verify | Telecom/electrical plans show 111A-CAM-01 and security/access-control scope for the new TR area; verify room naming, CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B18_Assessment!A46:J46
18 | B18_Assessment | Security | 111B | Verify | Existing security cabinet shown in 111B; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B18_Assessment!A47:J47
18 | B18_Assessment | Security | 213 | Verify | Existing security cabinet shown in 213; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B18_Assessment!A48:J48
20 | B18_Assessment | Fire | 1B | Verify | Cover sheet states Building 20 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. | B20_Assessment!A20:J20
20 | B18_Assessment | Fire | 8A | Verify | Existing closet; verify protection-in-place and firestopping after cable transfer or reuse. | B20_Assessment!A21:J21
20 | B18_Assessment | HVAC | 1B | N/A | Cover sheet states mechanical scope is excluded. Verify whether Office 1B ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | B20_Assessment!A25:J25
20 | B18_Assessment | HVAC | 8A | Verify | Existing Tel/Data Closet 8A includes indoor AC unit to remain/protect in place; verify operation during cutover and whether equipment remains after transition. | B20_Assessment!A26:J26
20 | B18_Assessment | Electrical | 1B | Verify | 20T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | B20_Assessment!A30:J30
20 | B18_Assessment | Electrical | 8A | Verify | Existing 8A elevation shows UPS on ground, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | B20_Assessment!A31:J31
20 | B18_Assessment | Telecom | 1B | Verify | 20T-701 identifies TE01-1B-1: 21 WAO total, 24 active ports per survey, 30 ports per schedule, 33 total ports with 10% allowance. Provide new wall-mount TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. | B20_Assessment!A35:J35
20 | B20_Assessment | Telecom | 8A | Verify | Existing Tel/Data Closet 8A contains open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy 48-port patch panel and Fiber LIU. Field verify all active services. | B20_Assessment!A36:J36
20 | B20_Assessment | Security | 1B | Verify | Building 20 does not appear to create a new TR door/PACS package. Verify any existing cameras/security devices in Office 1B and ensure no camera angle or VMS integration is disrupted. | B20_Assessment!A40:J40
20 | B20_Assessment | Security | 8A | Verify | Keynotes indicate existing cameras are to be retained and re-used/protected in place; verify existing security equipment and cabinet impacts during cutover. | B20_Assessment!A41:J41
21 | B20_Assessment | Fire | 100A | Verify | Cover sheet states Building 21_19 receives a Telecom Enclosure and fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. | B21_Assessment!A22:J22
21 | B20_Assessment | Fire | B1.TR | Verify | Existing B21 basement TR; verify protection-in-place and firestopping after cable transfer or reuse. | B21_Assessment!A23:J23
21 | B20_Assessment | Fire | B05TR | Verify | Existing B19 B05TR; verify protection-in-place and firestopping after cable transfer or reuse. | B21_Assessment!A24:J24
21 | B20_Assessment | HVAC | 100A | Verify | Mechanical sheets exist in index. Verify whether new TE heat load in Office 100A is supported by existing/new HVAC and whether any mechanical scope applies despite TE designation. | B21_Assessment!A28:J28
21 | B20_Assessment | HVAC | B1.TR | Verify | Existing B21 B1.TR; verify environmental conditions during cutover and whether legacy equipment remains active. | B21_Assessment!A29:J29
21 | B20_Assessment | HVAC | B05TR | Verify | Existing B19 B05TR; verify environmental conditions and whether equipment remains active during/after Building 21 transfer. | B21_Assessment!A30:J30
21 | B20_Assessment | Electrical | 100A | Verify | 21_19T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switches, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | B21_Assessment!A34:J34
21 | B20_Assessment | Electrical | B1.TR | Verify | Existing B21 B1.TR elevation shows UPS on ground, Cisco switch, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements. | B21_Assessment!A35:J35
21 | B20_Assessment | Electrical | B05TR | Verify | Existing B19 B05TR elevations show APC floor UPS, legacy patch panels, Cisco switch and Fiber LIU; verify power source, active equipment and transfer/retention requirements. | B21_Assessment!A36:J36
21 | B20_Assessment | Telecom | 100A | Verify | 21_19T-701 identifies RM 104 schedule: 90 WAO total, 67 active ports per survey, 119 ports per schedule, and 131 total ports with 10% allowance. 659 ft cable tray total: 63 ft basement and 596 ft first level. | B21_Assessment!A40:J40
21 | B20_Assessment | Telecom | B1.TR | Verify | Existing B21 B1.TR equipment includes multiple legacy patch panels, Cisco switch, UPS on ground, Fiber LIU and APC floor UPS; verify active services and transfer plan to new TE. | B21_Assessment!A41:J41
21 | B20_Assessment | Telecom | B05TR | Verify | Existing B19 B05TR equipment includes legacy Ortronics patch panels, Cisco switch, Fiber LIU and APC floor UPS; verify active services and whether B19/B21 devices are served from new enclosure. | B21_Assessment!A42:J42
21 | B21_Assessment | Security | 100A | Verify | Building 21_19 appears to create a TE enclosure rather than a full TR door/PACS package. Verify any existing cameras/security devices in Room 100A and ensure no camera angle or VMS integration is disrupted. | B21_Assessment!A46:J46
21 | B21_Assessment | Security | B1.TR | Verify | Verify any existing security device/cabinet impacts during cutover. | B21_Assessment!A47:J47
21 | B21_Assessment | Security | B05TR | Verify | Verify existing security/camera protection-in-place and any impact from B19/B21 shared telecom equipment. | B21_Assessment!A48:J48
22 | B21_Assessment | Fire | 102 | Verify | Cover sheet states Building 22 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. | B22_Assessment!A20:J20
22 | B21_Assessment | Fire | 103 | Verify | Existing TE room; verify protection-in-place and firestopping after cable transfer or reuse. | B22_Assessment!A21:J21
22 | B21_Assessment | HVAC | 102 | N/A | Cover sheet states mechanical scope is excluded. Verify whether Break Room 102 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | B22_Assessment!A25:J25
22 | B21_Assessment | HVAC | 103 | Verify | Existing Room 103 equipment area; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B22_Assessment!A26:J26
22 | B21_Assessment | Electrical | 102 | Verify | 22T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | B22_Assessment!A30:J30
22 | B21_Assessment | Electrical | 103 | Verify | Existing 103 elevation shows APC UPS, Cisco switch, SERTEX utility service, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | B22_Assessment!A31:J31
22 | B21_Assessment | Telecom | 102 | Verify | 22T-701 identifies TR01-102-1: 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total port quantities, and 8 total ports with 10% allowance. Provide new wall-mount 12RU TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. | B22_Assessment!A35:J35
22 | B22_Assessment | Telecom | 103 | Verify | Existing Room 103 contains APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall and ports 1-24 to Bldg 19 ports 73-96. Field verify all active services and B19 handoff. | B22_Assessment!A36:J36
22 | B22_Assessment | Security | 102 | Verify | Building 22 does not appear to create a new full TR door/PACS package. Verify any existing cameras/security devices in Break Room 102 and ensure no camera angle or VMS integration is disrupted. | B22_Assessment!A40:J40
22 | B22_Assessment | Security | 103 | Verify | Verify security/access conditions and whether any legacy security equipment is present at existing TE location. | B22_Assessment!A41:J41
33 | B22_Assessment | Fire | B23 | Verify | Cover sheet states Building 33 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. | B33_Assessment!A20:J20
33 | B22_Assessment | Fire | B17 | Verify | Existing Tel Closet; verify protection-in-place and firestopping after cable transfer or reuse. | B33_Assessment!A21:J21
33 | B22_Assessment | HVAC | B23 | N/A | Cover sheet states mechanical scope is excluded. Verify whether Office B23 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | B33_Assessment!A25:J25
33 | B22_Assessment | HVAC | B17 | Verify | Existing B17 enlarged plan identifies an existing indoor AC unit. Verify operation during cutover and determine whether active legacy equipment remains after transfer to B23. | B33_Assessment!A26:J26
33 | B22_Assessment | Electrical | B23 | Verify | 33T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | B33_Assessment!A30:J30
33 | B22_Assessment | Electrical | B17 | Verify | Existing B17 elevations show UPS on floor, Cisco switches, SERTEX utility service, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements before disconnect/removal. | B33_Assessment!A31:J31
33 | B22_Assessment | Telecom | B23 | Verify | 33T-701 identifies TE01-B23-1: 55 WAO total, 34 active ports per survey, 88 total ports per schedule, and 97 total ports with 10% allowance. Basement cable tray schedule totals 102 ft. Provide 10 new Cat6A cross-connect cables from existing TE to new TE location. | B33_Assessment!A35:J35
33 | B33_Assessment | Telecom | B17 | Verify | Existing B17 rack elevations include Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, passive Fiber LIU/wall mount, UPS on floor and cross-building port references to Bldgs 3, 80 and 82. | B33_Assessment!A36:J36
33 | B33_Assessment | Security | B23 | Verify | Building 33 does not appear to create a new full TR door/PACS package. Verify existing cameras/security devices in B23 and ensure no camera angle or VMS integration is disrupted. | B33_Assessment!A40:J40
33 | B33_Assessment | Security | B17 | Verify | Existing B17 enlarged plan identifies network door controller, keypad and equipment box; verify protection-in-place and whether any security equipment is relocated or recabled. | B33_Assessment!A41:J41
61 | B33_Assessment | Fire | B13H-A | Verify | Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. | B61_Assessment!A24:J24
61 | B33_Assessment | Fire | 124 | Verify | Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. | B61_Assessment!A25:J25
61 | B33_Assessment | Fire | 226 | Verify | Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. | B61_Assessment!A26:J26
61 | B33_Assessment | Fire | 137 / 137A | Verify | Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | B61_Assessment!A27:J27
61 | B33_Assessment | HVAC | B13H-A | Verify | Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. | B61_Assessment!A31:J31
61 | B33_Assessment | HVAC | 124 | Verify | Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. | B61_Assessment!A32:J32
61 | B33_Assessment | HVAC | 226 | Verify | Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. | B61_Assessment!A33:J33
61 | B33_Assessment | HVAC | 137 / 137A | Verify | Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | B61_Assessment!A34:J34
61 | B33_Assessment | Electrical | B13H-A | Verify | Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. | B61_Assessment!A38:J38
61 | B33_Assessment | Electrical | 124 | Verify | Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. | B61_Assessment!A39:J39
61 | B33_Assessment | Electrical | 226 | Verify | Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. | B61_Assessment!A40:J40
61 | B33_Assessment | Electrical | 137 / 137A | Verify | Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | B61_Assessment!A41:J41
61 | B33_Assessment | Telecom | B13H-A | Verify | 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. | B61_Assessment!A45:J45
61 | B33_Assessment | Telecom | 124 | Verify | 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. | B61_Assessment!A46:J46
61 | B33_Assessment | Telecom | 226 | Verify | 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. | B61_Assessment!A47:J47
61 | B33_Assessment | Telecom | 137 / 137A | Verify | 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service. | B61_Assessment!A48:J48
61 | B33_Assessment | Security | B13H-A | Verify | Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. | B61_Assessment!A52:J52
61 | B61_Assessment | Security | 124 | Verify | Verify TR door hardware and access control, CCTV camera, network door controller and integration. | B61_Assessment!A53:J53
61 | B61_Assessment | Security | 226 | Verify | Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. | B61_Assessment!A54:J54
61 | B61_Assessment | Security | 137 / 137A | Verify | Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | B61_Assessment!A55:J55
62 | B61_Assessment | Fire | B24A | Verify | 0 | B62_TR_Assessment!A24:J24
62 | B61_Assessment | Fire | 125 | Verify | 0 | B62_TR_Assessment!A25:J25
62 | B61_Assessment | Fire | 225 | Verify | 0 | B62_TR_Assessment!A26:J26
62 | B61_Assessment | HVAC | B24A | Verify | 0 | B62_TR_Assessment!A31:J31
62 | B61_Assessment | HVAC | 125 | Verify | 0 | B62_TR_Assessment!A32:J32
62 | B61_Assessment | HVAC | 225 | Verify | 0 | B62_TR_Assessment!A33:J33
62 | B62_TR_Assessment | Electrical | B24A | Verify | 0 | B62_TR_Assessment!A38:J38
62 | B62_TR_Assessment | Electrical | 125 | Verify | 0 | B62_TR_Assessment!A39:J39
62 | B62_TR_Assessment | Electrical | 225 | Verify | 0 | B62_TR_Assessment!A40:J40
70 | B62_TR_Assessment | Fire | B27 | Verify | 0 | B70_TR_Assessment!A24:J24
70 | B62_TR_Assessment | Fire | 125A | Verify | 0 | B70_TR_Assessment!A25:J25
70 | B62_TR_Assessment | Fire | 262A | Verify | 0 | B70_TR_Assessment!A26:J26
70 | B62_TR_Assessment | HVAC | B27 | Verify | 0 | B70_TR_Assessment!A31:J31
70 | B62_TR_Assessment | HVAC | 125A | Verify | 0 | B70_TR_Assessment!A32:J32
70 | B62_TR_Assessment | HVAC | 262A | Verify | 0 | B70_TR_Assessment!A33:J33
70 | B70_TR_Assessment | Electrical | B27 | Verify | 0 | B70_TR_Assessment!A38:J38
70 | B70_TR_Assessment | Electrical | 125A | Verify | 0 | B70_TR_Assessment!A39:J39
70 | B70_TR_Assessment | Electrical | 262A | Verify | 0 | B70_TR_Assessment!A40:J40
78 | B70_TR_Assessment | Electrical | B30 | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, and rated penetrations. | B78_Assessment!A30:J30
78 | B70_TR_Assessment | Electrical | B35 | Verify | Verify FP/FA modifications, FEC location, temporary firestopping and final UL systems. | B78_Assessment!A31:J31
78 | B70_TR_Assessment | Electrical | 1232 | Verify | Verify first-level TR sprinkler/FA work, FEC location and cable tray penetrations. | B78_Assessment!A32:J32
78 | B70_TR_Assessment | Electrical | 227A | Verify | Verify second-level TR sprinkler/FA work, FEC location, vertical riser penetrations and firestopping. | B78_Assessment!A33:J33
78 | B70_TR_Assessment | Fire | 342 | Verify | Verify third-level TR fire protection/fire alarm coordination and firestop work. | B78_Assessment!A34:J34
78 | B70_TR_Assessment | Fire | 401 | Verify | Verify fourth-level TR fire protection/fire alarm coordination and firestop work. | B78_Assessment!A35:J35
78 | B70_TR_Assessment | Fire | Existing rooms | Verify | Verify existing rooms remain protected during cutover and no unsealed penetrations remain. | B78_Assessment!A36:J36
78 | B70_TR_Assessment | Fire | B30 | Verify | Mechanical sheets included for basement. Verify dedicated cooling equipment, capacity, condensate, emergency source, controls/BACnet and high-temperature alarm. | B78_Assessment!A40:J40
78 | B70_TR_Assessment | Fire | B35 | Verify | Verify dedicated cooling and relationship to B30/B35 telecom buildout. | B78_Assessment!A41:J41
78 | B70_TR_Assessment | Fire | 1232 | Verify | Verify first-level TR cooling, controls, emergency power and alarm tie-in. | B78_Assessment!A42:J42
78 | B70_TR_Assessment | Fire | 227A | Verify | Verify second-level TR cooling, condensate route and 24/7 operation. | B78_Assessment!A43:J43
78 | B70_TR_Assessment | HVAC | 342 | Verify | Verify third-level TR cooling and control/alarm integration. | B78_Assessment!A44:J44
78 | B70_TR_Assessment | HVAC | 401 | Verify | Verify fourth-level TR cooling and control/alarm integration. | B78_Assessment!A45:J45
78 | B70_TR_Assessment | HVAC | Existing rooms | Verify | Existing telecom rooms likely have legacy cooling dependencies. Verify active equipment temperature and any protect-in-place cooling requirements. | B78_Assessment!A46:J46
78 | B70_TR_Assessment | HVAC | B30 | Verify | Rack elevations identify new rack UPS/PDU and future rack. Verify panelboard/source, SPD, rack receptacles, PDU feeds, labels, load measurement and LOTO. | B78_Assessment!A50:J50
78 | B70_TR_Assessment | HVAC | B35 | Verify | Verify rack UPS/PDU source, spare/future rack provisions and grounding/bonding. | B78_Assessment!A51:J51
78 | B70_TR_Assessment | HVAC | 1232 | Verify | Verify first-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. | B78_Assessment!A52:J52
78 | B70_TR_Assessment | HVAC | 227A | Verify | Verify second-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. | B78_Assessment!A53:J53
78 | B70_TR_Assessment | Electrical | 342 | Verify | Verify third-level rack receptacles for two racks, UPS/PDU, panel sources and labels. | B78_Assessment!A54:J54
78 | B70_TR_Assessment | Electrical | 401 | Verify | Verify fourth-level rack receptacles, UPS/PDU, panel sources and labels. | B78_Assessment!A55:J55
78 | B70_TR_Assessment | Electrical | Existing rooms | Verify | Existing rack elevations show wall-mounted racks/2-post racks, existing UPS/PDU and demarc/fiber equipment. Confirm active power and transfer needs. | B78_Assessment!A56:J56
78 | B70_TR_Assessment | Electrical | B30 | Verify | 78_78AT-701: 210 WAO total, 23 active ports, 311 scheduled ports, 342 with allowance; rack IDs TR01-B30-1/-2. Basement cable tray total 1,702 ft. | B78_Assessment!A60:J60
78 | B70_TR_Assessment | Electrical | B35 | Verify | 78_78AT-702: 53 WAO total, 23 active ports, 64 scheduled ports, 70 with allowance. Confirm rack ID/room relation and active services. | B78_Assessment!A61:J61
78 | B70_TR_Assessment | Electrical | 1232 | Verify | 78_78AT-702/703: 301 WAO total, 388 active ports, 404 scheduled ports, 444 with allowance. Large active port count; high cutover risk. | B78_Assessment!A62:J62
78 | B70_TR_Assessment | Electrical | 227A | Verify | 78_78AT-703/704: 256 WAO total, 153 active ports, 348 scheduled ports, 383 with allowance. Verify second-level test records and riser labels. | B78_Assessment!A63:J63
78 | B70_TR_Assessment | Telecom | 342 | Verify | 78_78AT-704: 158 WAO total, 163 active ports, 289 scheduled ports, 318 with allowance. Rack IDs TR01-342-1/-2. | B78_Assessment!A64:J64
78 | B70_TR_Assessment | Telecom | 401 | Verify | 78_78AT-705: 89 WAO total, 65 active ports, 123 scheduled ports, 135 with allowance. | B78_Assessment!A65:J65
78 | B70_TR_Assessment | Telecom | Existing rooms | Verify | Photo references identify existing telecom rooms 15E, 1234, 353, 308A and 408A; verify all active services and transfer plan. | B78_Assessment!A66:J66
78 | B70_TR_Assessment | Telecom | B30 | Verify | TR scope includes wall-mounted CCTV cameras and PACS for TR doors. Verify CR/RX/DC/ES/MD, controller and VMS integration. | B78_Assessment!A70:J70
78 | B70_TR_Assessment | Telecom | B35 | Verify | Verify PACS/CCTV integration and door hardware coordination. | B78_Assessment!A71:J71
78 | B70_TR_Assessment | Telecom | 1232 | Verify | Verify first-level TR PACS/CCTV and VMS integration. | B78_Assessment!A72:J72
78 | B70_TR_Assessment | Telecom | 227A | Verify | Verify second-level TR PACS/CCTV and VMS integration. | B78_Assessment!A73:J73
78 | B78_Assessment | Security | 342 | Verify | Verify third-level TR PACS/CCTV and VMS integration. | B78_Assessment!A74:J74
78 | B78_Assessment | Security | 401 | Verify | Verify fourth-level TR PACS/CCTV and VMS integration. | B78_Assessment!A75:J75
78 | B78_Assessment | Security | Existing rooms | Verify | Verify existing PACS/security devices are protected-in-place or recabled without VMS/PACS disruption. | B78_Assessment!A76:J76
80 | B78_Assessment | Fire | 102 | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, and temporary firestopping during cable pulls. | B80_Assessment!A20:J20
80 | B78_Assessment | Fire | 127A / 126 | Verify | Existing telecom closet/room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | B80_Assessment!A21:J21
80 | B78_Assessment | HVAC | 102 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 102 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet interface, thermostat/control point, condensate pump/path, disconnects, and high-temperature alarm. | B80_Assessment!A25:J25
80 | B78_Assessment | HVAC | 127A / 126 | Verify | Existing telecom room/closet may remain active during cutover. Verify existing environmental condition and whether any active equipment remains after migration to Room 102. | B80_Assessment!A26:J26
80 | B78_Assessment | Electrical | 102 | Verify | Electrical plans/schedules identify B80-TR102A fed from BUS-B80-MDP and B80-TR102B fed from BUS-B80-E1, with rack receptacles, normal/emergency circuits, CU-1-01, SPD requirements and 30-day load measurement requirements. | B80_Assessment!A30:J30
80 | B78_Assessment | Electrical | 127A / 126 | Verify | Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | B80_Assessment!A31:J31
80 | B78_Assessment | Telecom | 102 | Verify | 80T-701 identifies RM102 with 117 WAO total, 98 active ports per survey, 195 total ports per schedule, and 215 total ports with 10% allowance. Rack IDs include TR01-102-1 and TR01-102-2; rack elevation shows 1 new rack plus future rack with switches, Cat6A patch panels, Cat5e patch panel, Fiber LIU, UPS and PDU. | B80_Assessment!A35:J35
80 | B80_Assessment | Telecom | 127A / 126 | Verify | Existing rack elevation shows Cisco switches, legacy optical Fiber LIU on wall, multiple legacy Ortronics 24/48-port patch panels, legacy Cat5e 24-port patch panel, and APC floor UPS. Contractor must transfer existing devices to new rack and protect active services. | B80_Assessment!A36:J36
80 | B80_Assessment | Security | 102 | Verify | Electrical/telecom plans show access-control scope and camera 102-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, electric strike, camera/VMS integration, and door hardware coordination. | B80_Assessment!A40:J40
80 | B80_Assessment | Security | 127A / 126 | Verify | Verify existing security/PACS equipment conditions and whether any existing camera/security device is protected, recabled, or removed during cutover. | B80_Assessment!A41:J41
82 | B80_Assessment | Fire | 102 | Verify | Cover sheet states Building 82 receives a Telecom Enclosure and fire protection scope is excluded. Still verify rated penetrations, 4-inch sleeve, wall/floor openings, temporary firestopping, and life-safety device impacts. | B82_Assessment!A20:J20
82 | B80_Assessment | Fire | B01-A | Verify | Existing telecom room; verify protection-in-place and firestopping after cable transfer or reuse. | B82_Assessment!A21:J21
82 | B80_Assessment | HVAC | 102 | Verify | Mechanical and electrical drawings show IU-1-01 in/near Telecom Room 102 and CU-1-01 outdoor unit. Mechanical notes call for BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency/standby source, condensate pump/path, disconnects, controls, and high-temp alarm. | B82_Assessment!A25:J25
82 | B80_Assessment | HVAC | B01-A | Verify | Existing telecom room may remain active during cutover. Verify existing environmental conditions and whether active equipment remains after transfer to Room 102. | B82_Assessment!A26:J26
82 | B80_Assessment | Electrical | 102 | Verify | Electrical plans/schedules identify TE receptacle, CU-1-01, B82-MDP and B82-P-EMER sources, with SPD devices integral to new telecom panelboards. Verify receptacle type, grounding/bonding, emergency source, labels, and circuit loading. | B82_Assessment!A30:J30
82 | B80_Assessment | Electrical | B01-A | Verify | Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | B82_Assessment!A31:J31
82 | B80_Assessment | Telecom | 102 | Verify | 82T-701 identifies RM102 with 26 WAO total, 31 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. Rack ID TR01-102-01. Cable tray schedule totals 278 ft on first level. New enclosure includes APC UPS, two PDUs, network switch, Cat6A patch panel and Fiber LIU. | B82_Assessment!A35:J35
82 | B82_Assessment | Telecom | B01-A | Verify | Existing B01-A elevations identify Cisco switches, cable management, two Ortronics 24-port patch panels with 11 and 6 used, existing patch panels and APC floor UPS. Field verify active services and transfer plan to new TE. | B82_Assessment!A36:J36
82 | B82_Assessment | Security | 102 | Verify | Building 82 appears to create a TE enclosure rather than a full TR door/PACS package. Verify existing cameras/security devices in Room 102 and ensure no camera angle or VMS integration is disrupted. | B82_Assessment!A40:J40
82 | B82_Assessment | Security | B01-A | Verify | Keynotes indicate existing cameras are to be retained and re-used. Verify security/access conditions and whether any legacy security equipment is present at existing telecom room. | B82_Assessment!A41:J41
BCH | B82_Assessment | Fire | 107 | Verify | Cover sheet states BCH receives a Telecom Enclosure and mechanical/fire protection scope has been excluded. Still verify existing life-safety protection, rated penetrations, 4-inch sleeve fire caulk, temporary firestopping and abandoned penetration patching. | BCH_Assessment!A20:J20
BCH | B82_Assessment | Fire | 00 / 107 | Verify | TE-only scope does not appear to require new FEC/fire sprinkler work, but all wall/floor/ceiling penetrations must be sealed and rated assemblies maintained. | BCH_Assessment!A21:J21
BCH | B82_Assessment | HVAC | 107 | N/A | Cover sheet explicitly excludes mechanical scope. Verify existing room ambient conditions are acceptable for TE equipment and that no active network equipment will overheat. | BCH_Assessment!A25:J25
BCH | B82_Assessment | HVAC | 00 / 107 | N/A | If the final scope is a 45RU new telecom room rather than a small TE, HVAC exclusion should be confirmed with VA/AE because telecom-room heat load may differ from TE assumptions. | BCH_Assessment!A26:J26
BCH | B82_Assessment | Electrical | 107 | Verify | Electrical plan includes first-level electrical work and notes for new wall-mount telecom enclosure, grounding/bonding and camera. Verify circuit source, receptacle type, UPS/PDU load, emergency source if required, grounding/bonding and labels. | BCH_Assessment!A30:J30
BCH | B82_Assessment | Electrical | 00 / 107 | Verify | BCHT-604 shows 12RU TE equipment with APC UPS and PDUs and also a BCH 45RU new telecom room elevation. Confirm exact UPS/PDU/rack power requirement before acceptance. | BCH_Assessment!A31:J31
BCH | B82_Assessment | Telecom | 107 | Verify | BCHT-101 identifies telecom plan first level and enlarged Room 107. BCHT-604 identifies new telecom room/no existing elevations. There is no BCHT-701 schedule in the drawing index, so WAO/cable-tray totals must be field verified from plans and contractor coordination drawings. | BCH_Assessment!A35:J35
BCH | BCH_Assessment | Telecom | 00 / 107 | Verify | BCHT-604 identifies a 12RU TE elevation: APC UPS, two PDUs, network switch, 48-port Cat6A patch panel and Fiber LIU. Also shows BCH Crescent House Room 107 new telecom room elevation. Confirm governing rack/enclosure and labeling. | BCH_Assessment!A36:J36
BCH | BCH_Assessment | Security | 107 | Verify | Telecom/electrical notes reference new IP-addressable camera with wall mount at 8'-6" A.F.F. and VMS integration. Verify whether PACS applies; TE buildings typically do not create full TR door/PACS scope. | BCH_Assessment!A40:J40
BCH | BCH_Assessment | Security | 00 / 107 | Verify | Verify existing camera/security conditions, protection-in-place, and any recabling or VMS integration required. | BCH_Assessment!A41:J41
MCR | BCH_Assessment | Fire | 107 / MCR | Verify | MCR has full fire protection scope including wet pipe and clean-agent fire suppression system. Verify preaction/clean-agent design, agent release interface, fire alarm matrix, detection, abort/release stations, room integrity and acceptance testing. | MCR_Assessment!A28:J28
MCR | BCH_Assessment | Fire | 031 | Verify | Verify fiber entrance room protection, rated penetrations, firestopping, detector/strobe coverage and no gaps after cable tray installation. | MCR_Assessment!A29:J29
MCR | BCH_Assessment | Fire | MDA-A/B | Verify | Verify sprinkler/clean-agent coverage around MDA equipment, fire alarm devices, rack clearance and final firestop assemblies. | MCR_Assessment!A30:J30
MCR | BCH_Assessment | Fire | HDA-A/B | Verify | Verify clean-agent coverage, detector placement, alarm interfaces, and open cabinet airflow protection. | MCR_Assessment!A31:J31
MCR | BCH_Assessment | Fire | Existing 107/137 | Verify | Existing systems must remain protected during temporary fiber, umbilical cord and core relocation work. Verify no impairment without approved fire watch/impairment plan. | MCR_Assessment!A32:J32
MCR | BCH_Assessment | HVAC | 107 / MCR | Verify | Telecom notes call for indoor computer room air conditioner (CRAC) units tied to building management system. Mechanical sheets included; verify redundant capacity, setpoints, humidity, condensate, controls, alarms and emergency power. | MCR_Assessment!A36:J36
MCR | BCH_Assessment | HVAC | UPS-A / UPS-B | Verify | UPS rooms/equipment require thermal load validation, ventilation, emergency power and alarm integration. Verify battery/UPS environmental requirements. | MCR_Assessment!A37:J37
MCR | BCH_Assessment | HVAC | MDA-A/B | Verify | Verify airflow/cold aisle/hot aisle assumptions, blanking panels, floor/ceiling distribution and temperature monitoring. | MCR_Assessment!A38:J38
MCR | BCH_Assessment | HVAC | HDA-A/B | Verify | Server cabinets and patch fields require stable 24/7 cooling and monitoring. Confirm no local hot spots at dense LIU/patch panel zones. | MCR_Assessment!A39:J39
MCR | BCH_Assessment | HVAC | Existing 107/137 | Verify | During split-core temporary phase, existing MCR/server equipment remains active. Verify existing cooling remains in service until cutover and decommissioning are complete. | MCR_Assessment!A40:J40
MCR | BCH_Assessment | Electrical | 107 / MCR | Verify | Electrical set includes site plan, enlarged MCR plans, one-lines and schedules. Verify switchboard/service, ATS/generator integration, normal/emergency/UPS distribution, grounding, lightning protection, SPD, load measurements and commissioning. | MCR_Assessment!A44:J44
MCR | BCH_Assessment | Electrical | MDA-A/B | Verify | MDA rack elevations include new 4-post floor cabinets, LIUs and network elements. Verify redundant A/B power feeds and PDU arrangements. | MCR_Assessment!A45:J45
MCR | BCH_Assessment | Electrical | HDA-A/B | Verify | HDA cabinets include server cabinet front/rear elevations with patch panels and active equipment. Confirm A/B feed separation, PDU mounting, load capacity and labels. | MCR_Assessment!A46:J46
MCR | BCH_Assessment | Electrical | Existing 107/137 | Verify | Existing rack elevations identify multiple APC/Chatsworth/HP PDUs, APC Smart UPS and Eaton 9PX units. Verify what transfers, what stays, and temporary power during migration. | MCR_Assessment!A47:J47
MCR | BCH_Assessment | Electrical | Site / Utility | Verify | New MCR is standalone critical infrastructure. Verify utility service, generator/ATS paths, emergency distribution, grounding electrode and ductbank/site electrical coordination. | MCR_Assessment!A48:J48
MCR | BCH_Assessment | Telecom | 107 / MCR | Verify | MCRT-101 shows new MCR with MDA-A/B, HDA-A/B, UPS-A/B, cameras and fiber path legend. MCRT-701 shows 10 WAO total, 720 WAO available, 98.1% expansion capacity, 10 total ports with 20% allowance and 359 ft cable tray. | MCR_Assessment!A52:J52
MCR | BCH_Assessment | Telecom | 031 | Verify | MCRT-701 Data Device and Circuit Schedule - Fiber Entrance Room 1: outlets 31-A/B/C/D plus security devices 07-CAM-03/04/07/08/11; Rack ID TR01-031-1. | MCR_Assessment!A53:J53
MCR | BCH_Assessment | Telecom | MDA-A/B | Verify | MCRT-607: MDA A/B racks contain horizontal distribution LIUs, hybrid FOC, 48x Cat6A to HDA, and reserved LAN/spine/aggregation elements. Maintain A/B path separation. | MCR_Assessment!A54:J54
MCR | BCH_Assessment | Telecom | HDA-A/B | Verify | MCRT-608/609: HDA A/B include 48-port Cat6A patch panels, HD fiber LIUs, backbone side A/B LIU and server cabinet arrangements. | MCR_Assessment!A55:J55
MCR | BCH_Assessment | Telecom | Existing 107/137 | Verify | Existing MCR rows 1-3 and B61 server cabinet transfer references are extensive. Maintain service using temporary fiber/umbilical cords and phased core relocation. | MCR_Assessment!A56:J56
MCR | BCH_Assessment | Security | 107 / MCR | Verify | MCRT-101 identifies cameras 07-CAM-01 through 07-CAM-12 around the MCR. Telecom notes call for IP-addressable network cameras integrated into existing VMS and PACS/access-control systems including iSTAR Edge/Avigilon ACM controller. | MCR_Assessment!A60:J60
MCR | BCH_Assessment | Security | 031 | Verify | MCRT-701 includes security camera/data devices assigned to TR01-031-1. Confirm camera IDs, mounting, cabling, and VMS commissioning. | MCR_Assessment!A61:J61
MCR | MCR_Assessment | Security | MDA-A/B | Verify | Verify camera coverage, door/access points, VMS monitoring and access control zones for critical equipment. | MCR_Assessment!A62:J62
MCR | MCR_Assessment | Security | HDA-A/B | Verify | Verify coverage of HDA cabinets, doors, motion detection and any lockable cabinet/security requirements. | MCR_Assessment!A63:J63
MCR | MCR_Assessment | Security | Existing 107/137 | Verify | Existing security systems must remain functional during transition; protect existing camera angles and access controls until final turnover. | MCR_Assessment!A64:J64
SITE | MCR_Assessment | Electrical | Overall Site | Verify | Electrical site plans ES101/ES401 are included. Existing utility locations are approximate; coordinate electrical vaults, underground electrical, storm drain manholes and sanitary manholes. | SITE_Assesment!A46:J46
SITE | MCR_Assessment | Electrical | THH / Manholes | Verify | Locking covers and handhole/manhole locations must be field verified. Confirm bonding/grounding requirements where metallic components are present. | SITE_Assesment!A47:J47
SITE | MCR_Assessment | Electrical | MCR / Provider Entrance | Verify | T-601 shows WAN/provider fiber entrances and new fiber Path A/B to the MCR. Coordinate with Century Link/service provider and MCR activation. | SITE_Assesment!A48:J48
SITE | MCR_Assessment | Electrical | Building Tie-ins | Verify | Coordinate conduit penetrations with building electrical/telecom/firestop scope and avoid conflicts with existing services. | SITE_Assesment!A49:J49
SITE | MCR_Assessment | Telecom | Campus Backbone | Verify | Legend identifies new fiber in A route, B route, and A+B routes in separate conduits. Confirm no cross-connect gaps at THHs/manholes. | SITE_Assesment!A53:J53
SITE | MCR_Assessment | Telecom | MCR Provider / WAN | Verify | Site one-line shows WAN fiber from service provider and temporary/provider extension pathways. Coordinate with MCR activation and OIT. | SITE_Assesment!A54:J54
SITE | MCR_Assessment | Telecom | Building Drops | Verify | Each building tie-in must be tested, labeled, and accepted before connection to active operations. | SITE_Assesment!A55:J55
SITE | MCR_Assessment | Telecom | THH Network | Verify | T-601 one-line lists THH #1-#19 and path counts such as 6 Path A + 4 Path B, 6 Path A + 6 Path B, 7 Path A + 7 Path B, 5 Path A + 4 Path B, and 9 Path A + 7 Path B. | SITE_Assesment!A56:J56
SITE | SITE_Assesment | Security | Campus Site Work | Verify | Coordinate staging, access, material storage, noisy work, utility interruption, trench barricades and public access with owner. | SITE_Assesment!A60:J60
SITE | SITE_Assesment | Security | Road / Parking Impacts | Verify | General notes specifically identify accessible parking and public right-of-way impacts; temporary barricades must prevent injury and protect parking signage. | SITE_Assesment!A61:J61
SITE | SITE_Assesment | Security | Critical Utility Crossings | Verify | Hand digging at existing utility crossings is in base bid. Confirm permits, Dig Safe, VA utility locate and escort requirements before excavation. | SITE_Assesment!A62:J62

## B61_Assessment
BUILDING 61 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 61 | Building Phase | PILOT | Overall Status | PILOT PHASE | Readiness | 55% | Construction Ready | YES
Review Date | 2026-06-25 19:04 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 61 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B13H-A / 124 / 226 / existing 137-137A Demarc
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing.
HVAC Status | Not Started | Electrical Status | Not Started | Telecom Status | Not Started | Fire Protection Status | Not Started | Fire Alarm Status | Not Started
Security Status | Not Started | Next Action | Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
61 | B13H-A | Basement | Basement telecom / support area | Telecom Room | 1 | 1 | Pass | 61A-400 / 61E-401 / 61T-100 / 61T-401 / 61T-604 / 61T-701 | Basement TR identified as RM B13H-A with Rack ID TR01-B13H-A-1. Schedules identify 88 WAO total, 74 active ports, 129 scheduled ports, 142 ports with 10% allowance. Electrical panels include B61-TRB13A/B. Mechanical cooling includes IU-0-01/CU-0-01.
61 | 124 | First | First-level telecom area | Telecom Room | 1 | 1 | Pass | 61A-400 / 61E-402 / 61T-101 / 61T-401 / 61T-604 / 61T-701 | First-level TR identified as Room 124 / Rack ID TR01-124-1. Electrical panels include B61-TR124A/B. Mechanical cooling includes IU-1-01/CU-1-01. Verify room naming against electrical schedule references that also call out RM137B rack receptacles.
61 | 226 | Second | Second-level telecom area | Telecom Room | 1 | 1 | Pass | 61A-401 / 61E-402 / 61T-102 / 61T-401 / 61T-605 / 61T-702 | Second-level TR identified as Room 226 / Rack ID TR01-226-1. Schedules identify 109 WAO total, 126 active ports, 156 scheduled ports, 172 ports with 10% allowance. Electrical panels include B61-TR226A/B. Mechanical cooling includes IU-2-01/CU-2-01.
61 | 137 / 137A | First | Existing server/demarc/telecom equipment rooms | Existing demarc / server transition point | 11 | 0 | Pass | 61T-402 / 61T-606 / 61T-607 / 61R-900 | Existing Room 137/137A rack inventory and demarc/server equipment include existing 4-post racks, PACS/equipment racks, APC UPS/PDU equipment, Fujitsu FLM equipment, wall-mounted patch panels, and local elevations. Protect active services and verify what remains, transfers, or is modified.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B13H-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify rated walls/open-to-deck conditions, door/security, floor finish, ladder rack/cable tray, future rack clearance, wall backing, and pathway entries.
124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify rated construction, door hardware, ceiling/deck, rack/future rack clearances, wall backing, and riser/pathway entries.
226 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR; verify rated construction, door hardware, ceiling/deck, rack/future rack clearances, wall backing, and riser/pathway entries.
137 / 137A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing demarc/server rooms; verify existing rack inventory, operational continuity, active circuits, access control, airflow and protection-in-place.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B13H-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping.
124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems.
226 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping.
137 / 137A | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B13H-A | IU-0-01 / CU-0-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms.
124 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm.
226 | IU-2-01 / CU-2-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in.
137 / 137A | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B13H-A | Verify | 5 kW / 208V rack UPS | Verify | Verify | B61-TRB13A / B61-TRB13B | Verify | Verify | Verify | Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels.
124 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B61-TR124A / B61-TR124B | Verify | Verify | Verify | Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules.
226 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B61-TR226A / B61-TR226B | Verify | Verify | Verify | Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels.
137 / 137A | Existing / Verify | Existing APC UPS/PDU | Existing / Verify | Verify | B61-TR137AA / B61-TR137AB / existing | Verify | Verify | Verify | Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B13H-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total.
124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance.
226 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations.
137 / 137A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
B13H-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration.
124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify TR door hardware and access control, CCTV camera, network door controller and integration.
226 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration.
137 / 137A | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B61-R1 | All | Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | Large multi-room scope with active demarc/server equipment.
B61-R2 | B13H-A / 124 / 226 | Hazardous material abatement plans exist for first and second levels | High | Medium | 6 | Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation | GC / IH / COR | Closed | Drawing index includes 61H-101 and 61H-102 hazardous material abatement plans.
B61-R3 | 137 / 137A | Existing server/demarc equipment may remain active during cutover | Critical | Medium | 8 | Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path | OIT / Telecom | Closed | Existing APC/Fujitsu/rack/patch equipment shown in Room 137 inventory/rack elevations.
B61-R4 | All TRs | Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR/server readiness.
B61-R5 | All TRs | Panel source, UPS/PDU and rack receptacle coordination could delay energization | Critical | Medium | 8 | Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements | Electrical / GCC | Closed | Multiple telecom panelboards and PD panels shown.
B61-R6 | All | Large cable tray scope creates coordination and firestop risk | High | Medium | 6 | Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 890 ft, first 499 ft, second 578 ft.
B61-R7 | All | Telecom/fiber cutover could affect active hospital communications and server/demarc services | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | WAO counts and active ports are substantial across B13H-A, 124 and 226.
B61-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope building with multiple divisions.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B61-Q1 | Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B61-Q2 | What active services and circuits are currently housed in Room 137/137A? | OIT / Contractor | Closed |  |  | Potential outage/cutover risk
B61-Q3 | Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? | Electrical / Designer | Closed |  |  | Electrical PMIS mapping risk
B61-Q4 | Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B61-Q5 | Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? | GC / COR | Closed |  |  | Life-safety acceptance risk
B61-Q6 | Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B61-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and temporary firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B61-Q8 | Which third-party inspections, commissioning forms and OIT acceptance records are required before turnover? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
B61-Q9 | How did this sheetget made? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B61-P001 | B13H-A | Existing Condition | Basement TR B13H-A walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and penetrations |  | Paul |  | B61-R1/B61-R2 | Closed
B61-P002 | 124 | Existing Condition | First-level TR 124 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and penetrations |  | Paul |  | B61-R1/B61-R4 | Closed
B61-P003 | 226 | Existing Condition | Second-level TR 226 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and riser penetrations |  | Paul |  | B61-R1/B61-R4 | Closed
B61-P004 | 137 / 137A | Existing Equipment | Existing server/demarc racks, APC UPS/PDU, Fujitsu equipment, patch panels, PACS/equipment racks and cable entries |  | Paul |  | B61-R3/B61-R7 | Closed
B61-P005 | All TRs | HVAC | IU/CU-0-01, IU/CU-1-01, IU/CU-2-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B61-R4 | Closed
B61-P006 | All TRs | Electrical | B61 telecom panels, PD panels, rack receptacles, UPS/PDU, breakers, SPDs, labels and grounding/bonding |  | Paul |  | B61-R5 | Closed
B61-P007 | All | Cable Tray / Firestop | Basement/first/second cable tray route, supports, seismic bracing, penetrations and before/after firestopping |  | Paul |  | B61-R6 | Closed
B61-P008 | All | Telecom / Security | Racks, Fiber LIU, Cat6A, patch panels, labels/test records, CCTV, PACS and existing equipment transfer work |  | Paul |  | B61-R7/B61-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B13H-A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Basement TR with 142 total ports including allowance, dedicated cooling, UPS/PDU, cable tray and fire/life-safety scope.
124 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | First-level TR with dedicated cooling, UPS/PDU, cable tray and potential electrical room-name mapping issue.
226 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Second-level TR with 172 total ports including allowance, dedicated cooling, UPS/PDU and riser/firestop coordination.
137 / 137A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Existing demarc/server room inventory; protect active services until cutover and acceptance complete.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 0% | 0% | 🟢 | 0%
UPS Installation | Not Started | 0% | 0% | 🟢 | 0%
Fiber Installation | Not Started | 0% | 0% | 🟢 | 0%
Firestopping | Not Started | 0% | 0% | 🟢 | 0%
Payment Confidence |  | 0% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified By | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | No | No | 0
Rack Installed | Not Started | No | No | 0
Fiber Tested | Not Started | No | No | 0
UPS Operational | Not Started | No | No | 0
Network Equipment Received | Not Started | No | No | 0
National OIT Approval | Not Started | No | No | 0
Local OIT Ready | Not Started | No | No | 0
Activation Scheduled | Not Started | No | No | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Complete | No | No | No | N/A
Cable Tray | Complete | No | No | No | N/A
Firestop System | Complete | No | No | No | N/A
HVAC Equipment | Complete | No | No | No | N/A
Electrical Equipment | Complete | No | No | No | N/A
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started | 8 | 0 | 0 | 0%
Telecom | Not Started | 8 | 0 | 0 | 0%
Mechanical | Not Started | 10 | 0 | 0 | 0%
Firestop | Not Started | 10 | 0 | 0 | 0%
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | N/A | N/A | 0
QA/QC Complete | Not Started | N/A | N/A | 0
Deficiencies Closed | Not Started | N/A | N/A | 0
OIT Ready | Not Started | N/A | N/A | 0
Documentation Complete | Not Started | N/A | N/A | 0
Recommended for Acceptance | Not Started | N/A | N/A | 0
Acceptance Readiness |  |  |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
What
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
Note on B99: Capture OIT dependencies, especially national coordination and equipment availability.
Note on B108: Capture OIT dependencies, especially national coordination and equipment availability.
Note on B120: Compare installed materials against approved submittals/spec sections.
Note on B129: Planned vs actual production supports delay/time-extension rebuttal.

## CM_PM Operations
CM/PM OPERATIONS — CONSOLIDATED REPORTING LAYER
Assessment sheets remain the source of truth. This sheet summarizes existing PMIS data by reporting section and provides one manual register only for CM/PM-specific actions, deliverables, and COR decisions.
REPORT CONTROLS
Selected Building | 61 | Report Cycle | Weekly
Period Start | 2026-07-13 | Period End | 2026-07-17
Prepared By | Paul | Reviewed With | Aisha
Buildings |  | Avg Readiness |  | Rooms |  | Open Risks |  | Open Questions |  | Active Shutdowns |  | Not Ready |  | COR Decisions
30 |  | 50.67% |  | 814 |  | 0 |  | 0 |  | 1 |  | 29 |  | 6
1. PROJECT AND ASSESSMENT STATUS
Building | Assessment Sheet | Status | Readiness | Construction Ready | Rooms | Open Risks | Open Questions | Next Action | Major Blocker | OIT Status | Acceptance Status
01 | B01_Assessment | Yellow | 50% | No | 29 | 0 | 0 | Field verify Room 107, existing B02, 138, and 282; confirm active services, existing rack/equipment transfer, B01-TR107A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 394 ft cable tray routes, and telecom cutover sequence. | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning. | Blocked | Not Ready
02 | B02_Assessment | Yellow | 50% | No | 30 | 0 | 0 | Field verify new Rooms 141, 236, 342 and existing B-06/141/236; confirm active services, rack/equipment transfer, B02-TR141A/B, B02-TR236A/B, B02-TR342A/B panel sources, CU-1-01/CU-2-01/CU-3-01 cooling assignments, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, 2,560 ft cable tray routes, and telecom cutover sequence. | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance. | Blocked | Not Ready
03 | B03_Assessment | Yellow | 50% | No | 29 | 0 | 0 | Field verify Room 101E, existing Room 107, and existing DMARC Room 101C; confirm active services, existing rack/equipment transfer, B03-TR101CA/B panel sources, CU-01 cooling assignment, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 961 ft cable tray routes, Room 107 inventory, and telecom cutover/fiber transfer sequence. | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance. | Blocked | Not Ready
04 | B04_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify TR rooms B05, 141, and 244A; confirm cooling, panel/circuiting, fire alarm/sprinkler impacts, FEC locations, and cutover/phasing plan. | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open. | Blocked | Not Ready
05 | B05_Assessment | Yellow | 55% | No | 26 | 0 | 0 | Field verify Room 150 TE location, existing 153-A equipment to remain/transition, electrical source, UPS/PDU receptacles, PACS/CCTV requirements, firestopping, and cutover sequence. | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified. | Blocked | Not Ready
06 | B06_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify existing B-01 equipment, Rooms 178 and 233, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, and telecom cutover sequence. | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open. | Blocked | Not Ready
07 | B07_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify TR B-18 and 228A; confirm rack/equipment layout, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, and telecom cutover sequence. | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open. | Blocked | Not Ready
08 | B08_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify B-15, B12B, and 2065A; confirm active services, 2065A rack layout, panel/power source, IU/CU cooling, hazardous material/abatement impacts, FEC locations, PACS/CCTV, and telecom cutover sequence. | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open. | Blocked | Not Ready
09 | B09_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify B01, 104B, and 206A; confirm existing equipment and active services, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, and telecom cutover sequence. | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open. | Blocked | Not Ready
10 | B10_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify attic Telecom Room 200A, basement normal/emergency electrical source rooms B24/B25, existing wall-mounted rack/equipment, panel sources B10-TR200AA/AB, IU/CU-1-01 cooling, FEC/fire alarm/sprinkler impacts, hazardous/abatement scope, and telecom cutover plan. | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination. | Blocked | Not Ready
12 | B12_Assessment | Yellow | 60% | No | 26 | 0 | 0 | Field verify existing fiber pathway through Building 12, existing rack/demarc/serving closet condition, floor/wall penetrations, routing from basement/first/second level telecom plans, phasing/cutover approach, and test/label/as-built deliverables. | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover. | Blocked | Not Ready
13 | B13_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify Room 124 and existing Tel Room 222; confirm active services, rack/equipment transfer, B13-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | Blocked | Not Ready
14 | B14_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify Room 119 and existing basement Tel/F Panel B.01/B2; confirm active services, rack/equipment transfer, B14-TR119A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 14 includes new first-level Telecom Room 119 and existing basement telecom rooms B.01/B2; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | Blocked | Not Ready
15 | B15_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify Room 124A, existing Tel Room 222 and basement B01; confirm active services, rack/equipment transfer, B15-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 15 includes new first-level Telecom Room 124A and existing telecom transition points at second-level Tel Room 222 and basement B01; field verification, active service cutover, 240V UPS/PDU power, dedicated heat-pump cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | Blocked | Not Ready
16 | B16_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify Room 015 and existing Room 014; confirm active services, rack/equipment transfer, B16-TR015A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, panel replacement/load measurement, and telecom cutover sequence. | Building 16 includes new basement Telecom Room 015 and existing basement Telecom Room 014; field verification, active service transfer, 240V UPS/PDU power, dedicated cooling, panel replacement/source coordination, firestopping, PACS/CCTV integration, and cable tray coordination remain open. | Blocked | Not Ready
17 | B17_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify Telecom Room 118, existing B35A, and Building 29 service path; confirm active services, B17-TR118A/B panel sources, BUS-B17-EQDP / BUS-B17-NPB1-R sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, hazardous material impacts, and cutover plan. | Building 17_29 includes new first-level Telecom Room 118 serving Building 17 and Building 29, plus existing basement Telecom Closet B35A; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, cable tray, firestopping, and PACS/CCTV integration remain open. | Blocked | Not Ready
18 | B18_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify Telecom Room 110, existing TE 111B, existing Closet 213, and all active services; confirm B18-TR110A/B panel sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, lead-paint/hazardous impacts, and cutover plan. | Building 18 includes new first-level Telecom Room 110 and existing telecom transition rooms 111B and 213; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, lead-paint/first-level hazardous material coordination, firestopping, cable tray, and PACS/CCTV integration remain open. | Blocked | Not Ready
20 | B20_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify Office 1B new TE location, existing Tel/Data Closet 8A, active services, TE01-1B-1 schedule, existing open TE cabinet, existing ground bar/patch panel/equipment box/indoor AC/backboard, 459 ft cable tray route, 10 Cat6A cross-connect cables, power/UPS/PDU source, and fiber Path A/B cutover. | Building 20 is a telecom-enclosure building, not a full TR buildout. Scope centers on new first-level Office 1B wall-mount TE enclosure and existing Tel/Data Closet 8A; mechanical and fire protection scope are excluded by the cover sheet, but field verification, active equipment transfer, fiber/copper cutover, cable tray, firestopping, power/UPS/PDU, and existing equipment protection remain open. | Blocked | Not Ready
21 | B21_Assessment | Yellow | 50% | No | 27 | 0 | 0 | Field verify new TE location at M&O Foreman Office 100A, existing B21 B1.TR, existing B19 B05TR, B19-serving-B21 relationship, active services, TR01-104-1 / 100-A schedule, 659 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, and all firestopping/penetrations. | Building 21 is combined with Building 19 and is primarily a telecom-enclosure scope. New first-level M&O Foreman Office 100A / RM 104 schedule is served by a new 12RU TE enclosure, while existing Building 21 B1.TR and Building 19 B05TR equipment remain transition points. Fire protection scope is excluded, but mechanical/electrical sheets exist for equipment support. Field verification, active-service transfer, 659 ft cable tray, firestopping, UPS/PDU power, fiber/copper cutover, and B19/B21 scope boundary remain open. | Blocked | Not Ready
22 | B22_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify Break Room 102 new TE location, existing Room 103 wall/wall-mount TE, active services, TR01-102-1 schedule, 139 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, and existing B19 port relationship. | Building 22 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new first-level Break Room 102 TE enclosure and existing first-level wall/wall-mount TE Room 103. Field verification, active service transfer, 139 ft cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, and B19 utility service relationship remain open. | Blocked | Not Ready
33 | B33_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify EEO Manager Office B23 new TE location, existing Tel Closet B17, active services, TE01-B23-1 schedule, 102 ft basement cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, existing camera/security devices, and B17 legacy port/service relationships. | Building 33 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new basement EEO Manager Office B23 TE enclosure and existing Tel Closet B17. Field verification, active service transfer, 102 ft basement cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, fiber/copper cutover, and legacy service relationships to Buildings 3, 80 and 82 remain open. | Blocked | Not Ready
61 | B61_Assessment | PILOT PHASE | 55% | YES | 29 | 0 | 0 | Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence. | Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. | Blocked | Not Ready
62 | B62_TR_Assessment | Yellow | 50% | No | 23 | 0 | 0 | Verify cooling power path, firestopping, extinguisher location, and existing conditions | Cooling / emergency power not verified | Blocked | Not Ready
70 | B70_TR_Assessment | Yellow | 50% | No | 23 | 0 | 0 | Verify cooling power path, firestopping, extinguisher locations, and migration phasing | Cooling / emergency power and existing TR phasing not verified | Blocked | Not Ready
78 | B78_Assessment | Yellow | 50% | No | 32 | 0 | 0 | Field verify rooms B30, B35, 1232, 227A, 342, 401 and existing telecom rooms 15E, 1234, 353, 308A, 408A; confirm active equipment, rack transfers, HVAC units, panel sources, UPS/PDU power, FEC locations, FA/FP modifications, PACS/CCTV, hazardous material impacts, cable tray routes, firestopping, and cutover sequence. | Building 78/78A is a very large full-scope TR building with basement through fourth-level telecom rooms, existing telecom rooms, hazardous abatement, architectural, fire protection, mechanical, electrical, security, telecom, rack elevations and photo references. Major open issues include active service cutover, dedicated HVAC validation, panel/UPS/PDU coordination, 4,849 ft cable tray routes, firestopping, PACS/CCTV, existing rack transfers, and turnover testing. | Blocked | Not Ready
80 | B80_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify Telecom Room 102 and existing 127A/126; confirm active services, existing rack/equipment transfer, B80-TR102A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, cable tray route, and telecom cutover sequence. | Building 80 includes a new first-level Telecom Room 102 and existing Tel Closet 127A / photo-reference Room 126 transition point. Field verification, active equipment transfer, dedicated cooling IU-1-01/CU-1-01, B80-TR102A/B power, 811 ft cable tray, firestopping, PACS/CCTV, existing two-post rack migration, and room-number mapping remain open. | Blocked | Not Ready
82 | B82_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify Room 102 new TE location, existing B01-A, active services, TR01-102-01 schedule, 278 ft cable tray route, 10 Cat6A cable legend, UPS/PDU source, B82-MDP/B82-P-EMER connections, IU-1-01/CU-1-01 cooling, fiber paths A/B, firestopping/sleeves, existing cameras and TE cutover plan. | Building 82 is identified as a Telecom Enclosure (TE) building on the cover sheet, with fire protection scope excluded, but mechanical sheets show IU-1-01/CU-1-01 dedicated cooling for Room 102 and electrical drawings show B82-MDP/B82-P-EMER power. Scope centers on new first-level Telecom Room 102 / 12RU enclosure and existing first-level Telecom Room B01-A transition point. Field verification, active-equipment transfer, 278 ft cable tray, firestopping, UPS/PDU power, HVAC controls, fiber/copper cutover, and room/equipment mapping remain open. | Blocked | Not Ready
BCH | BCH_Assessment | Yellow | 50% | No | 26 | 0 | 0 | Field verify Room 107, Room 00-107 rack/elevation reference, new TE/enclosure location, active services, cable tray route, power/UPS/PDU source, grounding/bonding, fiber Path A/B, 4-inch sleeve/firestop scope, camera/VMS scope, and confirm whether the BCH rack elevation is TE-only or new telecom room buildout. | Crescent House/BCH is a Telecom Enclosure (TE) scope with mechanical and fire protection excluded by the cover sheet. Scope centers on first-level Room 107 and rack/equipment location shown as Room 00-107 / BCH Crescent House. Field verification, room naming, wall-mounted TE versus 45RU room/rack elevation conflict, active-service cutover, power/UPS/PDU source, firestopping, fiber A/B routing, and cable tray/WAO quantities remain open. | Blocked | Not Ready
MCR | MCR_Assessment | Yellow | 50% | No | 31 | 0 | 0 | Field verify new MCR Room 107 / Room 031 naming, MDA-A/B and HDA-A/B rack rows, existing MCR/server equipment in 107/137, UPS-A/B, CRAC units, clean-agent/preaction/fire alarm systems, MCR panel/ATS/generator sources, camera/access control devices, fiber Path A/B, service provider entrance, cable tray/firestop scope, third-party inspections, and phased activation/cutover sequence. | MCR is the most critical EHRM infrastructure building. Scope includes new Main Computer Room, new MDA A/B rows, HDA A/B rows, existing server/MCR equipment transfer from 107/137, redundant fiber Path A/B, new CRAC cooling, UPS A/B, electrical service/ATS/generator integration, clean-agent fire suppression, wet sprinkler/fire alarm interfaces, PACS/CCTV, 359 ft cable tray, and MCR activation window. Major risk is service continuity during backbone/core migration and VA activation. | Blocked | Not Ready
SITE | SITE_Assesment | Yellow | 50% | No | 32 | 0 | 0 | Field verify all THH/manhole locations, utility depths, trench routes, concrete ductbank sizes, Path A/B conduit counts, building tie-in points, site electrical conflicts, MCR/provider entrance points, restoration limits, traffic/pedestrian controls, inspection hold points, and fiber testing/acceptance sequence. | Site package controls the redundant telecommunications backbone for the full EHRM campus. Scope includes site survey, electrical site plans, telecom site plans, enlarged views, plan/profile sheets for Path A/B, concrete ductbank, direct-bury conduit, handholes THH #1-#19, communication manholes with locking covers, concrete pullboxes, trench restoration, and the site one-line fiber diagram. Major risks are existing utility conflicts, A/B path separation, ductbank inspection before backfill, MCR activation sequencing, and coordination of multiple building tie-ins. | Blocked | Not Ready
2. FIELD AND INSPECTION ACTIVITY
Building | Fire / Life Safety | HVAC / Cooling | Electrical / UPS | Telecom / Fiber | Security / PACS / CCTV | Owner Risks | Open Questions
01 | • Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems. • Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. • Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes. • Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place. | • Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup. • Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration. • Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear. • Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating. | • Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation. • Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements. • Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition. • Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope. | • 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1. • Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan. • Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence. • Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway. | • Electrical/telecom plans show new access control, power supply/battery backup for PACS, HDP12/FIPS-compliant PIV-ready card reader with PIN pad, and camera 107-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration and door hardware coordination. • Verify existing security/CCTV equipment and any retained cameras. Maintain camera angles where existing security cameras are recabled. • Verify existing security/access conditions and protection-in-place during rack transfer. • Verify second-level existing security/CCTV impacts during cabling and equipment transfer. | • High: Existing conditions for Room 107 and transition rooms B02/138/282 not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing equipment may remain active during transfer to Room 107 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat, humidity and high-temp alarms • High: B01-TR107A/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPD, labels, 30-day load measurement and LOTO needs • High: 394 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications across basement/first/second levels — Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | • B01-Q1 — Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? [Closed] Impact: Room inventory could miss scope • B01-Q2 — What active services are currently fed from existing Rooms B02, 138 and 282? [Closed] Impact: Potential communications/security outage • B01-Q3 — What equipment from existing racks transfers to new Room 107 versus remains/decommissions? [Closed] Impact: Cutover and rack elevation risk • B01-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? [Closed] Impact: Cooling continuity unclear • B01-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? [Closed] Impact: Life-safety acceptance risk • B01-Q6 — Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Closed] Impact: Electrical readiness unknown
02 | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping. • Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping. • Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | • Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms. • Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm. • Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration. • Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete. | • Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels. • Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping. • Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits. • Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs. | • 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray. • 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope. • 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count. • Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover. | • Plans show 174-CAM-01 associated with the first-level TR area and PACS/security requirements. Verify camera/VMS integration, access controller/power supply, CR/RX/DC/ES/MD and door hardware. • Plans show 236-CAM-01. Verify camera/VMS integration, access control, door hardware, motion/detection devices and power. • Plans show 342-CAM-01 and 342A-CK-A. Verify camera/VMS integration and access control/security rough-in. • Maintain existing camera angles when re-cabling and protect existing PACS/equipment racks during transfer. | • High: Existing conditions for Rooms 141/236/342 and existing B-06/141/236 not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing equipment may remain active during transfer to new TRs — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified — Confirm each IU/CU serving each TR, power source, condensate route, controls, BACnet, thermostat and high-temp alarms • High: B02-TR141/236/342 A/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPDs, labels, 30-day load measurement and LOTO needs • High: 2,560 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications across several floors — Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | • B02-Q1 — Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? [Open] Impact: Room inventory could miss scope • B02-Q2 — What active services are currently fed from existing Rooms B-06, 141 and 236? [Open] Impact: Potential communications/security outage • B02-Q3 — What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? [Open] Impact: Cutover and rack elevation risk • B02-Q4 — Which IU/CU pair serves each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B02-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? [Open] Impact: Life-safety acceptance risk • B02-Q6 — Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown
03 | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse. • Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer. • Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations. | • Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm. • Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete. • Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains. • No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements. | • Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements. • Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements. • Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer. • Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations. | • 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2. • Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover. • Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted. • Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced. | • Plans require PACS for TR doors and electrical details include access-controlled door rough-in. Verify access controller, power supply/battery backup, CR/RX/DC/ES/MD devices, reader, strike and door hardware coordination. • Enlarged plan and schedule identify 101C-CAM-01 and 101C-CK-A. Verify camera/VMS integration, existing camera angles and protection-in-place. • Verify existing security/CCTV/PACS impacts during basement telecom room transfer. • Maintain existing camera angles when re-cabling; verify WAP/security/clock/Centrak devices are relabeled and tested. | • High: Existing conditions for Room 101E and transition rooms 107/101C not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing DMARC/fiber/telecom equipment may remain active during transfer to Room 101E — Document active services, protect in place, identify OIT/provider cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified — Confirm CU-01/IU serving Room 101E, power source, condensate, controls, BACnet, thermostat and high-temp alarms • High: B03-TR101CA/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPDs, PXR20 trip units, labels, 30-day load measurement and LOTO needs • High: 961 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications and provider/DMARC services — Require cutover plan, test records, labels, as-builts, OIT/provider coordination and VA acceptance before active connection | • B03-Q1 — Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? [Open] Impact: Room inventory could miss scope • B03-Q2 — What active services are currently fed from existing Room 107 and DMARC Room 101C? [Open] Impact: Potential communications/provider outage • B03-Q3 — What existing equipment transfers to new Room 101E versus remains/decommissions? [Open] Impact: Cutover and rack elevation risk • B03-Q4 — Which IU/CU pair serves Room 101E and is it on emergency/backup power? [Open] Impact: Cooling continuity unclear • B03-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? [Open] Impact: Life-safety acceptance risk • B03-Q6 — Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown
04 | • Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning. • FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies. • Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations. | • Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up. • Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control. • Verify cooling unit, routing, condensate, controls, and emergency/backup power path. | • Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits. • Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting. • Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source. | • New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • TR/panel identified; verify rack elevation and pathway details against 04T sheets. | • Verify access-controlled TR door, camera, and VMS/PACS integration. • Architectural notes require door/access control coordination; verify card reader/electric strike rough-in. • Verify room security details and device integration with VA systems. | • High: Existing conditions across basement/first/second TR areas not verified — Perform existing conditions survey with photos before mobilization • High: Basement TR routing may conflict with existing utilities / abatement areas — Coordinate hazardous material survey, utility locations, penetrations, and pathway routing • High: 1-hour fire/smoke-rated envelope and 45-minute door not field verified — Inspect rated walls, door/frame, ceiling/open-to-deck conditions, and penetrations • Critical: Cooling emergency power / 24/7 continuity not verified — Confirm source power for indoor/outdoor units, controls, condensate pumps, and alarms • High: UPS/PDU/rack electrical source and load coordination unresolved — Verify panel schedules, source, SPD, breaker sizes, labeling, and load measurements • Critical: Telecom/fiber cutover could affect active hospital communications — Require phasing plan, test results, and VA/OIT acceptance before cutover | • B04-Q1 — Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? [Open] Impact: Incomplete room inventory / missed scope • B04-Q2 — Are B05, 141, and 244A cooling systems on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B04-Q3 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B04-Q4 — What is the approved migration and cutover sequence for active Building 04 services? [Open] Impact: Potential communications outage • B04-Q5 — Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? [Open] Impact: Work stoppage or exposure risk • B04-Q6 — Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? [Open] Impact: Electrical delay or overload risk
05 | • Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts. • Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling. | • Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling. • Existing wall/wall-mount TE area; verify existing environmental conditions during field survey. | • 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source. • Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover. | • New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU. • Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records. | • Project general scope includes CCTV and PACS for telecom spaces; verify whether TE location receives camera/access control or is served by existing room controls. • Verify existing security protection and whether access-control work is needed for existing TE area. | • High: Telecom Enclosure installation details not field verified — Survey wall/backing, clearances, power, conduit/wireway, and access path before installation • Critical: Existing legacy equipment/cabling may remain active during cutover — Document active services, create cutover plan, protect-in-place until new TE is operational • Medium: Mechanical/fire protection scope excluded may hide interface risks — Confirm no added cooling/sprinkler work is required and document basis for N/A • High: Electrical panel/circuit source for TE equipment not confirmed — Verify 05E-401/501/601/701 schedules, UPS/PDU receptacles, labels, and emergency power source • High: Firestopping/penetration sealing still required despite fire protection scope exclusion — Inspect all new and reused conduits, sleeves, wall/floor penetrations, and temporary firestop • Medium: Commissioning / acceptance documentation may be treated as minor due to TE scope — Track testing, labeling, OIT acceptance, third-party inspections, and as-builts | • B05-Q1 — Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? [Open] Impact: Room inventory could be wrong • B05-Q2 — What active services are currently fed from the existing 153-A TE/legacy patch panels? [Open] Impact: Potential communications outage • B05-Q3 — What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? [Open] Impact: Cutover risk • B05-Q4 — Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? [Open] Impact: Power source cannot be verified • B05-Q5 — Is emergency/backup power required or provided for the TE UPS/PDU source? [Open] Impact: Continuity requirement unclear • B05-Q6 — Are firestopping locations and surface raceway/conduit routes shown and coordinated? [Open] Impact: Rated assembly/firestop risk
06 | • Existing equipment area; verify no cabling penetrations are left unsealed. • Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs. • Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft. | • Verify basement equipment environmental condition and any heat/load issues during cutover. • Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route. • Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls. | • Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements. • Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation. • Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power. | • Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS. • Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification. • Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | • Verify existing basement access/security while protecting active equipment. • Electrical enlarged plan references existing card reader to remain/protect in place and new tri-tech motion sensor; verify PACS/CCTV integration. • Verify door hardware/access control, motion sensor, camera, and VA security integration. | • High: Existing conditions across B-01, 178 and 233 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing basement equipment may remain active during cutover — Document active services and protect in place until new system is tested and accepted • Critical: Electrical panel replacement/new telecom power could interrupt active systems — Coordinate load measurement, panel renovation, shutdowns and temporary power plan • High: Room 233 conversion/rated wall and door work may impact adjacent patient toilet/private bath areas — Verify phasing, barriers, infection control and temporary life-safety provisions • Critical: Dedicated cooling emergency power, controls, condensate and BACnet interface not verified — Confirm emergency power source, disconnects, condensate routes, BACnet adapter and high-temp alarms • Critical: Fire alarm/sprinkler impairments and penetrations may affect occupied operations — Track impairments, fire watch, temporary firestop and third-party reports | • B06-Q1 — Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? [Open] Impact: Room inventory could miss scope • B06-Q2 — What active services are fed from existing B-01 and Room 178 legacy equipment? [Open] Impact: Potential communications outage • B06-Q3 — What is the approved cutover sequence for B-01, 178 and 233? [Open] Impact: Cutover risk • B06-Q4 — Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B06-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B06-Q6 — Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? [Open] Impact: Electrical readiness unknown
07 | • Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination. • Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications. | • Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm. • Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route. | • Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement. • Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels. | • 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU. • TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover. | • Verify access control, door hardware and CCTV/PACS integration for basement TR. • Architectural notes require access control hardware modifications at new rated door; verify card reader, electric strike, door position switch, motion sensor and camera. | • High: Existing conditions for B-18 and 228A not field verified — Perform existing conditions survey with photos before mobilization • High: Basement TR conversion may conflict with existing utilities, office finishes or active pathways — Verify routing, clearances, penetrations, existing conduit and access before work • High: Second-floor rated wall/door work and exterior furring wall/window enclosure could affect schedule — Coordinate architectural work, door/frame, wall rating, furring wall, finishes and infection control barriers • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignments, emergency source, BACnet/interface, condensate pump routing and alarm points • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B07-TRB18A/B and B07-TR228A/B panel schedules, circuit labels, SPDs and load measurements • Critical: Telecom/fiber cutover may affect active hospital communications — Require cutover plan, test results, OIT coordination and VA acceptance before active connection | • B07-Q1 — Confirm final TR scope: B-18 basement and 228A second floor only? [Open] Impact: Room inventory could miss scope • B07-Q2 — Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? [Open] Impact: Cooling scope unclear • B07-Q3 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B07-Q4 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B07-Q5 — What active services are currently fed from B-18 and/or existing pathways serving 228A? [Open] Impact: Potential communications outage • B07-Q6 — Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? [Open] Impact: Electrical readiness unknown
08 | • Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected. • Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers. • Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades. | • Verify existing environmental conditions and whether active legacy equipment remains during cutover. • Field verify whether TE equipment load requires cooling or if served by existing building HVAC. • Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls. | • Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements. • Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel. • Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope. | • Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS. • Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance. • New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS. | • Verify existing basement access/security while protecting active equipment. • 45-minute door shown; verify access-control hardware applicability and whether TE is secured. • Door schedule/hardware note requires coordination with electrical/access control; verify card reader, electric strike, door position, motion sensor, camera and VA integration. | • High: Existing conditions for B-15, B12B and 2065A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing basement legacy equipment may remain active during cutover — Document active services, protect in place and define cutover/demo sequence • High: Basement B12B appears as Office in architectural schedule but TE in telecom/electrical schedules — Field verify actual TE location, room name, door/wall rating and panel/cable routing • High: Second-floor Telecom Room conversion includes rated wall/door/open-to-deck work and possible hazardous material impacts — Coordinate architectural work, dust barriers, floor abatement, FEC and rated assemblies before construction • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignment, emergency source, BACnet/interface, condensate routing and alarm points • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B08-TR2065AA/AB panel schedules, rack receptacles, SPD, labels and load measurement requirements | • B08-Q1 — Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? [Open] Impact: Room inventory may miss scope • B08-Q2 — What active services are currently fed from existing B-15 equipment? [Open] Impact: Potential communications outage • B08-Q3 — Is B12B truly a TE/equipment location or only a cabling pathway/service area? [Open] Impact: Scope ambiguity • B08-Q4 — Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? [Open] Impact: Cooling continuity unclear • B08-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? [Open] Impact: Life safety acceptance risk • B08-Q6 — Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown
09 | • Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR. • Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft. • Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations. | • Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms. • Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power. • Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power. | • Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes. • Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits. • Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits. | • Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover. • Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. • Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | • Enlarged plans show existing/new security boxes, network door controller, camera/security scope; verify PACS/CCTV integration and protection of active security systems. • First-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 104B camera designation; verify card reader, electric strike, door contact, motion and camera. • Second-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 206A camera designation; verify PACS/VMS integration and commissioning. | • High: Existing conditions for B01, 104B and 206A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Basement TR includes existing equipment and could remain active during cutover — Document active services, protect-in-place and define cutover/demo sequence • High: Hazardous material abatement plans exist for basement, first and second levels — Coordinate ACM/lead/abatement review before penetrations, flooring removal or ceiling/wall work • High: Rated wall/door work and fire/smoke assemblies could affect schedule and acceptance — Verify wall ratings, door/frame rating, penetrations, smoke/fire barriers and access control hardware • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignments, emergency source, BACnet/interface, condensate routing and alarms • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B09-TRB01A/B, B09-TR104BA/B, B09-TR206AA/B schedules, SPDs, labels and load measurements | • B09-Q1 — Confirm final TR scope: B01 basement, 104B first level, and 206A second level? [Open] Impact: Room inventory may miss scope • B09-Q2 — What active services are currently fed from B01 existing equipment/security/network devices? [Open] Impact: Potential communications/security outage • B09-Q3 — What hazardous/abatement steps apply to B01, 104B and 206A work areas? [Open] Impact: Work delay or exposure risk • B09-Q4 — Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B09-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B09-Q6 — Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown
10 | • Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping. • Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place. • Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment. | • Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm. • No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work. • No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted. | • Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels. • Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing. • Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required. | • 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover. • Coordinate telecom power pathways through/source from basement electrical room if applicable. • Coordinate emergency source/backup power pathways for telecom equipment and cooling. | • General scope requires PACS/CCTV for TR doors; verify door hardware, access controller, camera/VMS integration and any existing attic access/security constraints. • Verify security impact only if electrical source room access or devices are modified. • Verify emergency electrical room security impact if work requires access control changes. | • High: Attic Telecom Room existing conditions and access not field verified — Survey Room 200A, attic access route, existing rack/equipment, floor/deck conditions, clearances and utilities • High: Hazardous material abatement plan exists for attic level — Coordinate attic abatement/IH review before penetrations, ceiling/floor work, cabling or HVAC/electrical installation • Critical: Existing wall-mounted rack/equipment may remain active during cutover — Document active services, protect in place and develop night-shift cutover/temporary rack plan • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 capacity, power source, condensate routing, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, generator/ATS path and shutdown sequencing unclear — Verify B10-MDP, B10-L10-E, ATS-B10-LSD, panel feeders, load measurement and LOTO before electrical work • Critical: Fire alarm/sprinkler/firestopping work in attic TR could affect occupied operations — Track impairments, fire watch, sprinkler/head changes, FA device work, rated penetrations and temporary firestopping | • B10-Q1 — Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? [Open] Impact: Room inventory could miss scope • B10-Q2 — What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? [Open] Impact: Potential communications outage • B10-Q3 — What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? [Open] Impact: Work delay/exposure risk • B10-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? [Open] Impact: Cooling continuity unclear • B10-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? [Open] Impact: Life-safety acceptance risk • B10-Q6 — Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? [Open] Impact: Electrical readiness unknown
12 | • No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route. • No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work. | • No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment. • Field verify existing environmental conditions only if existing service point/equipment is accessed. | • No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown. • Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling. | • Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing. • 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only. | • No new TR door or PACS/CCTV package shown for Building 12; verify security access only for work areas and existing equipment rooms. • Confirm access requirements to existing closet/demarc while protecting active operations. | • High: Fiber-only scope could be mistaken for full TR scope or skipped as minor work — Clearly tag Building 12 as fiber-only and verify required fiber path, testing, labels and acceptance deliverables • High: Existing pull-through pathway not field verified — Trace basement/first/second level pathway, conduit/cable tray capacity, pull points and access before scheduled pull • Critical: Existing service continuity during fiber pull/cutover may not be defined — Coordinate with VA OIT, submit phasing/cutover plan, and maintain legacy service until new fiber is tested and accepted • High: Pathway penetrations/firestopping may be overlooked because there is no architectural/FP package — Inspect all new/reused penetrations and require permanent or temporary firestopping at end of shift • Medium: Existing termination/demarc location and ownership unclear — Field document existing rack/demarc/serving closet and confirm where new fiber terminates or passes through • High: Test reports, labels and as-builts may be incomplete for fiber-only work — Track fiber OTDR/certification, labeling, route documentation and VA/OIT acceptance before closeout | • B12-Q1 — Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? [Open] Impact: Scope misunderstanding • B12-Q2 — What exact pathway does the Building 12 fiber take through basement, first and second levels? [Open] Impact: Fiber pull and access risk • B12-Q3 — Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? [Open] Impact: Termination and ownership unclear • B12-Q4 — Are existing conduits/cable trays available and below fill limits for the new fiber? [Open] Impact: Pathway capacity risk • B12-Q5 — Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? [Open] Impact: Life safety/firestop risk • B12-Q6 — What is the approved cutover/testing/acceptance sequence for Building 12 fiber? [Open] Impact: Possible outage or acceptance delay
13 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | • Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B. • Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124. | • Electrical enlarged plan shows security/access-control device callouts at Room 124 and 124-CAM-01 camera designation; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 124 and existing Tel Room 222 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing Tel Room 222 equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B13-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B13-Q1 — Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? [Open] Impact: Room inventory could miss scope • B13-Q2 — What active services are currently fed from existing Tel Room 222 equipment? [Open] Impact: Potential communications/security outage • B13-Q3 — What hazardous/abatement steps apply to first-level Room 124 work? [Open] Impact: Work delay or exposure risk • B13-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? [Open] Impact: Cooling continuity unclear • B13-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? [Open] Impact: Life-safety acceptance risk • B13-Q6 — Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
14 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing basement tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Existing basement telecom room; verify no unsealed penetrations remain after cable transfer or reuse. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 119 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel/F Panel room; verify existing environmental conditions during cutover and whether legacy equipment remains active. • Existing telecom room reference; field verify cooling/ventilation and active equipment condition. | • Electrical plan/schedules identify B14-TR119A/B, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and panel load measurement requirements. • Existing basement wall-mounted TE/equipment area; verify power source, active equipment, UPS/PDU status, and transition requirements before disconnect or removal. • Existing telecom room photo reference; confirm power sources and any cutover requirements. | • 14T-701 identifies Room 119 schedule: 44 WAO total, 29 active ports per survey, 76 total ports per schedule, and 84 total ports with 10% allowance. New Rack ID TR01-119-1 serves first and second level outlets with Fiber Path A/B. • Existing Room B.01 equipment includes wall-mounted TE, Cisco switch/legacy patch panel, telco patch, plywood backboards, and legacy Fiber LIU; verify active services and transfer plan to Room 119. • Existing basement telecom room B2 is identified by photo reference; verify active devices, routing, and relation to B.01. | • Telecom/electrical plans show 119-CAM-01 and security/access-control scope for Room 119; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Verify whether existing security equipment remains, is relocated, or requires temporary protection during cutover. • Verify security/access conditions and whether any legacy security equipment is present. | • High: Existing conditions for Room 119 and existing basement telecom rooms B.01/B2 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing basement telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B14-TR119A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B14-Q1 — Confirm final telecom scope: new Room 119 and existing basement B.01/B2 transition only? [Open] Impact: Room inventory could miss scope • B14-Q2 — What active services are currently fed from existing B.01/B2 equipment? [Open] Impact: Potential communications/security outage • B14-Q3 — What hazardous/abatement steps apply to first-level Room 119 work? [Open] Impact: Work delay or exposure risk • B14-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 119? [Open] Impact: Cooling continuity unclear • B14-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 119? [Open] Impact: Life-safety acceptance risk • B14-Q6 — Are B14-TR119A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
15 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Existing basement telecom/crossover room; verify no unsealed penetrations remain after cable transfer or reuse. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124A and CU-1-01 outdoor heat-pump/A/C unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 is shown with existing/remain indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. • Existing basement telecom/crossover space; verify environmental conditions and whether active equipment remains during cutover. | • Electrical enlarged plans and schedules identify B15-TR124AA/AB, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and 30-day load measurement requirements. • Existing rack/equipment area; verify power source, active equipment, APC floor UPS status, and transition requirements before disconnect or removal. • Existing B-01 crossover; verify power sources and cutover needs for legacy patch panel/crossover. | • 15T-701 identifies Room 109A schedule but field plan/electrical room callouts identify Telecom Room 124A; schedule has 62 WAO total, 76 active ports per survey, 101 total ports per schedule, and 111 total ports with 10% allowance. New Rack ID TR15-109A-01 serves basement, first and second level outlets. • Existing Room 222 equipment includes wall/wall-mounted TE, Cisco switches, legacy 48-port patch panels, ground bar, plywood backboard, security cabinet, and floor UPS; verify active services and transfer plan to Room 124A. • Existing B-01 crossover includes legacy 24-port patch panel; verify active devices, routing, and relation to Room 222 and Room 124A. | • Telecom/electrical plans show 124A-CAM-1 and security/access-control scope for Room 124A; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Verify security/access conditions and whether any legacy security equipment is present. | • High: Existing conditions for Room 124A and existing telecom rooms 222/B01 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B15-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B15-Q1 — Confirm final telecom scope: new Room 124A and existing Rooms 222/B01 transition only? [Open] Impact: Room inventory could miss scope • B15-Q2 — Why does 15T-701 reference RM 109A while plans and electrical schedules identify Telecom Room 124A? [Open] Impact: Room naming mismatch could affect PMIS tracking • B15-Q3 — What active services are currently fed from existing Room 222 and B01 equipment? [Open] Impact: Potential communications/security outage • B15-Q4 — What hazardous/abatement steps apply to first-level Room 124A work? [Open] Impact: Work delay or exposure risk • B15-Q5 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124A? [Open] Impact: Cooling continuity unclear • B15-Q6 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124A? [Open] Impact: Life-safety acceptance risk
16 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 015 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Telecom Room 014; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • Electrical plans/schedules identify B16-TR015A/B, 240V rack UPS requirements, rack receptacles, TR receptacles, lighting, access controller, CU-1-01, SPD requirements, existing panel demolition/replacement, and 30-day load measurement requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 16T-701 identifies Room 015-A schedule: 25 WAO total, 25 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. New Rack ID TR01-015-A-1 serves basement, first, second and attic level outlets. • Existing Room 014 equipment includes wall/TE rack, floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU; verify active services and transfer plan to Room 015. | • Telecom/electrical plans show 015-CAM-1 and security/access-control scope for Room 015; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Room 014; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 015 and existing Telecom Room 014 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • High: Basement TR buildout may conflict with existing utilities, water heater/stair/storage conditions and pathway routing — Survey adjacent Water Heater 010, Vacant 011/012/013, Stair 014, pathway/ductbank routing, and constructability constraints • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B16-TR015A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B16-Q1 — Confirm final telecom scope: new Room 015 and existing Room 014 transition only? [Open] Impact: Room inventory could miss scope • B16-Q2 — What active services are currently fed from existing Room 014 equipment? [Open] Impact: Potential communications/security outage • B16-Q3 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 015? [Open] Impact: Cooling continuity unclear • B16-Q4 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 015? [Open] Impact: Life-safety acceptance risk • B16-Q5 — Are B16-TR015A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown • B16-Q6 — Which existing panel/circuit breaker/feeder demolition and replacement affects Room 015 telecom power? [Open] Impact: Panel outage/cutover risk
17 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom closet; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Verify firestopping at pathway penetrations between Building 17 and Building 29 and any rated floor/wall assemblies. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 118 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing B35A is shown with existing indoor AC unit; verify whether it remains active, is abandoned, or needs temporary protection during cutover. • No dedicated cooling expected for pathway; verify any equipment cabinets or active service locations in Building 29 if applicable. | • Electrical plans/schedules identify B17-TR118A fed from BUS-B17-NPB1-R and B17-TR118B fed from BUS-B17-EQDP, with TR RM118 rack receptacles, 208V UPS/PDU equipment, CU-1-01, SPD requirements, and 30-day load measurement requirements. • Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. • Verify whether any Building 29 equipment or extension path requires power, grounding, bonding, or labeling tied back to B17 TR 118. | • 17_29T-701 identifies Room 118 schedule: 113 WAO total, 67 active ports per survey, 154 total ports per schedule, and 169 total ports with 10% allowance. Rack ID TR17-118-1 serves basement, first, second-level outlets and Building 29 path. • Existing Room B35A equipment includes SERTEX utility service ports, legacy Ortronics patch panels, Cisco switches, wall-mounted TE, Fiber/legacy equipment, security cabinet, and floor UPS; verify active services and transfer plan to Room 118. • Building 29 is shown served from B17; verify fiber from Building 17 to Building 29, path to B29 4-inch PVC, outlet labels, test records and as-builts. | • Telecom/electrical plans show 118-CAM-01 and security/access-control scope for Room 118; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in B35A; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Verify Building 29 pathway and any security scope tied into B17 TR 118/VMS/PACS. | • High: Existing conditions for Room 118, B35A and Building 29 service path not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 208V UPS/PDU and panel source coordination could delay energization — Verify B17-TR118A/B schedules, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, SPD, labels, load measurement and LOTO needs • High: Cable tray and pathway scope is large and crosses multiple levels/building service boundary — Verify 517 ft cable tray, supports, seismic bracing, 40% fill, path to B29 4-inch PVC, penetrations and labeling before install | • B17-Q1 — Confirm final telecom scope: new Room 118, existing B35A, and Building 29 served from B17? [Open] Impact: Room inventory or PMIS mapping could miss scope • B17-Q2 — What active services are currently fed from existing B35A equipment? [Open] Impact: Potential communications/security outage • B17-Q3 — What exact Building 29 outlets/devices are served through TR17-118-1? [Open] Impact: Building 29 scope boundary unclear • B17-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 118? [Open] Impact: Cooling continuity unclear • B17-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 118? [Open] Impact: Life-safety acceptance risk • B17-Q6 — Are B17-TR118A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
18 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing TE room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. • Existing second-level closet; verify protection-in-place and firestopping after transfer or abandonment. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 110 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing TE 111B; verify existing environmental conditions during cutover and whether legacy equipment remains active. • Existing Closet 213; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • Electrical plans/schedules identify B18-TR110A/B, 208V rack UPS requirements, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and telecom panelboard schedule requirements. • Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. • Existing rack/equipment area; verify active equipment, APC UPS status, source circuits, SERTEX utility service and transfer requirements before disconnect/removal. | • 18T-701 identifies RM 111A schedule: 86 WAO total, 61 active ports per survey, 122 ports per schedule, and 134 total ports with 10% allowance. New rack elevation is Room 110, 1 rack plus future, with UPS, Future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. • Existing Room 111B equipment includes wall-mounted rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber optic housing; verify active services and transfer plan to Room 110. • Existing Room 213 equipment includes SERTEX utility service ports, Cisco switch, multiple legacy Ortronics patch panels, wall/wall-mount TE and APC floor UPS; verify active services and transfer plan to Room 110. | • Telecom/electrical plans show 111A-CAM-01 and security/access-control scope for the new TR area; verify room naming, CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in 111B; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Existing security cabinet shown in 213; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 110, Room 111B and Room 213 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material / lead-based paint abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 208V UPS/PDU and panel source coordination could delay energization — Verify B18-TR110A/B schedules, rack receptacles, SPD, labels, source circuits and LOTO needs • High: Cable tray and pathway scope crosses first and second levels — Verify 315 ft cable tray, supports, seismic bracing, 40% fill, penetrations, coordination with lighting/HVAC and labeling before install | • B18-Q1 — Confirm final telecom scope: new Room 110 with existing 111B and 213 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B18-Q2 — Why does 18T-701 reference RM 111A while new rack/electrical plans identify Telecom Room 110? [Open] Impact: Room naming mismatch could affect PMIS tracking • B18-Q3 — What active services are currently fed from existing 111B and 213 equipment? [Open] Impact: Potential communications/security outage • B18-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 110? [Open] Impact: Cooling continuity unclear • B18-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 110? [Open] Impact: Life-safety acceptance risk • B18-Q6 — Are B18-TR110A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
20 | • Cover sheet states Building 20 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. • Existing closet; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Office 1B ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing Tel/Data Closet 8A includes indoor AC unit to remain/protect in place; verify operation during cutover and whether equipment remains after transition. | • 20T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing 8A elevation shows UPS on ground, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 20T-701 identifies TE01-1B-1: 21 WAO total, 24 active ports per survey, 30 ports per schedule, 33 total ports with 10% allowance. Provide new wall-mount TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing Tel/Data Closet 8A contains open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy 48-port patch panel and Fiber LIU. Field verify all active services. | • Building 20 does not appear to create a new TR door/PACS package. Verify any existing cameras/security devices in Office 1B and ensure no camera angle or VMS integration is disrupted. • Keynotes indicate existing cameras are to be retained and re-used/protected in place; verify existing security equipment and cabinet impacts during cutover. | • High: Existing conditions for new Office 1B TE and existing Tel/Data Closet 8A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in 8A may remain active during transfer to new TE in 1B — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Room naming and TE designation could cause PMIS mapping confusion — Track as Building 20 / Office 1B / TE01-1B-1 and link existing Room 8A as transition point • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Office 1B — Verify heat load, office ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 459 feet of cable tray/pathway requires coordination despite small port count — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B20-Q1 — Confirm final scope: new wall-mount TE enclosure in Office 1B and existing Tel/Data Closet 8A transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B20-Q2 — What active services are currently fed from existing 8A open TE cabinet and related equipment? [Open] Impact: Potential communications/security outage • B20-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Office 1B? [Open] Impact: Electrical readiness unknown • B20-Q4 — Is Office 1B HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B20-Q5 — Are existing cameras/security devices in Building 20 protected and retained with no VMS/PACS changes? [Open] Impact: Security continuity unclear • B20-Q6 — Are all 459 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
21 | • Cover sheet states Building 21_19 receives a Telecom Enclosure and fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. • Existing B21 basement TR; verify protection-in-place and firestopping after cable transfer or reuse. • Existing B19 B05TR; verify protection-in-place and firestopping after cable transfer or reuse. | • Mechanical sheets exist in index. Verify whether new TE heat load in Office 100A is supported by existing/new HVAC and whether any mechanical scope applies despite TE designation. • Existing B21 B1.TR; verify environmental conditions during cutover and whether legacy equipment remains active. • Existing B19 B05TR; verify environmental conditions and whether equipment remains active during/after Building 21 transfer. | • 21_19T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switches, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing B21 B1.TR elevation shows UPS on ground, Cisco switch, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements. • Existing B19 B05TR elevations show APC floor UPS, legacy patch panels, Cisco switch and Fiber LIU; verify power source, active equipment and transfer/retention requirements. | • 21_19T-701 identifies RM 104 schedule: 90 WAO total, 67 active ports per survey, 119 ports per schedule, and 131 total ports with 10% allowance. 659 ft cable tray total: 63 ft basement and 596 ft first level. • Existing B21 B1.TR equipment includes multiple legacy patch panels, Cisco switch, UPS on ground, Fiber LIU and APC floor UPS; verify active services and transfer plan to new TE. • Existing B19 B05TR equipment includes legacy Ortronics patch panels, Cisco switch, Fiber LIU and APC floor UPS; verify active services and whether B19/B21 devices are served from new enclosure. | • Building 21_19 appears to create a TE enclosure rather than a full TR door/PACS package. Verify any existing cameras/security devices in Room 100A and ensure no camera angle or VMS integration is disrupted. • Verify any existing security device/cabinet impacts during cutover. • Verify existing security/camera protection-in-place and any impact from B19/B21 shared telecom equipment. | • High: Existing conditions for new 100A TE, B21 B1.TR and B19 B05TR not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment may remain active during transfer to new TE enclosure — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • High: Room naming mismatch: schedule says RM 104 / TR01-104-1 while plan/enlarged view identifies Room 100A — Track PMIS as Building 21 / Room 100A / Schedule RM 104 / Rack ID TR01-104-1 and confirm with designer • High: B19/B21 combined package may blur scope boundary and ownership of ports — Separate Building 21 work, Building 19 transition work, and shared service/cross-connect items in PMIS notes • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 659 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B21-Q1 — Confirm final scope: new TE enclosure at Room 100A/RM 104 and existing B21 B1.TR plus B19 B05TR transition? [Open] Impact: Room inventory or PMIS mapping could miss scope • B21-Q2 — Why does 21_19T-701 list RM 104 / TR01-104-1 while enlarged plan identifies Room 100A? [Open] Impact: Room naming mismatch could affect PMIS tracking • B21-Q3 — What active services are currently fed from existing B21 B1.TR and B19 B05TR equipment? [Open] Impact: Potential communications/security outage • B21-Q4 — What exactly is meant by '19 serving 21' on the new TE enclosure elevation? [Open] Impact: Building 19/21 boundary unclear • B21-Q5 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in 100A? [Open] Impact: Electrical readiness unknown • B21-Q6 — Are all 659 ft of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
22 | • Cover sheet states Building 22 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. • Existing TE room; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Break Room 102 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing Room 103 equipment area; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • 22T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing 103 elevation shows APC UPS, Cisco switch, SERTEX utility service, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 22T-701 identifies TR01-102-1: 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total port quantities, and 8 total ports with 10% allowance. Provide new wall-mount 12RU TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing Room 103 contains APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall and ports 1-24 to Bldg 19 ports 73-96. Field verify all active services and B19 handoff. | • Building 22 does not appear to create a new full TR door/PACS package. Verify any existing cameras/security devices in Break Room 102 and ensure no camera angle or VMS integration is disrupted. • Verify security/access conditions and whether any legacy security equipment is present at existing TE location. | • High: Existing conditions for new Break Room 102 TE and existing Room 103 TE not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in 103 may remain active during transfer to new TE in 102 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Break Room 102 use may conflict with wall-mount TE access and clearances — Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Break Room 102 — Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 139 feet of cable tray/pathway requires coordination despite small port count — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B22-Q1 — Confirm final scope: new wall-mount TE enclosure in Break Room 102 and existing Room 103 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B22-Q2 — What active services are currently fed from existing Room 103 equipment? [Open] Impact: Potential communications/security outage • B22-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? [Open] Impact: Electrical readiness unknown • B22-Q4 — Is Break Room 102 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B22-Q5 — Are existing cameras/security devices in Building 22 protected and retained with no VMS/PACS changes? [Open] Impact: Security continuity unclear • B22-Q6 — Are all 139 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
33 | • Cover sheet states Building 33 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. • Existing Tel Closet; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Office B23 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing B17 enlarged plan identifies an existing indoor AC unit. Verify operation during cutover and determine whether active legacy equipment remains after transfer to B23. | • 33T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing B17 elevations show UPS on floor, Cisco switches, SERTEX utility service, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 33T-701 identifies TE01-B23-1: 55 WAO total, 34 active ports per survey, 88 total ports per schedule, and 97 total ports with 10% allowance. Basement cable tray schedule totals 102 ft. Provide 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing B17 rack elevations include Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, passive Fiber LIU/wall mount, UPS on floor and cross-building port references to Bldgs 3, 80 and 82. | • Building 33 does not appear to create a new full TR door/PACS package. Verify existing cameras/security devices in B23 and ensure no camera angle or VMS integration is disrupted. • Existing B17 enlarged plan identifies network door controller, keypad and equipment box; verify protection-in-place and whether any security equipment is relocated or recabled. | • High: Existing conditions for new B23 TE and existing B17 Tel Closet not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in B17 may remain active during transfer to new TE in B23 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Office B23 use may conflict with wall-mount TE access and clearances — Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Office B23 — Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 102 feet of basement cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B33-Q1 — Confirm final scope: new wall-mount TE enclosure in B23 and existing B17 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B33-Q2 — What active services are currently fed from existing B17 equipment? [Open] Impact: Potential communications/security outage • B33-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in B23? [Open] Impact: Electrical readiness unknown • B33-Q4 — Is Office B23 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B33-Q5 — Are existing cameras/security devices in Building 33 protected and retained with no VMS/PACS disruption? [Open] Impact: Security continuity unclear • B33-Q6 — Are all 102 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
61 | • Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. • Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. • Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. • Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | • Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. • Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. • Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. • Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | • Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. • Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. • Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. • Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | • 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. • 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. • 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. • 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service. | • Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. • Verify TR door hardware and access control, CCTV camera, network door controller and integration. • Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. • Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | • High: Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • High: Hazardous material abatement plans exist for first and second levels — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation • Critical: Existing server/demarc equipment may remain active during cutover — Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path • Critical: Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified — Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements • High: Large cable tray scope creates coordination and firestop risk — Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | • B61-Q1 — Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? [Open] Impact: Room inventory could miss scope • B61-Q2 — What active services and circuits are currently housed in Room 137/137A? [Open] Impact: Potential outage/cutover risk • B61-Q3 — Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? [Open] Impact: Electrical PMIS mapping risk • B61-Q4 — Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? [Open] Impact: Cooling continuity unclear • B61-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B61-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown
62 | • Verify | • Verify | • Verify | • Verify | • No security / pacs / cctv items captured for this building. | • High: Cooling redundancy / emergency power not verified — Confirm power path for cooling, controls, condensate pump • High: Firestopping condition unknown — Survey penetrations and temporary/permanent firestop plan • Medium: Existing room conditions undocumented — Create photo record before construction begins • High: Condensate leak risk near IT equipment — Verify condensate routing and alarms | • B62-Q1 — Are cooling units emergency powered? [Open] Impact: Cannot confirm continuity of operations • B62-Q2 — Are future rack loads included in HVAC sizing? [Open] Impact: Cooling may be undersized after expansion • B62-Q3 — Is extinguisher location identified within 75 feet? [Open] Impact: Life safety / acceptance risk • B62-Q4 — Are all penetrations fully documented and firestopped? [Open] Impact: Fire/smoke spread risk
70 | • Verify | • Verify | • Verify | • Verify | • No security / pacs / cctv items captured for this building. | • High: Cooling emergency power / continuity not verified — Confirm power path for cooling, controls, BACnet adapter, and condensate pump • High: 1-hour rated/smoke-rated TR envelope and penetrations not field verified — Survey walls, doors, sleeves, trays, firestop, and head-of-wall conditions • Medium: Existing basement service conditions may constrain routing and access — Document existing utilities, clearances, and phasing around active systems • High: Existing TR/service equipment transfer could affect active operations — Require phasing plan and maintain analog/low-voltage systems operational • High: Condensate leak risk near IT equipment — Verify condensate routing, insulation, pump power, and alarms | • B70-Q1 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cannot confirm continuity of operations • B70-Q2 — Are future rack loads included in HVAC sizing for B27, 125A, and 262A? [Open] Impact: Cooling may be undersized after expansion • B70-Q3 — Are extinguisher cabinet locations identified within 75 feet of each TR? [Open] Impact: Acceptance / life safety risk • B70-Q4 — Are all wall/floor penetrations and speed sleeves shown and firestopped? [Open] Impact: Fire/smoke spread risk • B70-Q5 — What phasing is required to keep existing low-voltage/analog systems operational? [Open] Impact: Potential communications interruption
78 | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, and rated penetrations. • Verify FP/FA modifications, FEC location, temporary firestopping and final UL systems. • Verify first-level TR sprinkler/FA work, FEC location and cable tray penetrations. • Verify second-level TR sprinkler/FA work, FEC location, vertical riser penetrations and firestopping. • Verify third-level TR fire protection/fire alarm coordination and firestop work. | • Mechanical sheets included for basement. Verify dedicated cooling equipment, capacity, condensate, emergency source, controls/BACnet and high-temperature alarm. • Verify dedicated cooling and relationship to B30/B35 telecom buildout. • Verify first-level TR cooling, controls, emergency power and alarm tie-in. • Verify second-level TR cooling, condensate route and 24/7 operation. • Verify third-level TR cooling and control/alarm integration. | • Rack elevations identify new rack UPS/PDU and future rack. Verify panelboard/source, SPD, rack receptacles, PDU feeds, labels, load measurement and LOTO. • Verify rack UPS/PDU source, spare/future rack provisions and grounding/bonding. • Verify first-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. • Verify second-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. • Verify third-level rack receptacles for two racks, UPS/PDU, panel sources and labels. | • 78_78AT-701: 210 WAO total, 23 active ports, 311 scheduled ports, 342 with allowance; rack IDs TR01-B30-1/-2. Basement cable tray total 1,702 ft. • 78_78AT-702: 53 WAO total, 23 active ports, 64 scheduled ports, 70 with allowance. Confirm rack ID/room relation and active services. • 78_78AT-702/703: 301 WAO total, 388 active ports, 404 scheduled ports, 444 with allowance. Large active port count; high cutover risk. • 78_78AT-703/704: 256 WAO total, 153 active ports, 348 scheduled ports, 383 with allowance. Verify second-level test records and riser labels. • 78_78AT-704: 158 WAO total, 163 active ports, 289 scheduled ports, 318 with allowance. Rack IDs TR01-342-1/-2. | • TR scope includes wall-mounted CCTV cameras and PACS for TR doors. Verify CR/RX/DC/ES/MD, controller and VMS integration. • Verify PACS/CCTV integration and door hardware coordination. • Verify first-level TR PACS/CCTV and VMS integration. • Verify second-level TR PACS/CCTV and VMS integration. • Verify third-level TR PACS/CCTV and VMS integration. | • High: Existing conditions and active equipment across six TRs and existing telecom rooms not field verified — Perform detailed room-by-room existing condition survey with photos and active-service inventory • High: Hazardous material abatement plans exist for basement and third level — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or MEP installation • Critical: Existing telecom equipment may remain active during cutover — Document active services, OIT windows, rack inventory, temporary utilities and rollback plan • Critical: Dedicated cooling sequence, emergency power, condensate and alarms not verified — Confirm HVAC equipment serving each TR, emergency source, condensate, controls/BACnet and high-temp alarms • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify telecom panelboards, breakers, rack receptacles, UPS/PDU sources, SPDs, labels and LOTO requirements • High: Large cable tray scope creates coordination and firestop risk — Verify 4,849 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | • B78-Q1 — Confirm final telecom room list and PMIS mapping: B30, B35, 1232, 227A, 342, 401 plus existing rooms 15E/1234/353/308A/408A? [Open] Impact: Room inventory could miss scope • B78-Q2 — What active services currently remain in each existing telecom room/photo reference location? [Open] Impact: Potential outage/cutover risk • B78-Q3 — Are Room 1232 and existing Room 1234 separate rooms or naming/mapping references for the same telecom space? [Open] Impact: PMIS mapping risk • B78-Q4 — Which dedicated cooling units serve each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B78-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B78-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown
80 | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom closet/room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 102 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet interface, thermostat/control point, condensate pump/path, disconnects, and high-temperature alarm. • Existing telecom room/closet may remain active during cutover. Verify existing environmental condition and whether any active equipment remains after migration to Room 102. | • Electrical plans/schedules identify B80-TR102A fed from BUS-B80-MDP and B80-TR102B fed from BUS-B80-E1, with rack receptacles, normal/emergency circuits, CU-1-01, SPD requirements and 30-day load measurement requirements. • Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | • 80T-701 identifies RM102 with 117 WAO total, 98 active ports per survey, 195 total ports per schedule, and 215 total ports with 10% allowance. Rack IDs include TR01-102-1 and TR01-102-2; rack elevation shows 1 new rack plus future rack with switches, Cat6A patch panels, Cat5e patch panel, Fiber LIU, UPS and PDU. • Existing rack elevation shows Cisco switches, legacy optical Fiber LIU on wall, multiple legacy Ortronics 24/48-port patch panels, legacy Cat5e 24-port patch panel, and APC floor UPS. Contractor must transfer existing devices to new rack and protect active services. | • Electrical/telecom plans show access-control scope and camera 102-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, electric strike, camera/VMS integration, and door hardware coordination. • Verify existing security/PACS equipment conditions and whether any existing camera/security device is protected, recabled, or removed during cutover. | • High: Existing conditions for Room 102 and existing 127A/126 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing telecom equipment may remain active during transfer to Room 102 — Document active services, protect in place, identify OIT cutover windows, phasing and rollback plan • High: Room-number mismatch between Tel Closet 127A and photo/rack reference Room 126/127-A — Track both IDs in PMIS and confirm field room signage/owner mapping before punch list and turnover • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: B80-TR102A/B UPS/PDU and panel source coordination could delay energization — Verify panel sources BUS-B80-MDP and BUS-B80-E1, breakers, receptacles, SPD, labels, load measurement and LOTO needs • High: 811 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | • B80-Q1 — Confirm final telecom scope: new Room 102 with existing 127A/126 transition only? [Open] Impact: Room inventory could miss scope • B80-Q2 — What active services are currently fed from existing Room 127A/126 equipment? [Open] Impact: Potential communications/security outage • B80-Q3 — Are Room 127A and Room 126 the same telecom room, or separate locations? [Open] Impact: PMIS mapping and turnover risk • B80-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? [Open] Impact: Cooling continuity unclear • B80-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 102? [Open] Impact: Life-safety acceptance risk • B80-Q6 — Are B80-TR102A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
82 | • Cover sheet states Building 82 receives a Telecom Enclosure and fire protection scope is excluded. Still verify rated penetrations, 4-inch sleeve, wall/floor openings, temporary firestopping, and life-safety device impacts. • Existing telecom room; verify protection-in-place and firestopping after cable transfer or reuse. | • Mechanical and electrical drawings show IU-1-01 in/near Telecom Room 102 and CU-1-01 outdoor unit. Mechanical notes call for BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency/standby source, condensate pump/path, disconnects, controls, and high-temp alarm. • Existing telecom room may remain active during cutover. Verify existing environmental conditions and whether active equipment remains after transfer to Room 102. | • Electrical plans/schedules identify TE receptacle, CU-1-01, B82-MDP and B82-P-EMER sources, with SPD devices integral to new telecom panelboards. Verify receptacle type, grounding/bonding, emergency source, labels, and circuit loading. • Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | • 82T-701 identifies RM102 with 26 WAO total, 31 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. Rack ID TR01-102-01. Cable tray schedule totals 278 ft on first level. New enclosure includes APC UPS, two PDUs, network switch, Cat6A patch panel and Fiber LIU. • Existing B01-A elevations identify Cisco switches, cable management, two Ortronics 24-port patch panels with 11 and 6 used, existing patch panels and APC floor UPS. Field verify active services and transfer plan to new TE. | • Building 82 appears to create a TE enclosure rather than a full TR door/PACS package. Verify existing cameras/security devices in Room 102 and ensure no camera angle or VMS integration is disrupted. • Keynotes indicate existing cameras are to be retained and re-used. Verify security/access conditions and whether any legacy security equipment is present at existing telecom room. | • High: Existing conditions for new Room 102 TE and existing B01-A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in B01-A may remain active during transfer to new TE in 102 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • High: Cover sheet says TE, but mechanical cooling is included for Room 102 — Confirm scope interpretation with VA/AE and ensure cooling is commissioned if it serves active TE equipment • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding, SPD and labels • High: 278 feet of first-level cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light/HVAC conflicts and firestop assemblies | • B82-Q1 — Confirm final scope: new 12RU wall-mount TE enclosure in Room 102 and existing B01-A transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B82-Q2 — What active services are currently fed from existing B01-A equipment? [Open] Impact: Potential communications/security outage • B82-Q3 — Is Room 102 officially a TE-only scope or a conditioned telecom room with mechanical support? [Open] Impact: Scope and commissioning responsibility unclear • B82-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? [Open] Impact: Cooling continuity unclear • B82-Q5 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? [Open] Impact: Electrical readiness unknown • B82-Q6 — Are all 278 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
BCH | • Cover sheet states BCH receives a Telecom Enclosure and mechanical/fire protection scope has been excluded. Still verify existing life-safety protection, rated penetrations, 4-inch sleeve fire caulk, temporary firestopping and abandoned penetration patching. • TE-only scope does not appear to require new FEC/fire sprinkler work, but all wall/floor/ceiling penetrations must be sealed and rated assemblies maintained. | • Cover sheet explicitly excludes mechanical scope. Verify existing room ambient conditions are acceptable for TE equipment and that no active network equipment will overheat. • If the final scope is a 45RU new telecom room rather than a small TE, HVAC exclusion should be confirmed with VA/AE because telecom-room heat load may differ from TE assumptions. | • Electrical plan includes first-level electrical work and notes for new wall-mount telecom enclosure, grounding/bonding and camera. Verify circuit source, receptacle type, UPS/PDU load, emergency source if required, grounding/bonding and labels. • BCHT-604 shows 12RU TE equipment with APC UPS and PDUs and also a BCH 45RU new telecom room elevation. Confirm exact UPS/PDU/rack power requirement before acceptance. | • BCHT-101 identifies telecom plan first level and enlarged Room 107. BCHT-604 identifies new telecom room/no existing elevations. There is no BCHT-701 schedule in the drawing index, so WAO/cable-tray totals must be field verified from plans and contractor coordination drawings. • BCHT-604 identifies a 12RU TE elevation: APC UPS, two PDUs, network switch, 48-port Cat6A patch panel and Fiber LIU. Also shows BCH Crescent House Room 107 new telecom room elevation. Confirm governing rack/enclosure and labeling. | • Telecom/electrical notes reference new IP-addressable camera with wall mount at 8'-6" A.F.F. and VMS integration. Verify whether PACS applies; TE buildings typically do not create full TR door/PACS scope. • Verify existing camera/security conditions, protection-in-place, and any recabling or VMS integration required. | • High: Existing conditions for Crescent House Room 107 not field verified — Perform existing conditions survey with photos before mobilization • High: Mechanical and fire protection are excluded despite telecom/electronics installation — Verify existing environmental and life-safety conditions support TE equipment; confirm no dedicated HVAC/FP requirement applies • High: Rack/elevation conflict: TE 12RU enclosure versus BCH Room 107 new telecom room elevation — Submit RFI/confirm with AE which elevation governs and map room/equipment in PMIS • Critical: Active services and existing devices may require phasing/temporary service — Document active services, maintain existing service, use phasing plan, temporary utilities and OIT cutover windows • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: Cable tray, sleeve and pathway quantities not scheduled in a BCHT-701 sheet — Require coordination drawings showing route, supports, fill, penetrations, sleeves and cable counts | • BCH-Q1 — Confirm final BCH scope: Room 107 TE enclosure only, or a new telecom room/rack buildout? [Open] Impact: PMIS scope and acceptance criteria unclear • BCH-Q2 — Why does BCHT-604 show a T78 12RU TE enclosure and a separate BCH Crescent House Room 107 new telecom room elevation? [Open] Impact: Rack/equipment mapping conflict • BCH-Q3 — What active services currently serve Crescent House and where are existing terminations located? [Open] Impact: Cutover/outage risk • BCH-Q4 — What is the approved power source, receptacle type and circuit capacity for the new UPS/PDU? [Open] Impact: Electrical readiness unknown • BCH-Q5 — Is existing HVAC/ambient condition acceptable for TE/network equipment since mechanical scope is excluded? [Open] Impact: Heat/load risk • BCH-Q6 — Are cable tray route, sleeve locations, supports and firestopping details shown/field verified without a BCHT-701 schedule? [Open] Impact: Install delay or firestop gap
MCR | • MCR has full fire protection scope including wet pipe and clean-agent fire suppression system. Verify preaction/clean-agent design, agent release interface, fire alarm matrix, detection, abort/release stations, room integrity and acceptance testing. • Verify fiber entrance room protection, rated penetrations, firestopping, detector/strobe coverage and no gaps after cable tray installation. • Verify sprinkler/clean-agent coverage around MDA equipment, fire alarm devices, rack clearance and final firestop assemblies. • Verify clean-agent coverage, detector placement, alarm interfaces, and open cabinet airflow protection. • Existing systems must remain protected during temporary fiber, umbilical cord and core relocation work. Verify no impairment without approved fire watch/impairment plan. | • Telecom notes call for indoor computer room air conditioner (CRAC) units tied to building management system. Mechanical sheets included; verify redundant capacity, setpoints, humidity, condensate, controls, alarms and emergency power. • UPS rooms/equipment require thermal load validation, ventilation, emergency power and alarm integration. Verify battery/UPS environmental requirements. • Verify airflow/cold aisle/hot aisle assumptions, blanking panels, floor/ceiling distribution and temperature monitoring. • Server cabinets and patch fields require stable 24/7 cooling and monitoring. Confirm no local hot spots at dense LIU/patch panel zones. • During split-core temporary phase, existing MCR/server equipment remains active. Verify existing cooling remains in service until cutover and decommissioning are complete. | • Electrical set includes site plan, enlarged MCR plans, one-lines and schedules. Verify switchboard/service, ATS/generator integration, normal/emergency/UPS distribution, grounding, lightning protection, SPD, load measurements and commissioning. • MDA rack elevations include new 4-post floor cabinets, LIUs and network elements. Verify redundant A/B power feeds and PDU arrangements. • HDA cabinets include server cabinet front/rear elevations with patch panels and active equipment. Confirm A/B feed separation, PDU mounting, load capacity and labels. • Existing rack elevations identify multiple APC/Chatsworth/HP PDUs, APC Smart UPS and Eaton 9PX units. Verify what transfers, what stays, and temporary power during migration. • New MCR is standalone critical infrastructure. Verify utility service, generator/ATS paths, emergency distribution, grounding electrode and ductbank/site electrical coordination. | • MCRT-101 shows new MCR with MDA-A/B, HDA-A/B, UPS-A/B, cameras and fiber path legend. MCRT-701 shows 10 WAO total, 720 WAO available, 98.1% expansion capacity, 10 total ports with 20% allowance and 359 ft cable tray. • MCRT-701 Data Device and Circuit Schedule - Fiber Entrance Room 1: outlets 31-A/B/C/D plus security devices 07-CAM-03/04/07/08/11; Rack ID TR01-031-1. • MCRT-607: MDA A/B racks contain horizontal distribution LIUs, hybrid FOC, 48x Cat6A to HDA, and reserved LAN/spine/aggregation elements. Maintain A/B path separation. • MCRT-608/609: HDA A/B include 48-port Cat6A patch panels, HD fiber LIUs, backbone side A/B LIU and server cabinet arrangements. • Existing MCR rows 1-3 and B61 server cabinet transfer references are extensive. Maintain service using temporary fiber/umbilical cords and phased core relocation. | • MCRT-101 identifies cameras 07-CAM-01 through 07-CAM-12 around the MCR. Telecom notes call for IP-addressable network cameras integrated into existing VMS and PACS/access-control systems including iSTAR Edge/Avigilon ACM controller. • MCRT-701 includes security camera/data devices assigned to TR01-031-1. Confirm camera IDs, mounting, cabling, and VMS commissioning. • Verify camera coverage, door/access points, VMS monitoring and access control zones for critical equipment. • Verify coverage of HDA cabinets, doors, motion detection and any lockable cabinet/security requirements. • Existing security systems must remain functional during transition; protect existing camera angles and access controls until final turnover. | • Critical: MCR is a new standalone critical facility with 120-sheet multi-discipline scope — Use discipline-by-discipline pre-install checklist, coordination drawings, third-party inspections and commissioning tracker • Critical: Existing MCR/server/core equipment transfer may interrupt hospital network operations — Require detailed OIT cutover plan, temporary fiber/umbilicals, rollback plan, VA activation windows and after-hours phasing • Critical: A/B fiber path diversity and backbone commissioning not verified — Verify OSP/ISP Path A/B routing, no intermediate splices, test results, labeling and geographic diversity • Critical: UPS-A/B, ATS/generator, panel source and PDU coordination could delay activation — Verify one-line, load banks, breaker settings, panel labels, generator/ATS tests, UPS start-up and A/B power mapping • Critical: CRAC capacity, redundancy, condensate, BMS/FMS alarms and emergency power not verified — Confirm mechanical schedules, CRAC start-up, controls, alarm points, emergency source, environmental monitoring and hot/cold aisle performance • Critical: Clean-agent/preaction/fire alarm interface and room integrity acceptance risk — Track clean-agent calculations, room integrity test, release/abort stations, FA matrix, sprinkler/preaction tests and AHJ/third-party acceptance | • MCR-Q1 — Confirm final room naming and PMIS mapping: MCR Room 107, Fiber Entrance Room 031, Existing 107/137 server/MCR references. [Open] Impact: Room inventory and turnover mapping could be wrong • MCR-Q2 — What existing core/server/rack equipment is being relocated from the existing MCR/server rooms, and what remains? [Open] Impact: Cutover and outage risk • MCR-Q3 — What is the approved MCR activation sequence and required VA/OIT hold points? [Open] Impact: Schedule/cutover impact • MCR-Q4 — Are UPS-A/B, generator/ATS and emergency power paths commissioned and mapped to each rack/PDU? [Open] Impact: Electrical readiness unknown • MCR-Q5 — Are CRAC units fully commissioned with BMS/FMS alarms, redundancy and emergency power? [Open] Impact: Cooling continuity risk • MCR-Q6 — Are clean-agent/preaction/fire alarm systems fully designed, tested and accepted? [Open] Impact: Life-safety acceptance risk
SPEC | • No fire / life safety items captured for this building. | • No hvac / cooling items captured for this building. | • No electrical / ups items captured for this building. | • No telecom / fiber items captured for this building. | • No security / pacs / cctv items captured for this building. | • No owner risks items captured for this building. | • No open questions items captured for this building.
3. RISKS, DEFICIENCIES, AND OPEN QUESTIONS
Building | Open Risks | Open Questions | Risk Density | Question Density | Owner Focus | Execution Gate | Dashboard Signal
01 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
02 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
03 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
04 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
05 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
06 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
07 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
08 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
09 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
10 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
12 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
13 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
14 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
15 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
16 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
17 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
18 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
20 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
21 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
22 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
33 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
61 | 0 | 0 | 0 | 0 | Monitor | Ready | 🔴 ATTENTION
62 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
70 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
78 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
80 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
82 | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
BCH | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
MCR | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
SITE | 0 | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
4. SCHEDULE, SHUTDOWNS, RELOCATIONS, AND OPERATIONAL IMPACTS
Shutdown ID | System | Building | Requested | Approved | Scheduled | Duration | Stakeholders Notified | Status | Notes
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0
Operational Item | Current Status | Impact | Source | Owner | Required Next Step
Contractor Baseline Schedule | Not Received | Inspection planning and sequencing cannot be fully aligned. | CM/PM manual register | Paul | Obtain schedule and perform logic/dependency review.
Occupied-Room Relocation | In Development | Construction sequencing may displace active hospital functions. | Building_Register / assessments | Aisha | Coordinate hospital stakeholders before schedule acceptance.
Post-Award Coordination | Pending | Roles, reporting, RFIs, submittals, and commissioning workflows remain unconfirmed. | CM/PM manual register | Paul | Hold kickoff and document responsibilities.
Shutdown Integration | Initial Data Available | Hospital operational activities must be integrated into contractor planning. | Shutdown_Tracker | Shared | Validate dates, approvals, and stakeholder notification.
Two-Week Look Ahead | Preconstruction | Continue assessments, document review, and A/E coordination. | PMIS / CM/PM | Shared | Update when contractor schedule is received.
5. DESIGN AND TECHNICAL COORDINATION
Building | Open Questions | Major Blocker | Fire / Life Safety | HVAC / Cooling | Electrical / UPS | Telecom / Fiber
01 | • B01-Q1 — Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? [Closed] Impact: Room inventory could miss scope • B01-Q2 — What active services are currently fed from existing Rooms B02, 138 and 282? [Closed] Impact: Potential communications/security outage • B01-Q3 — What equipment from existing racks transfers to new Room 107 versus remains/decommissions? [Closed] Impact: Cutover and rack elevation risk • B01-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? [Closed] Impact: Cooling continuity unclear • B01-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? [Closed] Impact: Life-safety acceptance risk • B01-Q6 — Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Closed] Impact: Electrical readiness unknown | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning. | • Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems. • Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. • Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes. • Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place. | • Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup. • Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration. • Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear. • Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating. | • Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation. • Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements. • Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition. • Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope. | • 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1. • Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan. • Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence. • Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway.
02 | • B02-Q1 — Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? [Open] Impact: Room inventory could miss scope • B02-Q2 — What active services are currently fed from existing Rooms B-06, 141 and 236? [Open] Impact: Potential communications/security outage • B02-Q3 — What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? [Open] Impact: Cutover and rack elevation risk • B02-Q4 — Which IU/CU pair serves each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B02-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? [Open] Impact: Life-safety acceptance risk • B02-Q6 — Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance. | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping. • Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping. • Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | • Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms. • Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm. • Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration. • Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete. | • Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels. • Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping. • Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits. • Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs. | • 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray. • 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope. • 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count. • Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover.
03 | • B03-Q1 — Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? [Open] Impact: Room inventory could miss scope • B03-Q2 — What active services are currently fed from existing Room 107 and DMARC Room 101C? [Open] Impact: Potential communications/provider outage • B03-Q3 — What existing equipment transfers to new Room 101E versus remains/decommissions? [Open] Impact: Cutover and rack elevation risk • B03-Q4 — Which IU/CU pair serves Room 101E and is it on emergency/backup power? [Open] Impact: Cooling continuity unclear • B03-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? [Open] Impact: Life-safety acceptance risk • B03-Q6 — Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance. | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse. • Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer. • Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations. | • Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm. • Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete. • Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains. • No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements. | • Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements. • Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements. • Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer. • Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations. | • 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2. • Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover. • Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted. • Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced.
04 | • B04-Q1 — Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? [Open] Impact: Incomplete room inventory / missed scope • B04-Q2 — Are B05, 141, and 244A cooling systems on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B04-Q3 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B04-Q4 — What is the approved migration and cutover sequence for active Building 04 services? [Open] Impact: Potential communications outage • B04-Q5 — Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? [Open] Impact: Work stoppage or exposure risk • B04-Q6 — Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? [Open] Impact: Electrical delay or overload risk | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open. | • Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning. • FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies. • Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations. | • Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up. • Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control. • Verify cooling unit, routing, condensate, controls, and emergency/backup power path. | • Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits. • Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting. • Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source. | • New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • TR/panel identified; verify rack elevation and pathway details against 04T sheets.
05 | • B05-Q1 — Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? [Open] Impact: Room inventory could be wrong • B05-Q2 — What active services are currently fed from the existing 153-A TE/legacy patch panels? [Open] Impact: Potential communications outage • B05-Q3 — What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? [Open] Impact: Cutover risk • B05-Q4 — Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? [Open] Impact: Power source cannot be verified • B05-Q5 — Is emergency/backup power required or provided for the TE UPS/PDU source? [Open] Impact: Continuity requirement unclear • B05-Q6 — Are firestopping locations and surface raceway/conduit routes shown and coordinated? [Open] Impact: Rated assembly/firestop risk | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified. | • Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts. • Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling. | • Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling. • Existing wall/wall-mount TE area; verify existing environmental conditions during field survey. | • 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source. • Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover. | • New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU. • Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records.
06 | • B06-Q1 — Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? [Open] Impact: Room inventory could miss scope • B06-Q2 — What active services are fed from existing B-01 and Room 178 legacy equipment? [Open] Impact: Potential communications outage • B06-Q3 — What is the approved cutover sequence for B-01, 178 and 233? [Open] Impact: Cutover risk • B06-Q4 — Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B06-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B06-Q6 — Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? [Open] Impact: Electrical readiness unknown | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open. | • Existing equipment area; verify no cabling penetrations are left unsealed. • Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs. • Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft. | • Verify basement equipment environmental condition and any heat/load issues during cutover. • Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route. • Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls. | • Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements. • Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation. • Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power. | • Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS. • Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification. • Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
07 | • B07-Q1 — Confirm final TR scope: B-18 basement and 228A second floor only? [Open] Impact: Room inventory could miss scope • B07-Q2 — Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? [Open] Impact: Cooling scope unclear • B07-Q3 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B07-Q4 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B07-Q5 — What active services are currently fed from B-18 and/or existing pathways serving 228A? [Open] Impact: Potential communications outage • B07-Q6 — Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open. | • Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination. • Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications. | • Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm. • Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route. | • Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement. • Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels. | • 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU. • TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover.
08 | • B08-Q1 — Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? [Open] Impact: Room inventory may miss scope • B08-Q2 — What active services are currently fed from existing B-15 equipment? [Open] Impact: Potential communications outage • B08-Q3 — Is B12B truly a TE/equipment location or only a cabling pathway/service area? [Open] Impact: Scope ambiguity • B08-Q4 — Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? [Open] Impact: Cooling continuity unclear • B08-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? [Open] Impact: Life safety acceptance risk • B08-Q6 — Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open. | • Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected. • Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers. • Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades. | • Verify existing environmental conditions and whether active legacy equipment remains during cutover. • Field verify whether TE equipment load requires cooling or if served by existing building HVAC. • Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls. | • Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements. • Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel. • Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope. | • Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS. • Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance. • New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS.
09 | • B09-Q1 — Confirm final TR scope: B01 basement, 104B first level, and 206A second level? [Open] Impact: Room inventory may miss scope • B09-Q2 — What active services are currently fed from B01 existing equipment/security/network devices? [Open] Impact: Potential communications/security outage • B09-Q3 — What hazardous/abatement steps apply to B01, 104B and 206A work areas? [Open] Impact: Work delay or exposure risk • B09-Q4 — Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B09-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B09-Q6 — Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open. | • Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR. • Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft. • Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations. | • Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms. • Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power. • Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power. | • Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes. • Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits. • Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits. | • Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover. • Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. • Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records.
10 | • B10-Q1 — Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? [Open] Impact: Room inventory could miss scope • B10-Q2 — What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? [Open] Impact: Potential communications outage • B10-Q3 — What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? [Open] Impact: Work delay/exposure risk • B10-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? [Open] Impact: Cooling continuity unclear • B10-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? [Open] Impact: Life-safety acceptance risk • B10-Q6 — Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? [Open] Impact: Electrical readiness unknown | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination. | • Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping. • Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place. • Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment. | • Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm. • No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work. • No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted. | • Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels. • Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing. • Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required. | • 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover. • Coordinate telecom power pathways through/source from basement electrical room if applicable. • Coordinate emergency source/backup power pathways for telecom equipment and cooling.
12 | • B12-Q1 — Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? [Open] Impact: Scope misunderstanding • B12-Q2 — What exact pathway does the Building 12 fiber take through basement, first and second levels? [Open] Impact: Fiber pull and access risk • B12-Q3 — Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? [Open] Impact: Termination and ownership unclear • B12-Q4 — Are existing conduits/cable trays available and below fill limits for the new fiber? [Open] Impact: Pathway capacity risk • B12-Q5 — Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? [Open] Impact: Life safety/firestop risk • B12-Q6 — What is the approved cutover/testing/acceptance sequence for Building 12 fiber? [Open] Impact: Possible outage or acceptance delay | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover. | • No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route. • No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work. | • No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment. • Field verify existing environmental conditions only if existing service point/equipment is accessed. | • No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown. • Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling. | • Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing. • 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only.
13 | • B13-Q1 — Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? [Open] Impact: Room inventory could miss scope • B13-Q2 — What active services are currently fed from existing Tel Room 222 equipment? [Open] Impact: Potential communications/security outage • B13-Q3 — What hazardous/abatement steps apply to first-level Room 124 work? [Open] Impact: Work delay or exposure risk • B13-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? [Open] Impact: Cooling continuity unclear • B13-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? [Open] Impact: Life-safety acceptance risk • B13-Q6 — Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | • Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B. • Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124.
14 | • B14-Q1 — Confirm final telecom scope: new Room 119 and existing basement B.01/B2 transition only? [Open] Impact: Room inventory could miss scope • B14-Q2 — What active services are currently fed from existing B.01/B2 equipment? [Open] Impact: Potential communications/security outage • B14-Q3 — What hazardous/abatement steps apply to first-level Room 119 work? [Open] Impact: Work delay or exposure risk • B14-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 119? [Open] Impact: Cooling continuity unclear • B14-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 119? [Open] Impact: Life-safety acceptance risk • B14-Q6 — Are B14-TR119A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 14 includes new first-level Telecom Room 119 and existing basement telecom rooms B.01/B2; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing basement tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Existing basement telecom room; verify no unsealed penetrations remain after cable transfer or reuse. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 119 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel/F Panel room; verify existing environmental conditions during cutover and whether legacy equipment remains active. • Existing telecom room reference; field verify cooling/ventilation and active equipment condition. | • Electrical plan/schedules identify B14-TR119A/B, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and panel load measurement requirements. • Existing basement wall-mounted TE/equipment area; verify power source, active equipment, UPS/PDU status, and transition requirements before disconnect or removal. • Existing telecom room photo reference; confirm power sources and any cutover requirements. | • 14T-701 identifies Room 119 schedule: 44 WAO total, 29 active ports per survey, 76 total ports per schedule, and 84 total ports with 10% allowance. New Rack ID TR01-119-1 serves first and second level outlets with Fiber Path A/B. • Existing Room B.01 equipment includes wall-mounted TE, Cisco switch/legacy patch panel, telco patch, plywood backboards, and legacy Fiber LIU; verify active services and transfer plan to Room 119. • Existing basement telecom room B2 is identified by photo reference; verify active devices, routing, and relation to B.01.
15 | • B15-Q1 — Confirm final telecom scope: new Room 124A and existing Rooms 222/B01 transition only? [Open] Impact: Room inventory could miss scope • B15-Q2 — Why does 15T-701 reference RM 109A while plans and electrical schedules identify Telecom Room 124A? [Open] Impact: Room naming mismatch could affect PMIS tracking • B15-Q3 — What active services are currently fed from existing Room 222 and B01 equipment? [Open] Impact: Potential communications/security outage • B15-Q4 — What hazardous/abatement steps apply to first-level Room 124A work? [Open] Impact: Work delay or exposure risk • B15-Q5 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124A? [Open] Impact: Cooling continuity unclear • B15-Q6 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124A? [Open] Impact: Life-safety acceptance risk | Building 15 includes new first-level Telecom Room 124A and existing telecom transition points at second-level Tel Room 222 and basement B01; field verification, active service cutover, 240V UPS/PDU power, dedicated heat-pump cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Existing basement telecom/crossover room; verify no unsealed penetrations remain after cable transfer or reuse. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124A and CU-1-01 outdoor heat-pump/A/C unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 is shown with existing/remain indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. • Existing basement telecom/crossover space; verify environmental conditions and whether active equipment remains during cutover. | • Electrical enlarged plans and schedules identify B15-TR124AA/AB, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and 30-day load measurement requirements. • Existing rack/equipment area; verify power source, active equipment, APC floor UPS status, and transition requirements before disconnect or removal. • Existing B-01 crossover; verify power sources and cutover needs for legacy patch panel/crossover. | • 15T-701 identifies Room 109A schedule but field plan/electrical room callouts identify Telecom Room 124A; schedule has 62 WAO total, 76 active ports per survey, 101 total ports per schedule, and 111 total ports with 10% allowance. New Rack ID TR15-109A-01 serves basement, first and second level outlets. • Existing Room 222 equipment includes wall/wall-mounted TE, Cisco switches, legacy 48-port patch panels, ground bar, plywood backboard, security cabinet, and floor UPS; verify active services and transfer plan to Room 124A. • Existing B-01 crossover includes legacy 24-port patch panel; verify active devices, routing, and relation to Room 222 and Room 124A.
16 | • B16-Q1 — Confirm final telecom scope: new Room 015 and existing Room 014 transition only? [Open] Impact: Room inventory could miss scope • B16-Q2 — What active services are currently fed from existing Room 014 equipment? [Open] Impact: Potential communications/security outage • B16-Q3 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 015? [Open] Impact: Cooling continuity unclear • B16-Q4 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 015? [Open] Impact: Life-safety acceptance risk • B16-Q5 — Are B16-TR015A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown • B16-Q6 — Which existing panel/circuit breaker/feeder demolition and replacement affects Room 015 telecom power? [Open] Impact: Panel outage/cutover risk | Building 16 includes new basement Telecom Room 015 and existing basement Telecom Room 014; field verification, active service transfer, 240V UPS/PDU power, dedicated cooling, panel replacement/source coordination, firestopping, PACS/CCTV integration, and cable tray coordination remain open. | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 015 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Telecom Room 014; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • Electrical plans/schedules identify B16-TR015A/B, 240V rack UPS requirements, rack receptacles, TR receptacles, lighting, access controller, CU-1-01, SPD requirements, existing panel demolition/replacement, and 30-day load measurement requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 16T-701 identifies Room 015-A schedule: 25 WAO total, 25 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. New Rack ID TR01-015-A-1 serves basement, first, second and attic level outlets. • Existing Room 014 equipment includes wall/TE rack, floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU; verify active services and transfer plan to Room 015.
17 | • B17-Q1 — Confirm final telecom scope: new Room 118, existing B35A, and Building 29 served from B17? [Open] Impact: Room inventory or PMIS mapping could miss scope • B17-Q2 — What active services are currently fed from existing B35A equipment? [Open] Impact: Potential communications/security outage • B17-Q3 — What exact Building 29 outlets/devices are served through TR17-118-1? [Open] Impact: Building 29 scope boundary unclear • B17-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 118? [Open] Impact: Cooling continuity unclear • B17-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 118? [Open] Impact: Life-safety acceptance risk • B17-Q6 — Are B17-TR118A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 17_29 includes new first-level Telecom Room 118 serving Building 17 and Building 29, plus existing basement Telecom Closet B35A; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, cable tray, firestopping, and PACS/CCTV integration remain open. | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom closet; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Verify firestopping at pathway penetrations between Building 17 and Building 29 and any rated floor/wall assemblies. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 118 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing B35A is shown with existing indoor AC unit; verify whether it remains active, is abandoned, or needs temporary protection during cutover. • No dedicated cooling expected for pathway; verify any equipment cabinets or active service locations in Building 29 if applicable. | • Electrical plans/schedules identify B17-TR118A fed from BUS-B17-NPB1-R and B17-TR118B fed from BUS-B17-EQDP, with TR RM118 rack receptacles, 208V UPS/PDU equipment, CU-1-01, SPD requirements, and 30-day load measurement requirements. • Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. • Verify whether any Building 29 equipment or extension path requires power, grounding, bonding, or labeling tied back to B17 TR 118. | • 17_29T-701 identifies Room 118 schedule: 113 WAO total, 67 active ports per survey, 154 total ports per schedule, and 169 total ports with 10% allowance. Rack ID TR17-118-1 serves basement, first, second-level outlets and Building 29 path. • Existing Room B35A equipment includes SERTEX utility service ports, legacy Ortronics patch panels, Cisco switches, wall-mounted TE, Fiber/legacy equipment, security cabinet, and floor UPS; verify active services and transfer plan to Room 118. • Building 29 is shown served from B17; verify fiber from Building 17 to Building 29, path to B29 4-inch PVC, outlet labels, test records and as-builts.
18 | • B18-Q1 — Confirm final telecom scope: new Room 110 with existing 111B and 213 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B18-Q2 — Why does 18T-701 reference RM 111A while new rack/electrical plans identify Telecom Room 110? [Open] Impact: Room naming mismatch could affect PMIS tracking • B18-Q3 — What active services are currently fed from existing 111B and 213 equipment? [Open] Impact: Potential communications/security outage • B18-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 110? [Open] Impact: Cooling continuity unclear • B18-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 110? [Open] Impact: Life-safety acceptance risk • B18-Q6 — Are B18-TR110A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 18 includes new first-level Telecom Room 110 and existing telecom transition rooms 111B and 213; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, lead-paint/first-level hazardous material coordination, firestopping, cable tray, and PACS/CCTV integration remain open. | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing TE room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. • Existing second-level closet; verify protection-in-place and firestopping after transfer or abandonment. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 110 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing TE 111B; verify existing environmental conditions during cutover and whether legacy equipment remains active. • Existing Closet 213; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • Electrical plans/schedules identify B18-TR110A/B, 208V rack UPS requirements, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and telecom panelboard schedule requirements. • Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. • Existing rack/equipment area; verify active equipment, APC UPS status, source circuits, SERTEX utility service and transfer requirements before disconnect/removal. | • 18T-701 identifies RM 111A schedule: 86 WAO total, 61 active ports per survey, 122 ports per schedule, and 134 total ports with 10% allowance. New rack elevation is Room 110, 1 rack plus future, with UPS, Future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. • Existing Room 111B equipment includes wall-mounted rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber optic housing; verify active services and transfer plan to Room 110. • Existing Room 213 equipment includes SERTEX utility service ports, Cisco switch, multiple legacy Ortronics patch panels, wall/wall-mount TE and APC floor UPS; verify active services and transfer plan to Room 110.
20 | • B20-Q1 — Confirm final scope: new wall-mount TE enclosure in Office 1B and existing Tel/Data Closet 8A transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B20-Q2 — What active services are currently fed from existing 8A open TE cabinet and related equipment? [Open] Impact: Potential communications/security outage • B20-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Office 1B? [Open] Impact: Electrical readiness unknown • B20-Q4 — Is Office 1B HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B20-Q5 — Are existing cameras/security devices in Building 20 protected and retained with no VMS/PACS changes? [Open] Impact: Security continuity unclear • B20-Q6 — Are all 459 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 20 is a telecom-enclosure building, not a full TR buildout. Scope centers on new first-level Office 1B wall-mount TE enclosure and existing Tel/Data Closet 8A; mechanical and fire protection scope are excluded by the cover sheet, but field verification, active equipment transfer, fiber/copper cutover, cable tray, firestopping, power/UPS/PDU, and existing equipment protection remain open. | • Cover sheet states Building 20 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. • Existing closet; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Office 1B ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing Tel/Data Closet 8A includes indoor AC unit to remain/protect in place; verify operation during cutover and whether equipment remains after transition. | • 20T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing 8A elevation shows UPS on ground, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 20T-701 identifies TE01-1B-1: 21 WAO total, 24 active ports per survey, 30 ports per schedule, 33 total ports with 10% allowance. Provide new wall-mount TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing Tel/Data Closet 8A contains open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy 48-port patch panel and Fiber LIU. Field verify all active services.
21 | • B21-Q1 — Confirm final scope: new TE enclosure at Room 100A/RM 104 and existing B21 B1.TR plus B19 B05TR transition? [Open] Impact: Room inventory or PMIS mapping could miss scope • B21-Q2 — Why does 21_19T-701 list RM 104 / TR01-104-1 while enlarged plan identifies Room 100A? [Open] Impact: Room naming mismatch could affect PMIS tracking • B21-Q3 — What active services are currently fed from existing B21 B1.TR and B19 B05TR equipment? [Open] Impact: Potential communications/security outage • B21-Q4 — What exactly is meant by '19 serving 21' on the new TE enclosure elevation? [Open] Impact: Building 19/21 boundary unclear • B21-Q5 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in 100A? [Open] Impact: Electrical readiness unknown • B21-Q6 — Are all 659 ft of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 21 is combined with Building 19 and is primarily a telecom-enclosure scope. New first-level M&O Foreman Office 100A / RM 104 schedule is served by a new 12RU TE enclosure, while existing Building 21 B1.TR and Building 19 B05TR equipment remain transition points. Fire protection scope is excluded, but mechanical/electrical sheets exist for equipment support. Field verification, active-service transfer, 659 ft cable tray, firestopping, UPS/PDU power, fiber/copper cutover, and B19/B21 scope boundary remain open. | • Cover sheet states Building 21_19 receives a Telecom Enclosure and fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. • Existing B21 basement TR; verify protection-in-place and firestopping after cable transfer or reuse. • Existing B19 B05TR; verify protection-in-place and firestopping after cable transfer or reuse. | • Mechanical sheets exist in index. Verify whether new TE heat load in Office 100A is supported by existing/new HVAC and whether any mechanical scope applies despite TE designation. • Existing B21 B1.TR; verify environmental conditions during cutover and whether legacy equipment remains active. • Existing B19 B05TR; verify environmental conditions and whether equipment remains active during/after Building 21 transfer. | • 21_19T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switches, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing B21 B1.TR elevation shows UPS on ground, Cisco switch, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements. • Existing B19 B05TR elevations show APC floor UPS, legacy patch panels, Cisco switch and Fiber LIU; verify power source, active equipment and transfer/retention requirements. | • 21_19T-701 identifies RM 104 schedule: 90 WAO total, 67 active ports per survey, 119 ports per schedule, and 131 total ports with 10% allowance. 659 ft cable tray total: 63 ft basement and 596 ft first level. • Existing B21 B1.TR equipment includes multiple legacy patch panels, Cisco switch, UPS on ground, Fiber LIU and APC floor UPS; verify active services and transfer plan to new TE. • Existing B19 B05TR equipment includes legacy Ortronics patch panels, Cisco switch, Fiber LIU and APC floor UPS; verify active services and whether B19/B21 devices are served from new enclosure.
22 | • B22-Q1 — Confirm final scope: new wall-mount TE enclosure in Break Room 102 and existing Room 103 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B22-Q2 — What active services are currently fed from existing Room 103 equipment? [Open] Impact: Potential communications/security outage • B22-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? [Open] Impact: Electrical readiness unknown • B22-Q4 — Is Break Room 102 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B22-Q5 — Are existing cameras/security devices in Building 22 protected and retained with no VMS/PACS changes? [Open] Impact: Security continuity unclear • B22-Q6 — Are all 139 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 22 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new first-level Break Room 102 TE enclosure and existing first-level wall/wall-mount TE Room 103. Field verification, active service transfer, 139 ft cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, and B19 utility service relationship remain open. | • Cover sheet states Building 22 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. • Existing TE room; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Break Room 102 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing Room 103 equipment area; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • 22T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing 103 elevation shows APC UPS, Cisco switch, SERTEX utility service, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 22T-701 identifies TR01-102-1: 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total port quantities, and 8 total ports with 10% allowance. Provide new wall-mount 12RU TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing Room 103 contains APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall and ports 1-24 to Bldg 19 ports 73-96. Field verify all active services and B19 handoff.
33 | • B33-Q1 — Confirm final scope: new wall-mount TE enclosure in B23 and existing B17 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B33-Q2 — What active services are currently fed from existing B17 equipment? [Open] Impact: Potential communications/security outage • B33-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in B23? [Open] Impact: Electrical readiness unknown • B33-Q4 — Is Office B23 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B33-Q5 — Are existing cameras/security devices in Building 33 protected and retained with no VMS/PACS disruption? [Open] Impact: Security continuity unclear • B33-Q6 — Are all 102 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 33 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new basement EEO Manager Office B23 TE enclosure and existing Tel Closet B17. Field verification, active service transfer, 102 ft basement cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, fiber/copper cutover, and legacy service relationships to Buildings 3, 80 and 82 remain open. | • Cover sheet states Building 33 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. • Existing Tel Closet; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Office B23 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing B17 enlarged plan identifies an existing indoor AC unit. Verify operation during cutover and determine whether active legacy equipment remains after transfer to B23. | • 33T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing B17 elevations show UPS on floor, Cisco switches, SERTEX utility service, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 33T-701 identifies TE01-B23-1: 55 WAO total, 34 active ports per survey, 88 total ports per schedule, and 97 total ports with 10% allowance. Basement cable tray schedule totals 102 ft. Provide 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing B17 rack elevations include Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, passive Fiber LIU/wall mount, UPS on floor and cross-building port references to Bldgs 3, 80 and 82.
61 | • B61-Q1 — Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? [Open] Impact: Room inventory could miss scope • B61-Q2 — What active services and circuits are currently housed in Room 137/137A? [Open] Impact: Potential outage/cutover risk • B61-Q3 — Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? [Open] Impact: Electrical PMIS mapping risk • B61-Q4 — Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? [Open] Impact: Cooling continuity unclear • B61-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B61-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown | Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. | • Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. • Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. • Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. • Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | • Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. • Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. • Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. • Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | • Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. • Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. • Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. • Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | • 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. • 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. • 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. • 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service.
62 | • B62-Q1 — Are cooling units emergency powered? [Open] Impact: Cannot confirm continuity of operations • B62-Q2 — Are future rack loads included in HVAC sizing? [Open] Impact: Cooling may be undersized after expansion • B62-Q3 — Is extinguisher location identified within 75 feet? [Open] Impact: Life safety / acceptance risk • B62-Q4 — Are all penetrations fully documented and firestopped? [Open] Impact: Fire/smoke spread risk | Cooling / emergency power not verified | • Verify | • Verify | • Verify | • Verify
70 | • B70-Q1 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cannot confirm continuity of operations • B70-Q2 — Are future rack loads included in HVAC sizing for B27, 125A, and 262A? [Open] Impact: Cooling may be undersized after expansion • B70-Q3 — Are extinguisher cabinet locations identified within 75 feet of each TR? [Open] Impact: Acceptance / life safety risk • B70-Q4 — Are all wall/floor penetrations and speed sleeves shown and firestopped? [Open] Impact: Fire/smoke spread risk • B70-Q5 — What phasing is required to keep existing low-voltage/analog systems operational? [Open] Impact: Potential communications interruption | Cooling / emergency power and existing TR phasing not verified | • Verify | • Verify | • Verify | • Verify
78 | • B78-Q1 — Confirm final telecom room list and PMIS mapping: B30, B35, 1232, 227A, 342, 401 plus existing rooms 15E/1234/353/308A/408A? [Open] Impact: Room inventory could miss scope • B78-Q2 — What active services currently remain in each existing telecom room/photo reference location? [Open] Impact: Potential outage/cutover risk • B78-Q3 — Are Room 1232 and existing Room 1234 separate rooms or naming/mapping references for the same telecom space? [Open] Impact: PMIS mapping risk • B78-Q4 — Which dedicated cooling units serve each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B78-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B78-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown | Building 78/78A is a very large full-scope TR building with basement through fourth-level telecom rooms, existing telecom rooms, hazardous abatement, architectural, fire protection, mechanical, electrical, security, telecom, rack elevations and photo references. Major open issues include active service cutover, dedicated HVAC validation, panel/UPS/PDU coordination, 4,849 ft cable tray routes, firestopping, PACS/CCTV, existing rack transfers, and turnover testing. | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, and rated penetrations. • Verify FP/FA modifications, FEC location, temporary firestopping and final UL systems. • Verify first-level TR sprinkler/FA work, FEC location and cable tray penetrations. • Verify second-level TR sprinkler/FA work, FEC location, vertical riser penetrations and firestopping. • Verify third-level TR fire protection/fire alarm coordination and firestop work. | • Mechanical sheets included for basement. Verify dedicated cooling equipment, capacity, condensate, emergency source, controls/BACnet and high-temperature alarm. • Verify dedicated cooling and relationship to B30/B35 telecom buildout. • Verify first-level TR cooling, controls, emergency power and alarm tie-in. • Verify second-level TR cooling, condensate route and 24/7 operation. • Verify third-level TR cooling and control/alarm integration. | • Rack elevations identify new rack UPS/PDU and future rack. Verify panelboard/source, SPD, rack receptacles, PDU feeds, labels, load measurement and LOTO. • Verify rack UPS/PDU source, spare/future rack provisions and grounding/bonding. • Verify first-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. • Verify second-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. • Verify third-level rack receptacles for two racks, UPS/PDU, panel sources and labels. | • 78_78AT-701: 210 WAO total, 23 active ports, 311 scheduled ports, 342 with allowance; rack IDs TR01-B30-1/-2. Basement cable tray total 1,702 ft. • 78_78AT-702: 53 WAO total, 23 active ports, 64 scheduled ports, 70 with allowance. Confirm rack ID/room relation and active services. • 78_78AT-702/703: 301 WAO total, 388 active ports, 404 scheduled ports, 444 with allowance. Large active port count; high cutover risk. • 78_78AT-703/704: 256 WAO total, 153 active ports, 348 scheduled ports, 383 with allowance. Verify second-level test records and riser labels. • 78_78AT-704: 158 WAO total, 163 active ports, 289 scheduled ports, 318 with allowance. Rack IDs TR01-342-1/-2.
80 | • B80-Q1 — Confirm final telecom scope: new Room 102 with existing 127A/126 transition only? [Open] Impact: Room inventory could miss scope • B80-Q2 — What active services are currently fed from existing Room 127A/126 equipment? [Open] Impact: Potential communications/security outage • B80-Q3 — Are Room 127A and Room 126 the same telecom room, or separate locations? [Open] Impact: PMIS mapping and turnover risk • B80-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? [Open] Impact: Cooling continuity unclear • B80-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 102? [Open] Impact: Life-safety acceptance risk • B80-Q6 — Are B80-TR102A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 80 includes a new first-level Telecom Room 102 and existing Tel Closet 127A / photo-reference Room 126 transition point. Field verification, active equipment transfer, dedicated cooling IU-1-01/CU-1-01, B80-TR102A/B power, 811 ft cable tray, firestopping, PACS/CCTV, existing two-post rack migration, and room-number mapping remain open. | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom closet/room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 102 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet interface, thermostat/control point, condensate pump/path, disconnects, and high-temperature alarm. • Existing telecom room/closet may remain active during cutover. Verify existing environmental condition and whether any active equipment remains after migration to Room 102. | • Electrical plans/schedules identify B80-TR102A fed from BUS-B80-MDP and B80-TR102B fed from BUS-B80-E1, with rack receptacles, normal/emergency circuits, CU-1-01, SPD requirements and 30-day load measurement requirements. • Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | • 80T-701 identifies RM102 with 117 WAO total, 98 active ports per survey, 195 total ports per schedule, and 215 total ports with 10% allowance. Rack IDs include TR01-102-1 and TR01-102-2; rack elevation shows 1 new rack plus future rack with switches, Cat6A patch panels, Cat5e patch panel, Fiber LIU, UPS and PDU. • Existing rack elevation shows Cisco switches, legacy optical Fiber LIU on wall, multiple legacy Ortronics 24/48-port patch panels, legacy Cat5e 24-port patch panel, and APC floor UPS. Contractor must transfer existing devices to new rack and protect active services.
82 | • B82-Q1 — Confirm final scope: new 12RU wall-mount TE enclosure in Room 102 and existing B01-A transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B82-Q2 — What active services are currently fed from existing B01-A equipment? [Open] Impact: Potential communications/security outage • B82-Q3 — Is Room 102 officially a TE-only scope or a conditioned telecom room with mechanical support? [Open] Impact: Scope and commissioning responsibility unclear • B82-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? [Open] Impact: Cooling continuity unclear • B82-Q5 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? [Open] Impact: Electrical readiness unknown • B82-Q6 — Are all 278 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 82 is identified as a Telecom Enclosure (TE) building on the cover sheet, with fire protection scope excluded, but mechanical sheets show IU-1-01/CU-1-01 dedicated cooling for Room 102 and electrical drawings show B82-MDP/B82-P-EMER power. Scope centers on new first-level Telecom Room 102 / 12RU enclosure and existing first-level Telecom Room B01-A transition point. Field verification, active-equipment transfer, 278 ft cable tray, firestopping, UPS/PDU power, HVAC controls, fiber/copper cutover, and room/equipment mapping remain open. | • Cover sheet states Building 82 receives a Telecom Enclosure and fire protection scope is excluded. Still verify rated penetrations, 4-inch sleeve, wall/floor openings, temporary firestopping, and life-safety device impacts. • Existing telecom room; verify protection-in-place and firestopping after cable transfer or reuse. | • Mechanical and electrical drawings show IU-1-01 in/near Telecom Room 102 and CU-1-01 outdoor unit. Mechanical notes call for BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency/standby source, condensate pump/path, disconnects, controls, and high-temp alarm. • Existing telecom room may remain active during cutover. Verify existing environmental conditions and whether active equipment remains after transfer to Room 102. | • Electrical plans/schedules identify TE receptacle, CU-1-01, B82-MDP and B82-P-EMER sources, with SPD devices integral to new telecom panelboards. Verify receptacle type, grounding/bonding, emergency source, labels, and circuit loading. • Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | • 82T-701 identifies RM102 with 26 WAO total, 31 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. Rack ID TR01-102-01. Cable tray schedule totals 278 ft on first level. New enclosure includes APC UPS, two PDUs, network switch, Cat6A patch panel and Fiber LIU. • Existing B01-A elevations identify Cisco switches, cable management, two Ortronics 24-port patch panels with 11 and 6 used, existing patch panels and APC floor UPS. Field verify active services and transfer plan to new TE.
BCH | • BCH-Q1 — Confirm final BCH scope: Room 107 TE enclosure only, or a new telecom room/rack buildout? [Open] Impact: PMIS scope and acceptance criteria unclear • BCH-Q2 — Why does BCHT-604 show a T78 12RU TE enclosure and a separate BCH Crescent House Room 107 new telecom room elevation? [Open] Impact: Rack/equipment mapping conflict • BCH-Q3 — What active services currently serve Crescent House and where are existing terminations located? [Open] Impact: Cutover/outage risk • BCH-Q4 — What is the approved power source, receptacle type and circuit capacity for the new UPS/PDU? [Open] Impact: Electrical readiness unknown • BCH-Q5 — Is existing HVAC/ambient condition acceptable for TE/network equipment since mechanical scope is excluded? [Open] Impact: Heat/load risk • BCH-Q6 — Are cable tray route, sleeve locations, supports and firestopping details shown/field verified without a BCHT-701 schedule? [Open] Impact: Install delay or firestop gap | Crescent House/BCH is a Telecom Enclosure (TE) scope with mechanical and fire protection excluded by the cover sheet. Scope centers on first-level Room 107 and rack/equipment location shown as Room 00-107 / BCH Crescent House. Field verification, room naming, wall-mounted TE versus 45RU room/rack elevation conflict, active-service cutover, power/UPS/PDU source, firestopping, fiber A/B routing, and cable tray/WAO quantities remain open. | • Cover sheet states BCH receives a Telecom Enclosure and mechanical/fire protection scope has been excluded. Still verify existing life-safety protection, rated penetrations, 4-inch sleeve fire caulk, temporary firestopping and abandoned penetration patching. • TE-only scope does not appear to require new FEC/fire sprinkler work, but all wall/floor/ceiling penetrations must be sealed and rated assemblies maintained. | • Cover sheet explicitly excludes mechanical scope. Verify existing room ambient conditions are acceptable for TE equipment and that no active network equipment will overheat. • If the final scope is a 45RU new telecom room rather than a small TE, HVAC exclusion should be confirmed with VA/AE because telecom-room heat load may differ from TE assumptions. | • Electrical plan includes first-level electrical work and notes for new wall-mount telecom enclosure, grounding/bonding and camera. Verify circuit source, receptacle type, UPS/PDU load, emergency source if required, grounding/bonding and labels. • BCHT-604 shows 12RU TE equipment with APC UPS and PDUs and also a BCH 45RU new telecom room elevation. Confirm exact UPS/PDU/rack power requirement before acceptance. | • BCHT-101 identifies telecom plan first level and enlarged Room 107. BCHT-604 identifies new telecom room/no existing elevations. There is no BCHT-701 schedule in the drawing index, so WAO/cable-tray totals must be field verified from plans and contractor coordination drawings. • BCHT-604 identifies a 12RU TE elevation: APC UPS, two PDUs, network switch, 48-port Cat6A patch panel and Fiber LIU. Also shows BCH Crescent House Room 107 new telecom room elevation. Confirm governing rack/enclosure and labeling.
MCR | • MCR-Q1 — Confirm final room naming and PMIS mapping: MCR Room 107, Fiber Entrance Room 031, Existing 107/137 server/MCR references. [Open] Impact: Room inventory and turnover mapping could be wrong • MCR-Q2 — What existing core/server/rack equipment is being relocated from the existing MCR/server rooms, and what remains? [Open] Impact: Cutover and outage risk • MCR-Q3 — What is the approved MCR activation sequence and required VA/OIT hold points? [Open] Impact: Schedule/cutover impact • MCR-Q4 — Are UPS-A/B, generator/ATS and emergency power paths commissioned and mapped to each rack/PDU? [Open] Impact: Electrical readiness unknown • MCR-Q5 — Are CRAC units fully commissioned with BMS/FMS alarms, redundancy and emergency power? [Open] Impact: Cooling continuity risk • MCR-Q6 — Are clean-agent/preaction/fire alarm systems fully designed, tested and accepted? [Open] Impact: Life-safety acceptance risk | MCR is the most critical EHRM infrastructure building. Scope includes new Main Computer Room, new MDA A/B rows, HDA A/B rows, existing server/MCR equipment transfer from 107/137, redundant fiber Path A/B, new CRAC cooling, UPS A/B, electrical service/ATS/generator integration, clean-agent fire suppression, wet sprinkler/fire alarm interfaces, PACS/CCTV, 359 ft cable tray, and MCR activation window. Major risk is service continuity during backbone/core migration and VA activation. | • MCR has full fire protection scope including wet pipe and clean-agent fire suppression system. Verify preaction/clean-agent design, agent release interface, fire alarm matrix, detection, abort/release stations, room integrity and acceptance testing. • Verify fiber entrance room protection, rated penetrations, firestopping, detector/strobe coverage and no gaps after cable tray installation. • Verify sprinkler/clean-agent coverage around MDA equipment, fire alarm devices, rack clearance and final firestop assemblies. • Verify clean-agent coverage, detector placement, alarm interfaces, and open cabinet airflow protection. • Existing systems must remain protected during temporary fiber, umbilical cord and core relocation work. Verify no impairment without approved fire watch/impairment plan. | • Telecom notes call for indoor computer room air conditioner (CRAC) units tied to building management system. Mechanical sheets included; verify redundant capacity, setpoints, humidity, condensate, controls, alarms and emergency power. • UPS rooms/equipment require thermal load validation, ventilation, emergency power and alarm integration. Verify battery/UPS environmental requirements. • Verify airflow/cold aisle/hot aisle assumptions, blanking panels, floor/ceiling distribution and temperature monitoring. • Server cabinets and patch fields require stable 24/7 cooling and monitoring. Confirm no local hot spots at dense LIU/patch panel zones. • During split-core temporary phase, existing MCR/server equipment remains active. Verify existing cooling remains in service until cutover and decommissioning are complete. | • Electrical set includes site plan, enlarged MCR plans, one-lines and schedules. Verify switchboard/service, ATS/generator integration, normal/emergency/UPS distribution, grounding, lightning protection, SPD, load measurements and commissioning. • MDA rack elevations include new 4-post floor cabinets, LIUs and network elements. Verify redundant A/B power feeds and PDU arrangements. • HDA cabinets include server cabinet front/rear elevations with patch panels and active equipment. Confirm A/B feed separation, PDU mounting, load capacity and labels. • Existing rack elevations identify multiple APC/Chatsworth/HP PDUs, APC Smart UPS and Eaton 9PX units. Verify what transfers, what stays, and temporary power during migration. • New MCR is standalone critical infrastructure. Verify utility service, generator/ATS paths, emergency distribution, grounding electrode and ductbank/site electrical coordination. | • MCRT-101 shows new MCR with MDA-A/B, HDA-A/B, UPS-A/B, cameras and fiber path legend. MCRT-701 shows 10 WAO total, 720 WAO available, 98.1% expansion capacity, 10 total ports with 20% allowance and 359 ft cable tray. • MCRT-701 Data Device and Circuit Schedule - Fiber Entrance Room 1: outlets 31-A/B/C/D plus security devices 07-CAM-03/04/07/08/11; Rack ID TR01-031-1. • MCRT-607: MDA A/B racks contain horizontal distribution LIUs, hybrid FOC, 48x Cat6A to HDA, and reserved LAN/spine/aggregation elements. Maintain A/B path separation. • MCRT-608/609: HDA A/B include 48-port Cat6A patch panels, HD fiber LIUs, backbone side A/B LIU and server cabinet arrangements. • Existing MCR rows 1-3 and B61 server cabinet transfer references are extensive. Maintain service using temporary fiber/umbilical cords and phased core relocation.
SPEC | • No open questions items captured for this building. |  | • No fire / life safety items captured for this building. | • No hvac / cooling items captured for this building. | • No electrical / ups items captured for this building. | • No telecom / fiber items captured for this building.
6. QUALITY AND CONSTRUCTION READINESS
Building | Overall Status | Construction Ready | Fire | HVAC | Electrical | Telecom | Security
01 | Yellow | No | Not Started | Not Started | Not Started | Not Started | Not Started
02 | Yellow | No | Not Started | Not Started | Not Started | Not Started | Not Started
03 | Yellow | No | Not Started | Not Started | Not Started | Not Started | Not Started
04 | Yellow | No | Verify | Verify | Verify | Verify | Verify
05 | Yellow | No | N/A | N/A | Verify | Verify | Verify
06 | Yellow | No | Verify | Verify | Verify | Verify | Verify
07 | Yellow | No | Verify | Verify | Verify | Verify | Verify
08 | Yellow | No | Verify | Verify | Verify | Verify | Verify
09 | Yellow | No | Verify | Verify | Verify | Verify | Verify
10 | Yellow | No | Verify | Verify | Verify | Verify | Verify
12 | Yellow | No | N/A / Verify | N/A | N/A / Verify | Verify | N/A / Verify
13 | Yellow | No | Verify | Verify | Verify | Verify | Verify
14 | Yellow | No | Verify | Verify | Verify | Verify | Verify
15 | Yellow | No | Verify | Verify | Verify | Verify | Verify
16 | Yellow | No | Verify | Verify | Verify | Verify | Verify
17 | Yellow | No | Verify | Verify | Verify | Verify | Verify
18 | Yellow | No | Verify | Verify | Verify | Verify | Verify
20 | Yellow | No | Excluded / Firestop Only | Excluded / Verify Existing | Verify | Verify | Verify Existing
21 | Yellow | No | Excluded / Firestop Only | Verify | Verify | Verify | Verify Existing
22 | Yellow | No | Excluded / Firestop Only | Excluded / Verify Existing | Verify | Verify | Verify Existing
33 | Yellow | No | Excluded / Firestop Only | Excluded / Verify Existing | Verify | Verify | Verify Existing
61 | PILOT PHASE | YES | Not Started | Not Started | Not Started | Not Started | Not Started
62 | Yellow | No | Verify | Verify | Verify | Verify | Verify
70 | Yellow | No | Verify | Verify | Verify | Verify | Verify
78 | Yellow | No | Verify | Verify | Verify | Verify | Verify
80 | Yellow | No | Verify | Verify | Verify | Verify | Verify
82 | Yellow | No | Excluded / Firestop Only | Verify | Verify | Verify | Excluded / Verify Existing
BCH | Yellow | No | Excluded / Firestop Only | Verify | Verify | Verify | Verify Existing
MCR | Yellow | No | Verify | Verify | Verify | Verify | Verify
SITE | Yellow | No | N/A / Maintain Access | N/A | Verify | Verify | Verify Site Access
7. OIT, COMMISSIONING, TURNOVER, AND ACCEPTANCE
Building | OIT Readiness | OIT Status | OIT Blocker / Constraint | Acceptance Readiness | Acceptance Status | Open Gate Count | Owner Decision Queue
01 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
02 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
03 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
04 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
05 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
06 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
07 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
08 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
09 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
10 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
12 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
13 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
14 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
15 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
16 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
17 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
18 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
20 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
21 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
22 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
33 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
61 | 0% | Blocked | No blocker documented | 0% | Not Ready | 0 | Resolve OIT Blocker
62 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
70 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
78 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
80 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
82 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
BCH | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
MCR | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
SITE | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
8. CM/PM DELIVERABLES, ACTIONS, AND CONTRACT ADMINISTRATION — MANUAL INPUT
Record ID | Record Type | Title | Building | Owner | Priority | Status | Date Opened | Due Date | COR Decision Required | Report Cycle | Include in COR Report | Decision / Action Needed | GCC Recommendation | Evidence / Link | Notes
DEL-001 | Deliverable | Weekly Inspection Report | ALL | Aisha | High | Open | 2026-07-16 |  | No | Weekly | Yes | Submit every Friday. | Compile assessment, inspection, risk, question, shutdown, and look-ahead data; Paul final review.
DEL-002 | PTR Update | Biweekly PTR Update | ALL | Paul | High | Open | 2026-07-16 |  | Yes | Biweekly | Yes | Confirm PTR ownership and access. | Prepare current comments, dates, issues, and milestone status at least 24 hours before meeting.
SCH-001 | Schedule Item | Contractor Baseline Schedule | ALL | Paul | Critical | Waiting | 2026-07-16 |  | Yes | Biweekly | Yes | Contractor schedule has not been received. | Obtain and review logic, shutdowns, relocations, submittals, procurement, testing, and commissioning dependencies.
ACT-001 | Action Item | Confirm COR Reporting Expectations | ALL | Paul | High | Open | 2026-07-16 |  | Yes | Weekly | Yes | Confirm templates, routing, due dates, minutes, PTR, and storage. | Document agreed reporting workflow before first recurring submission.
DQ-001 | Design Question | Consolidate Building 61 A/E Questions | 61 | Paul | High | In Progress | 2026-07-14 |  | Yes | Weekly | Yes | A/E clarification required. | Issue coordinated question package through COR. | B61_Assessment
ACT-002 | Action Item | Occupied Room Relocation Planning | ALL | Aisha | High | Open | 2026-07-10 |  | Yes | Weekly | Yes | Hospital direction needed for relocation approach. | Coordinate stakeholders before contractor sequencing is accepted. | Building_Register
DEL-003 | Pay Application | GC Pay Application Review | ALL | Paul | High | Not Started | 2026-07-16 |  | No | Monthly | Yes | Review within five business days of receipt. | Verify work complete versus work billed using schedule, assessments, field records, and deficiencies.
DEL-004 | Commissioning | Commissioning Responsibility Matrix | ALL | Aisha | High | Not Started | 2026-07-16 |  | Yes | Monthly | Yes | Confirm roles after kickoff. | Establish prerequisites, testing, documentation, training, and acceptance responsibilities. | Pilot / Specs
9. COR DECISIONS REQUIRED AND TWO-WEEK LOOK AHEAD
Record ID | Title | Building | Decision / Action Needed | Owner | Status
DEL-002 | Biweekly PTR Update | ALL | Confirm PTR ownership and access. | Paul | Open
SCH-001 | Contractor Baseline Schedule | ALL | Contractor schedule has not been received. | Paul | Waiting
ACT-001 | Confirm COR Reporting Expectations | ALL | Confirm templates, routing, due dates, minutes, PTR, and storage. | Paul | Open
DQ-001 | Consolidate Building 61 A/E Questions | 61 | A/E clarification required. | Paul | In Progress
ACT-002 | Occupied Room Relocation Planning | ALL | Hospital direction needed for relocation approach. | Aisha | Open
DEL-004 | Commissioning Responsibility Matrix | ALL | Confirm roles after kickoff. | Aisha | Not Started
Two-week look ahead: continue assessment completion; consolidate A/E questions; obtain and review the contractor baseline schedule; confirm COR reporting procedures; coordinate occupied-room relocation impacts; validate shutdown requirements; and establish commissioning responsibilities after the post-award meeting.
Formulas:
Weekly = IF([Selected Building]="","",IFERROR(INDEX(PMIS_Data!$S3:S40,1),""))
Rooms = IF([Selected Building]="","",IFERROR(INDEX(PMIS_Data!$T3:T40,1),""))

## COR_Report
COR PROJECT STATUS REPORT — PROJECT 518-22-700
Report Type | Weekly | Reporting Period Start | 2026-07-13
Prepared By | Paul Thibodeau | Reporting Period End | 2026-07-17
Reviewed With | Aisha | Selected Building | 61
Project Phase | Preconstruction | Contractor Schedule | Not Received
Report Source | PMIS assessments + CM/PM Operations
Buildings | Avg Readiness | Rooms | Open Risks | Open Questions | Shutdowns | Not Ready | COR Decisions
30 | 50.67% | 814 | 0 | 0 | 1 | 29 | 6
1. EXECUTIVE SUMMARY
The project is currently in Preconstruction. 30 buildings are represented in PMIS with an average readiness of 51%. Assessment sheets remain the source of truth and currently reflect 814 rooms, 0 open risks, 0 open questions, 1 active shutdowns, and 29 buildings not ready. CM/PM Operations identifies 6 open COR decisions. The contractor baseline schedule status is: Not Received.
2. ASSESSMENT AND FIELD ACTIVITY
Building | Status | Readiness | Rooms | Risks | Questions | Next Action | Major Blocker
01 | Yellow | 50% | 29 | 0 | 0 | Field verify Room 107, existing B02, 138, and 282; confirm active services, existing rack/equipment transfer, B01-TR107A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 394 ft cable tray routes, and telecom cutover sequence. | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning.
02 | Yellow | 50% | 30 | 0 | 0 | Field verify new Rooms 141, 236, 342 and existing B-06/141/236; confirm active services, rack/equipment transfer, B02-TR141A/B, B02-TR236A/B, B02-TR342A/B panel sources, CU-1-01/CU-2-01/CU-3-01 cooling assignments, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, 2,560 ft cable tray routes, and telecom cutover sequence. | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance.
03 | Yellow | 50% | 29 | 0 | 0 | Field verify Room 101E, existing Room 107, and existing DMARC Room 101C; confirm active services, existing rack/equipment transfer, B03-TR101CA/B panel sources, CU-01 cooling assignment, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 961 ft cable tray routes, Room 107 inventory, and telecom cutover/fiber transfer sequence. | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance.
04 | Yellow | 50% | 27 | 0 | 0 | Field verify TR rooms B05, 141, and 244A; confirm cooling, panel/circuiting, fire alarm/sprinkler impacts, FEC locations, and cutover/phasing plan. | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open.
05 | Yellow | 55% | 26 | 0 | 0 | Field verify Room 150 TE location, existing 153-A equipment to remain/transition, electrical source, UPS/PDU receptacles, PACS/CCTV requirements, firestopping, and cutover sequence. | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified.
06 | Yellow | 50% | 27 | 0 | 0 | Field verify existing B-01 equipment, Rooms 178 and 233, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, and telecom cutover sequence. | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open.
07 | Yellow | 50% | 26 | 0 | 0 | Field verify TR B-18 and 228A; confirm rack/equipment layout, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, and telecom cutover sequence. | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open.
08 | Yellow | 50% | 27 | 0 | 0 | Field verify B-15, B12B, and 2065A; confirm active services, 2065A rack layout, panel/power source, IU/CU cooling, hazardous material/abatement impacts, FEC locations, PACS/CCTV, and telecom cutover sequence. | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open.
09 | Yellow | 50% | 27 | 0 | 0 | Field verify B01, 104B, and 206A; confirm existing equipment and active services, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, and telecom cutover sequence. | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open.
10 | Yellow | 50% | 27 | 0 | 0 | Field verify attic Telecom Room 200A, basement normal/emergency electrical source rooms B24/B25, existing wall-mounted rack/equipment, panel sources B10-TR200AA/AB, IU/CU-1-01 cooling, FEC/fire alarm/sprinkler impacts, hazardous/abatement scope, and telecom cutover plan. | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination.
12 | Yellow | 60% | 26 | 0 | 0 | Field verify existing fiber pathway through Building 12, existing rack/demarc/serving closet condition, floor/wall penetrations, routing from basement/first/second level telecom plans, phasing/cutover approach, and test/label/as-built deliverables. | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover.
13 | Yellow | 50% | 26 | 0 | 0 | Field verify Room 124 and existing Tel Room 222; confirm active services, rack/equipment transfer, B13-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open.
3. RISKS, DEFICIENCIES, AND OPEN QUESTIONS
Building | Open Risks | Open Questions | Risk Density | Question Density | Owner Focus | Execution Gate | Dashboard Signal
01 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
02 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
03 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
04 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
05 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
06 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
07 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
08 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
09 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
10 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
12 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
13 | 0% | 0 | 0 | 0 | Monitor | Review | 🔴 ATTENTION
4. SCHEDULE, SHUTDOWNS, AND OPERATIONAL IMPACTS
Shutdown ID | System | Building | Requested | Approved | Scheduled | Duration | Stakeholders | Status | Notes
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational priorities include obtaining the contractor baseline schedule, coordinating occupied-room relocations, confirming the post-award workflow, validating shutdown requirements, and establishing a reliable two-week look-ahead.
5. DESIGN AND TECHNICAL COORDINATION
Building | Open Questions | Major Blocker | Fire / Life Safety | HVAC / Cooling | Electrical / UPS | Telecom / Fiber
01 | • B01-Q1 — Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? [Closed] Impact: Room inventory could miss scope • B01-Q2 — What active services are currently fed from existing Rooms B02, 138 and 282? [Closed] Impact: Potential communications/security outage • B01-Q3 — What equipment from existing racks transfers to new Room 107 versus remains/decommissions? [Closed] Impact: Cutover and rack elevation risk • B01-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? [Closed] Impact: Cooling continuity unclear • B01-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? [Closed] Impact: Life-safety acceptance risk • B01-Q6 — Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Closed] Impact: Electrical readiness unknown | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning. | • Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems. • Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. • Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes. • Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place. | • Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup. • Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration. • Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear. • Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating. | • Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation. • Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements. • Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition. • Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope. | • 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1. • Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan. • Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence. • Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway.
02 | • B02-Q1 — Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? [Open] Impact: Room inventory could miss scope • B02-Q2 — What active services are currently fed from existing Rooms B-06, 141 and 236? [Open] Impact: Potential communications/security outage • B02-Q3 — What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? [Open] Impact: Cutover and rack elevation risk • B02-Q4 — Which IU/CU pair serves each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B02-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? [Open] Impact: Life-safety acceptance risk • B02-Q6 — Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance. | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping. • Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping. • Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | • Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms. • Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm. • Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration. • Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete. | • Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels. • Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping. • Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits. • Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs. | • 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray. • 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope. • 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count. • Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover.
03 | • B03-Q1 — Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? [Open] Impact: Room inventory could miss scope • B03-Q2 — What active services are currently fed from existing Room 107 and DMARC Room 101C? [Open] Impact: Potential communications/provider outage • B03-Q3 — What existing equipment transfers to new Room 101E versus remains/decommissions? [Open] Impact: Cutover and rack elevation risk • B03-Q4 — Which IU/CU pair serves Room 101E and is it on emergency/backup power? [Open] Impact: Cooling continuity unclear • B03-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? [Open] Impact: Life-safety acceptance risk • B03-Q6 — Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance. | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse. • Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer. • Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations. | • Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm. • Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete. • Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains. • No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements. | • Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements. • Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements. • Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer. • Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations. | • 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2. • Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover. • Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted. • Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced.
04 | • B04-Q1 — Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? [Open] Impact: Incomplete room inventory / missed scope • B04-Q2 — Are B05, 141, and 244A cooling systems on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B04-Q3 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B04-Q4 — What is the approved migration and cutover sequence for active Building 04 services? [Open] Impact: Potential communications outage • B04-Q5 — Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? [Open] Impact: Work stoppage or exposure risk • B04-Q6 — Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? [Open] Impact: Electrical delay or overload risk | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open. | • Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning. • FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies. • Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations. | • Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up. • Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control. • Verify cooling unit, routing, condensate, controls, and emergency/backup power path. | • Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits. • Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting. • Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source. | • New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • TR/panel identified; verify rack elevation and pathway details against 04T sheets.
05 | • B05-Q1 — Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? [Open] Impact: Room inventory could be wrong • B05-Q2 — What active services are currently fed from the existing 153-A TE/legacy patch panels? [Open] Impact: Potential communications outage • B05-Q3 — What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? [Open] Impact: Cutover risk • B05-Q4 — Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? [Open] Impact: Power source cannot be verified • B05-Q5 — Is emergency/backup power required or provided for the TE UPS/PDU source? [Open] Impact: Continuity requirement unclear • B05-Q6 — Are firestopping locations and surface raceway/conduit routes shown and coordinated? [Open] Impact: Rated assembly/firestop risk | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified. | • Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts. • Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling. | • Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling. • Existing wall/wall-mount TE area; verify existing environmental conditions during field survey. | • 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source. • Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover. | • New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU. • Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records.
06 | • B06-Q1 — Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? [Open] Impact: Room inventory could miss scope • B06-Q2 — What active services are fed from existing B-01 and Room 178 legacy equipment? [Open] Impact: Potential communications outage • B06-Q3 — What is the approved cutover sequence for B-01, 178 and 233? [Open] Impact: Cutover risk • B06-Q4 — Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B06-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B06-Q6 — Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? [Open] Impact: Electrical readiness unknown | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open. | • Existing equipment area; verify no cabling penetrations are left unsealed. • Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs. • Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft. | • Verify basement equipment environmental condition and any heat/load issues during cutover. • Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route. • Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls. | • Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements. • Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation. • Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power. | • Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS. • Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification. • Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
07 | • B07-Q1 — Confirm final TR scope: B-18 basement and 228A second floor only? [Open] Impact: Room inventory could miss scope • B07-Q2 — Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? [Open] Impact: Cooling scope unclear • B07-Q3 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B07-Q4 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B07-Q5 — What active services are currently fed from B-18 and/or existing pathways serving 228A? [Open] Impact: Potential communications outage • B07-Q6 — Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open. | • Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination. • Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications. | • Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm. • Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route. | • Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement. • Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels. | • 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU. • TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover.
08 | • B08-Q1 — Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? [Open] Impact: Room inventory may miss scope • B08-Q2 — What active services are currently fed from existing B-15 equipment? [Open] Impact: Potential communications outage • B08-Q3 — Is B12B truly a TE/equipment location or only a cabling pathway/service area? [Open] Impact: Scope ambiguity • B08-Q4 — Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? [Open] Impact: Cooling continuity unclear • B08-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? [Open] Impact: Life safety acceptance risk • B08-Q6 — Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open. | • Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected. • Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers. • Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades. | • Verify existing environmental conditions and whether active legacy equipment remains during cutover. • Field verify whether TE equipment load requires cooling or if served by existing building HVAC. • Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls. | • Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements. • Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel. • Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope. | • Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS. • Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance. • New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS.
09 | • B09-Q1 — Confirm final TR scope: B01 basement, 104B first level, and 206A second level? [Open] Impact: Room inventory may miss scope • B09-Q2 — What active services are currently fed from B01 existing equipment/security/network devices? [Open] Impact: Potential communications/security outage • B09-Q3 — What hazardous/abatement steps apply to B01, 104B and 206A work areas? [Open] Impact: Work delay or exposure risk • B09-Q4 — Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B09-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B09-Q6 — Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open. | • Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR. • Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft. • Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations. | • Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms. • Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power. • Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power. | • Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes. • Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits. • Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits. | • Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover. • Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. • Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records.
10 | • B10-Q1 — Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? [Open] Impact: Room inventory could miss scope • B10-Q2 — What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? [Open] Impact: Potential communications outage • B10-Q3 — What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? [Open] Impact: Work delay/exposure risk • B10-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? [Open] Impact: Cooling continuity unclear • B10-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? [Open] Impact: Life-safety acceptance risk • B10-Q6 — Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? [Open] Impact: Electrical readiness unknown | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination. | • Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping. • Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place. • Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment. | • Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm. • No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work. • No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted. | • Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels. • Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing. • Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required. | • 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover. • Coordinate telecom power pathways through/source from basement electrical room if applicable. • Coordinate emergency source/backup power pathways for telecom equipment and cooling.
12 | • B12-Q1 — Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? [Open] Impact: Scope misunderstanding • B12-Q2 — What exact pathway does the Building 12 fiber take through basement, first and second levels? [Open] Impact: Fiber pull and access risk • B12-Q3 — Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? [Open] Impact: Termination and ownership unclear • B12-Q4 — Are existing conduits/cable trays available and below fill limits for the new fiber? [Open] Impact: Pathway capacity risk • B12-Q5 — Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? [Open] Impact: Life safety/firestop risk • B12-Q6 — What is the approved cutover/testing/acceptance sequence for Building 12 fiber? [Open] Impact: Possible outage or acceptance delay | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover. | • No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route. • No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work. | • No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment. • Field verify existing environmental conditions only if existing service point/equipment is accessed. | • No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown. • Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling. | • Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing. • 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only.
13 | • B13-Q1 — Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? [Open] Impact: Room inventory could miss scope • B13-Q2 — What active services are currently fed from existing Tel Room 222 equipment? [Open] Impact: Potential communications/security outage • B13-Q3 — What hazardous/abatement steps apply to first-level Room 124 work? [Open] Impact: Work delay or exposure risk • B13-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? [Open] Impact: Cooling continuity unclear • B13-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? [Open] Impact: Life-safety acceptance risk • B13-Q6 — Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | • Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B. • Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124.
6. QUALITY AND CONSTRUCTION READINESS
Building | Overall Status | Construction Ready | Fire | HVAC | Electrical | Telecom | Security
01 | Yellow | No | Not Started | Not Started | Not Started | Not Started | Not Started
02 | Yellow | No | Not Started | Not Started | Not Started | Not Started | Not Started
03 | Yellow | No | Not Started | Not Started | Not Started | Not Started | Not Started
04 | Yellow | No | Verify | Verify | Verify | Verify | Verify
05 | Yellow | No | N/A | N/A | Verify | Verify | Verify
06 | Yellow | No | Verify | Verify | Verify | Verify | Verify
07 | Yellow | No | Verify | Verify | Verify | Verify | Verify
08 | Yellow | No | Verify | Verify | Verify | Verify | Verify
09 | Yellow | No | Verify | Verify | Verify | Verify | Verify
10 | Yellow | No | Verify | Verify | Verify | Verify | Verify
12 | Yellow | No | N/A / Verify | N/A | N/A / Verify | Verify | N/A / Verify
13 | Yellow | No | Verify | Verify | Verify | Verify | Verify
7. OIT, COMMISSIONING, TURNOVER, AND ACCEPTANCE
Building | OIT Readiness | OIT Status | OIT Blocker | Acceptance Readiness | Acceptance Status | Open Gates | Owner Decision Queue
01 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
02 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
03 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
04 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
05 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
06 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
07 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
08 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
09 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
10 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
12 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
13 | 0% | Blocked | No blocker documented | 0% | Not Ready | 6 | Resolve OIT Blocker
8. CM/PM DELIVERABLES AND ACTIONS
Record ID | Type | Title | Building | Owner | Priority | Status | Opened | Due | Cycle | Decision Required | Recommendation
DEL-001 | Deliverable | Weekly Inspection Report | ALL | Aisha | High | Open | 2026-07-16 | 0 | Weekly | No | Compile assessment, inspection, risk, question, shutdown, and look-ahead data; Paul final review.
DEL-002 | PTR Update | Biweekly PTR Update | ALL | Paul | High | Open | 2026-07-16 | 0 | Biweekly | Yes | Prepare current comments, dates, issues, and milestone status at least 24 hours before meeting.
SCH-001 | Schedule Item | Contractor Baseline Schedule | ALL | Paul | Critical | Waiting | 2026-07-16 | 0 | Biweekly | Yes | Obtain and review logic, shutdowns, relocations, submittals, procurement, testing, and commissioning dependencies.
ACT-001 | Action Item | Confirm COR Reporting Expectations | ALL | Paul | High | Open | 2026-07-16 | 0 | Weekly | Yes | Document agreed reporting workflow before first recurring submission.
DQ-001 | Design Question | Consolidate Building 61 A/E Questions | 61 | Paul | High | In Progress | 2026-07-14 | 0 | Weekly | Yes | Issue coordinated question package through COR.
ACT-002 | Action Item | Occupied Room Relocation Planning | ALL | Aisha | High | Open | 2026-07-10 | 0 | Weekly | Yes | Coordinate stakeholders before contractor sequencing is accepted.
DEL-003 | Pay Application | GC Pay Application Review | ALL | Paul | High | Not Started | 2026-07-16 | 0 | Monthly | No | Verify work complete versus work billed using schedule, assessments, field records, and deficiencies.
DEL-004 | Commissioning | Commissioning Responsibility Matrix | ALL | Aisha | High | Not Started | 2026-07-16 | 0 | Monthly | Yes | Establish prerequisites, testing, documentation, training, and acceptance responsibilities.
9. COR DECISIONS AND TWO-WEEK LOOK AHEAD
Record ID | Title | Building | Decision / Action Needed | Owner | Status
DEL-002 | Biweekly PTR Update | ALL | Confirm PTR ownership and access. | Paul | Open
SCH-001 | Contractor Baseline Schedule | ALL | Contractor schedule has not been received. | Paul | Waiting
ACT-001 | Confirm COR Reporting Expectations | ALL | Confirm templates, routing, due dates, minutes, PTR, and storage. | Paul | Open
DQ-001 | Consolidate Building 61 A/E Questions | 61 | A/E clarification required. | Paul | In Progress
ACT-002 | Occupied Room Relocation Planning | ALL | Hospital direction needed for relocation approach. | Aisha | Open
DEL-004 | Commissioning Responsibility Matrix | ALL | Confirm roles after kickoff. | Aisha | Not Started
Two-week look ahead: continue assessment completion; consolidate A/E questions; obtain and review the contractor baseline schedule; confirm COR reporting procedures; coordinate occupied-room relocation impacts; validate shutdown requirements; and establish commissioning responsibilities after the post-award meeting.
Formulas:
COR Decisions = IF([Report Type]="","",'CM_PM Operations'!H241)
Status = IF([Report Type]="","",IFERROR('CM_PM Operations'!I241,""))

## Building_Register (hidden)
CAMPUS BUILDING REGISTER
Building-level scope, function, risk, and notes
Building ID | Building | Function | Criticality | Generator | Telecom Room | Status | 7.4.26 | Primary System | Questions | Notes
| Buildings | Level | SOLUTION | ROOM NUMBER | NUMBER OF RACKS |  |  | DISPLACES
| 1 | B | SERVED FROM L1
|  | 1 | TR | 107 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | HR OFFICE
|  | 2 | SERVED FROM L1
| 2 | B | SERVED FROM L1
|  | 1 | TR | 141 | 2 RACKS | OCCUPIED |  | PIV OFFICE
|  | 2 | TR | 236 | 2 RACKS | UNOCCUPIED |  | IRM CLOSET
|  | 3 | TR | 342 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | STORAGE
|  | 4 | SERVED FROM L3
| 3 | B | SERVED FROM L1
|  | 1 | TR | 101C | 2 RACKS | UNOCCUPIED |  | TELECOM ROOM
| 4 | B | TR | B18/19 | 2 RACKS | UNOCCUPIED |  | MOP STORAGE/BREAK ROOM
|  | 1 | TR | 141 | 1 NEW, 1 FUTURE | OCCUPIED |  | SOCIAL WORKER
|  | 2 | TR | 244 | 1 NEW, 1 FUTURE | OCCUPIED |  | CLINICAL PSYCHOLOGIST
| 5 | B | SERVED FROM L1
|  | 1 | TE | 150 | TE | UNOCCUPIED |  | FILE CABINETS TO BE RELOCATED
|  | 2 | LEASED SPACE - N/A
ATTIC
| 6 | B | SERVED FROM L1
|  | 1 | TR | 178 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | TELECOM ROOM
|  | 2 | TR | 233 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | PATIENT TOILET
| 7 | B | TR | B18/ 20G | 1 NEW, 1 FUTURE | UNOCCUPIED |  | OFFICE/ NEW ENTRY TO ADJACENT TOILET
|  | 1 | SERVED FROM L2
|  | 2 | TR | 228A | 2 RACKS | OCCUPIED |  | SHARED SOCIAL WORKER OFFICE
| 8 | B | SERVED FROM L2
|  | 1 | SERVED FROM L2
|  | 2 | TR | 2065A | 2 RACKS | UNOCCUPIED |  | TELECOM ROOM |  | RM #223A NOT 2065
ATTIC
| 9 | B | TR | B01 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | STORAGE ROOM |  | NEEDS AC
|  | 1 | TR | 104B | 1 NEW, 1 FUTURE | OCCUPIED |  | INTERVIEW ROOM | DRAWINGS SHOW SF DEFICENCY | ALLOCATE WALLS MOVE INTO 104A FOR CLEARANCE
WHY IS THERE ONLY 82 SF? DEVIATING FROM PLANS?
|  | 2 | TR | 206 | 1 NEW, 1 FUTURE | OCCUPIED |  | HALF OF OFFICE/UNOCCUPIED
| 10 | B | SERVED FROM L2
|  | 1 | SERVED FROM L2
|  | ATTIC | TR | 200A | 1 NEW, 1 FUTURE | UNOCCUPIED |  | UNOCCUPIED |  | NEEDS TO BE BROUGHT UP TO CODE/GUTTED
| 12 | B | FIBER ONLY
|  | 1 | FIBER ONLY
|  | 2 | FIBER ONLY
| 13 | B | SERVED FROM L1
|  | 1 | TR | 124 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | HALF OF TELEHEALTH |  | EMPTY BUILDING - SEWER ISSUE?
|  | 2 | SERVED FROM L1
| 14 | B | SERVED FROM L1
|  | 1 | TR | 119 | 1 NEW, 1 FUTURE | OCCUPIED |  | OFFICE |  | NO AC
|  | 2 | SERVED FROM L1
| 15 | B | SERVED FROM L1
|  | 1 | TR | 124 | 1 NEW, 1 FUTURE | OCCUPIED |  | HALF OF OFFICE |  | NO AC
|  | 2 | SERVED FROM L1
| 16 | B | TR | 15 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | TELECOM ROOM |  | HAS AC - 12KBTA - NOT UP TO CODE
|  | 1 | SERVED FROM LB
|  | 2 | SERVED FROM LB
|  | ATTIC | SERVED FROM LB
| 17_29 | B | SERVED FROM L1
|  | 1 | TR | 118 | 1 NEW, 1 FUTURE | OCCUPIED |  | OFFICE |  | TRENCHING FROM 29-17
|  | 2 | SERVED FROM L1
ATTIC
| 18 | B | SERVED FROM L1
|  | 1 | TR | 110 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | STORAGE |  | ACTUALLY ROOM 111A - 36KBTU - WW363E
|  | 2 | SERVED FROM L1
ATTIC
| 19 | B | SERVE FROM B21
|  | 1 | SERVE FROM B21
| 20_32 | 1 | TE | 1B | TE | OCCUPIED |  | BOOKCASE TO BE RELOCATED
| 21_19 | B | SERVE FROM L1
|  | 1 | TE | 100A | TE | OCCUPIED |  | REFRIGERATOR/FILE CABINET RELOCATED
| 22 | 1 | TE | 106 | TE |  |  |  |  | N/A - BREAKROOM?
|  | MEZZ | SERVE FROM L1
| 33 | B | TE | B23 | TE | OCCUPIED |  | CABINET REMOVED/ FILE CABINETS RELOCATED
|  | 1 | SERVE FROM LB
| 61 | B | TR | B13 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | RESTROOM, CORRIDOR, ALCOVE |  | NEEDS AC
|  | 1 | TR | 124 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | COPY ROOM, 2 STORAGE ROOMS | WALLS ALLOCATE FOR CLEARANCE NEEDED | CHECK PLANS TO SEE IF WALLS ARE KNOCKED DOWN
|  | 2 | TR | 226 | 1 NEW, 1 FUTURE | UNOCCUPIED |  | COPY/MAILROOM, FILE CABINET ALCOVE, WAITING ALCOVE | WALLS ALLOCATE FOR CLEARANCE NEEDED | CHECK PLANS TO SEE IF WALLS ARE KNOCKED DOWN
ATTIC
| 62 | B | TR | B24A | 1 NEW, 1 FUTURE | UNOCCUPIED |  | RESTROOM BEING USED AS STORAGE |  | DEMO - NO AC
|  | 1 | TR | 125 | 1 NEW, 1 FUTURE | OCCUPIED |  | MEDICATION ROOM |  | RN OFFICE
|  | 2 | TR | 225 | 1 NEW, 1 FUTURE | OCCUPIED |  | OFFICE |  | RN OFFICE - NO AC
PH
| 70 | B | TR | B27 | 1 NEW, 1 FUTURE | OCCUPIED |  | OFFICE
|  | 1 | TR | 125 | 1 NEW, 1 FUTURE | OCCUPIED |  | OFFICE CUBICLES
|  | 2 | TR | 262A | 1 NEW, 1 FUTURE | OCCUPIED |  | OFFICE
| 78_78A | B | B78-TR B78A-TR | B30 | 2 RACKS | UNOCCUPIED |  | STORAGE |  | NEEDS NEW AC
|  |  |  | B33 | 1 RACK | UNOCCUPIED |  | VOLUNTARY |  | NEEDS AC - NEW WALL BEING BUILT
|  | 1 | TR | 1232 | 2 RACKS | OCCUPIED |  | OFFICE
|  | 2 | TR | 227A | 2 RACKS | UNOCCUPIED |  | STORAGE |  | NEEDS TO BE EMPTIED
|  | 3 | TR | 342 | 2 RACKS | OCCUPIED |  | COUNSEL OFFICE |  | NO AC
|  | 4 | TR | 401 | 1 NEW, 1 FUTURE | OCCUPIED |  | PSYCH OFFICE |  | CENTRALIZED AC - NEEDS MINI SPLIT
PH
| 80 | B | SERVED FROM L1
|  | 1 | TR | 102 | 1 NEW, 1 FUTURE | OCCUPIED |  | PEER SUPPORT OFFICE |  | NO AC
| 81 | 1 | TE | 100F, 104 | (2) TE | OCCUPIED |  | UNOCCUPIED |  | 104 - OCCUPIED - NO AC
ATTIC
| 82 | B | SERVED FROM L1
|  | 1 | TE | 102 | TE | UNOCCUPIED |  | STORAGE
| BCHCRESCEN T HOUSE | 1 | TE | 107 | TE |  |  | PRINTER/CABINETS TO BE RELOCATED |  | N/A
2
ATTIC
MCR
SITE

## PMIS_Data (hidden)
PMIS_DATA — FORMULA-FED BUILDING / AREA ROLLUP | [15 empty] | Data | [7 empty] | Building Selector
Building | Sheet | Overall Status | Sheet Readiness | Avg Readiness | Construction Ready | Room Count | Open Risks | Open Questions | Open Photos | HVAC | Electrical | Telecom | Fire Protection | Fire Alarm | Security | Next Action | Major Blocker | Risk Density | Question Density | Photo Density | Owner Focus | Execution Gate | Shutdowns | Source Health | Payment Confidence | Payment Recommendation | OIT Readiness | OIT Status | OIT Blocker / Constraint | Material Compliance | QA / Material Status | Productivity Score | Productivity Status | Acceptance Readiness | Acceptance Status | Completion | Open Gate Count | Owner Decision Queue | Dashboard Signal | Owner Controls Health | Payment Row | OIT Row | Material Row | Productivity Row | Acceptance Row
01 | B01_Assessment | Yellow | 50% | 50% | No | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify Room 107, existing B02, 138, and 282; confirm active services, existing rack/equipment transfer, B01-TR107A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 394 ft cable tray routes, and telecom cutover sequence. | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 96 | 105 | 117 | 126 | 134
02 | B02_Assessment | Yellow | 50% | 50% | No | 30 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify new Rooms 141, 236, 342 and existing B-06/141/236; confirm active services, rack/equipment transfer, B02-TR141A/B, B02-TR236A/B, B02-TR342A/B panel sources, CU-1-01/CU-2-01/CU-3-01 cooling assignments, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, 2,560 ft cable tray routes, and telecom cutover sequence. | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 108 | 117 | 129 | 138 | 146
03 | B03_Assessment | Yellow | 50% | 50% | No | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify Room 101E, existing Room 107, and existing DMARC Room 101C; confirm active services, existing rack/equipment transfer, B03-TR101CA/B panel sources, CU-01 cooling assignment, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 961 ft cable tray routes, Room 107 inventory, and telecom cutover/fiber transfer sequence. | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 107 | 116 | 128 | 137 | 145
04 | B04_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify TR rooms B05, 141, and 244A; confirm cooling, panel/circuiting, fire alarm/sprinkler impacts, FEC locations, and cutover/phasing plan. | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 98 | 107 | 119 | 128 | 136
05 | B05_Assessment | Yellow | 55% | 55% | No | 26 | 0 | 0 | 0 | N/A | Verify | Verify | N/A | Verify | Verify | Field verify Room 150 TE location, existing 153-A equipment to remain/transition, electrical source, UPS/PDU receptacles, PACS/CCTV requirements, firestopping, and cutover sequence. | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 84 | 93 | 105 | 114 | 122
06 | B06_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify existing B-01 equipment, Rooms 178 and 233, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, and telecom cutover sequence. | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 98 | 107 | 119 | 128 | 136
07 | B07_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify TR B-18 and 228A; confirm rack/equipment layout, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, and telecom cutover sequence. | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 89 | 98 | 110 | 119 | 127
08 | B08_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify B-15, B12B, and 2065A; confirm active services, 2065A rack layout, panel/power source, IU/CU cooling, hazardous material/abatement impacts, FEC locations, PACS/CCTV, and telecom cutover sequence. | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 98 | 107 | 119 | 128 | 136
09 | B09_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify B01, 104B, and 206A; confirm existing equipment and active services, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, and telecom cutover sequence. | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 98 | 107 | 119 | 128 | 136
10 | B10_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify attic Telecom Room 200A, basement normal/emergency electrical source rooms B24/B25, existing wall-mounted rack/equipment, panel sources B10-TR200AA/AB, IU/CU-1-01 cooling, FEC/fire alarm/sprinkler impacts, hazardous/abatement scope, and telecom cutover plan. | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 98 | 107 | 119 | 128 | 136
12 | B12_Assessment | Yellow | 60% | 60% | No | 26 | 0 | 0 | 0 | N/A | N/A / Verify | Verify | N/A / Verify | N/A / Verify | N/A / Verify | Field verify existing fiber pathway through Building 12, existing rack/demarc/serving closet condition, floor/wall penetrations, routing from basement/first/second level telecom plans, phasing/cutover approach, and test/label/as-built deliverables. | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 84 | 93 | 105 | 114 | 122
13 | B13_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 124 and existing Tel Room 222; confirm active services, rack/equipment transfer, B13-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 91 | 100 | 112 | 121 | 129
14 | B14_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 119 and existing basement Tel/F Panel B.01/B2; confirm active services, rack/equipment transfer, B14-TR119A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 14 includes new first-level Telecom Room 119 and existing basement telecom rooms B.01/B2; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 99 | 108 | 120 | 129 | 137
15 | B15_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 124A, existing Tel Room 222 and basement B01; confirm active services, rack/equipment transfer, B15-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence. | Building 15 includes new first-level Telecom Room 124A and existing telecom transition points at second-level Tel Room 222 and basement B01; field verification, active service cutover, 240V UPS/PDU power, dedicated heat-pump cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 99 | 108 | 120 | 129 | 137
16 | B16_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Room 015 and existing Room 014; confirm active services, rack/equipment transfer, B16-TR015A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, panel replacement/load measurement, and telecom cutover sequence. | Building 16 includes new basement Telecom Room 015 and existing basement Telecom Room 014; field verification, active service transfer, 240V UPS/PDU power, dedicated cooling, panel replacement/source coordination, firestopping, PACS/CCTV integration, and cable tray coordination remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 91 | 100 | 112 | 121 | 129
17 | B17_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 118, existing B35A, and Building 29 service path; confirm active services, B17-TR118A/B panel sources, BUS-B17-EQDP / BUS-B17-NPB1-R sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, hazardous material impacts, and cutover plan. | Building 17_29 includes new first-level Telecom Room 118 serving Building 17 and Building 29, plus existing basement Telecom Closet B35A; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, cable tray, firestopping, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 99 | 108 | 120 | 129 | 137
18 | B18_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 110, existing TE 111B, existing Closet 213, and all active services; confirm B18-TR110A/B panel sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, lead-paint/hazardous impacts, and cutover plan. | Building 18 includes new first-level Telecom Room 110 and existing telecom transition rooms 111B and 213; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, lead-paint/first-level hazardous material coordination, firestopping, cable tray, and PACS/CCTV integration remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 98 | 107 | 119 | 128 | 136
20 | B20_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Office 1B new TE location, existing Tel/Data Closet 8A, active services, TE01-1B-1 schedule, existing open TE cabinet, existing ground bar/patch panel/equipment box/indoor AC/backboard, 459 ft cable tray route, 10 Cat6A cross-connect cables, power/UPS/PDU source, and fiber Path A/B cutover. | Building 20 is a telecom-enclosure building, not a full TR buildout. Scope centers on new first-level Office 1B wall-mount TE enclosure and existing Tel/Data Closet 8A; mechanical and fire protection scope are excluded by the cover sheet, but field verification, active equipment transfer, fiber/copper cutover, cable tray, firestopping, power/UPS/PDU, and existing equipment protection remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 90 | 99 | 111 | 120 | 128
21 | B21_Assessment | Yellow | 50% | 50% | No | 27 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify new TE location at M&O Foreman Office 100A, existing B21 B1.TR, existing B19 B05TR, B19-serving-B21 relationship, active services, TR01-104-1 / 100-A schedule, 659 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, and all firestopping/penetrations. | Building 21 is combined with Building 19 and is primarily a telecom-enclosure scope. New first-level M&O Foreman Office 100A / RM 104 schedule is served by a new 12RU TE enclosure, while existing Building 21 B1.TR and Building 19 B05TR equipment remain transition points. Fire protection scope is excluded, but mechanical/electrical sheets exist for equipment support. Field verification, active-service transfer, 659 ft cable tray, firestopping, UPS/PDU power, fiber/copper cutover, and B19/B21 scope boundary remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 98 | 107 | 119 | 128 | 136
22 | B22_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Break Room 102 new TE location, existing Room 103 wall/wall-mount TE, active services, TR01-102-1 schedule, 139 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, and existing B19 port relationship. | Building 22 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new first-level Break Room 102 TE enclosure and existing first-level wall/wall-mount TE Room 103. Field verification, active service transfer, 139 ft cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, and B19 utility service relationship remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 92 | 101 | 113 | 122 | 130
33 | B33_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Excluded / Verify Existing | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify EEO Manager Office B23 new TE location, existing Tel Closet B17, active services, TE01-B23-1 schedule, 102 ft basement cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, existing camera/security devices, and B17 legacy port/service relationships. | Building 33 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new basement EEO Manager Office B23 TE enclosure and existing Tel Closet B17. Field verification, active service transfer, 102 ft basement cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, fiber/copper cutover, and legacy service relationships to Buildings 3, 80 and 82 remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 91 | 100 | 112 | 121 | 129
61 | B61_Assessment | PILOT PHASE | 55% | 55% | YES | 29 | 0 | 0 | 0 | Not Started | Not Started | Not Started | Not Started | Not Started | Not Started | Field verify B13H-A, 124, 226, and existing 137/137A; confirm active services, rack/equipment transfer, B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB panel sources, IU/CU equipment, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, 1,966 ft cable tray routes, and cutover sequence. | Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. | 0 | 0 | 0 | Monitor | Ready | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 0% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 0 | Resolve OIT Blocker | 🔴 ATTENTION | 0% | 97 | 106 | 118 | 127 | 135
62 | B62_TR_Assessment | Yellow | 50% | 50% | No | 23 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Verify cooling power path, firestopping, extinguisher location, and existing conditions | Cooling / emergency power not verified | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 80 | 89 | 101 | 110 | 118
70 | B70_TR_Assessment | Yellow | 50% | 50% | No | 23 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Verify cooling power path, firestopping, extinguisher locations, and migration phasing | Cooling / emergency power and existing TR phasing not verified | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 84 | 93 | 105 | 114 | 122
78 | B78_Assessment | Yellow | 50% | 50% | No | 32 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify rooms B30, B35, 1232, 227A, 342, 401 and existing telecom rooms 15E, 1234, 353, 308A, 408A; confirm active equipment, rack transfers, HVAC units, panel sources, UPS/PDU power, FEC locations, FA/FP modifications, PACS/CCTV, hazardous material impacts, cable tray routes, firestopping, and cutover sequence. | Building 78/78A is a very large full-scope TR building with basement through fourth-level telecom rooms, existing telecom rooms, hazardous abatement, architectural, fire protection, mechanical, electrical, security, telecom, rack elevations and photo references. Major open issues include active service cutover, dedicated HVAC validation, panel/UPS/PDU coordination, 4,849 ft cable tray routes, firestopping, PACS/CCTV, existing rack transfers, and turnover testing. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 132 | 141 | 153 | 162 | 170
80 | B80_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify Telecom Room 102 and existing 127A/126; confirm active services, existing rack/equipment transfer, B80-TR102A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, cable tray route, and telecom cutover sequence. | Building 80 includes a new first-level Telecom Room 102 and existing Tel Closet 127A / photo-reference Room 126 transition point. Field verification, active equipment transfer, dedicated cooling IU-1-01/CU-1-01, B80-TR102A/B power, 811 ft cable tray, firestopping, PACS/CCTV, existing two-post rack migration, and room-number mapping remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 91 | 100 | 112 | 121 | 129
82 | B82_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Excluded / Verify Existing | Field verify Room 102 new TE location, existing B01-A, active services, TR01-102-01 schedule, 278 ft cable tray route, 10 Cat6A cable legend, UPS/PDU source, B82-MDP/B82-P-EMER connections, IU-1-01/CU-1-01 cooling, fiber paths A/B, firestopping/sleeves, existing cameras and TE cutover plan. | Building 82 is identified as a Telecom Enclosure (TE) building on the cover sheet, with fire protection scope excluded, but mechanical sheets show IU-1-01/CU-1-01 dedicated cooling for Room 102 and electrical drawings show B82-MDP/B82-P-EMER power. Scope centers on new first-level Telecom Room 102 / 12RU enclosure and existing first-level Telecom Room B01-A transition point. Field verification, active-equipment transfer, 278 ft cable tray, firestopping, UPS/PDU power, HVAC controls, fiber/copper cutover, and room/equipment mapping remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 91 | 100 | 112 | 121 | 129
BCH | BCH_Assessment | Yellow | 50% | 50% | No | 26 | 0 | 0 | 0 | Verify | Verify | Verify | Excluded / Firestop Only | Verify Existing | Verify Existing | Field verify Room 107, Room 00-107 rack/elevation reference, new TE/enclosure location, active services, cable tray route, power/UPS/PDU source, grounding/bonding, fiber Path A/B, 4-inch sleeve/firestop scope, camera/VMS scope, and confirm whether the BCH rack elevation is TE-only or new telecom room buildout. | Crescent House/BCH is a Telecom Enclosure (TE) scope with mechanical and fire protection excluded by the cover sheet. Scope centers on first-level Room 107 and rack/equipment location shown as Room 00-107 / BCH Crescent House. Field verification, room naming, wall-mounted TE versus 45RU room/rack elevation conflict, active-service cutover, power/UPS/PDU source, firestopping, fiber A/B routing, and cable tray/WAO quantities remain open. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 92 | 101 | 113 | 122 | 130
MCR | MCR_Assessment | Yellow | 50% | 50% | No | 31 | 0 | 0 | 0 | Verify | Verify | Verify | Verify | Verify | Verify | Field verify new MCR Room 107 / Room 031 naming, MDA-A/B and HDA-A/B rack rows, existing MCR/server equipment in 107/137, UPS-A/B, CRAC units, clean-agent/preaction/fire alarm systems, MCR panel/ATS/generator sources, camera/access control devices, fiber Path A/B, service provider entrance, cable tray/firestop scope, third-party inspections, and phased activation/cutover sequence. | MCR is the most critical EHRM infrastructure building. Scope includes new Main Computer Room, new MDA A/B rows, HDA A/B rows, existing server/MCR equipment transfer from 107/137, redundant fiber Path A/B, new CRAC cooling, UPS A/B, electrical service/ATS/generator integration, clean-agent fire suppression, wet sprinkler/fire alarm interfaces, PACS/CCTV, 359 ft cable tray, and MCR activation window. Major risk is service continuity during backbone/core migration and VA activation. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 118 | 127 | 139 | 148 | 156
SITE | SITE_Assesment | Yellow | 50% | 50% | No | 32 | 0 | 0 | 0 | N/A | Verify | Verify | N/A / Maintain Access | N/A | Verify Site Access | Field verify all THH/manhole locations, utility depths, trench routes, concrete ductbank sizes, Path A/B conduit counts, building tie-in points, site electrical conflicts, MCR/provider entrance points, restoration limits, traffic/pedestrian controls, inspection hold points, and fiber testing/acceptance sequence. | Site package controls the redundant telecommunications backbone for the full EHRM campus. Scope includes site survey, electrical site plans, telecom site plans, enlarged views, plan/profile sheets for Path A/B, concrete ductbank, direct-bury conduit, handholes THH #1-#19, communication manholes with locking covers, concrete pullboxes, trench restoration, and the site one-line fiber diagram. Major risks are existing utility conflicts, A/B path separation, ductbank inspection before backfill, MCR activation sequencing, and coordination of multiple building tie-ins. | 0 | 0 | 0 | Monitor | Review | 0 | Mapped | 0% | Withhold / Review | 0% | Blocked | No blocker documented | 50% | Deficiency / Review | 0% | Critical / Document | 0% | Not Ready | 0% | 6 | Resolve OIT Blocker | 🔴 ATTENTION | 10% | 116 | 125 | 137 | 146 | 154
33 | B33_Assessment | B33-R8 | B17 / Other Bldgs | Existing B17 cross-building service relationships may create cutover dependency | High | Medium | 6 | Verify ports to Bldgs 3, 80 and 82, SERTEX utility service, labels, test records, service provider dependency and OIT approval | Telecom / OIT | Closed | Existing B17 elevation identifies ports 1-72 to Bldg 3, 73-96 to Bldg 80, 97-120 to Bldg 82, and 121-144 to Bldg 3.
61 | B33_Assessment | B61-R1 | All | Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | Large multi-room scope with active demarc/server equipment.
61 | B33_Assessment | B61-R2 | B13H-A / 124 / 226 | Hazardous material abatement plans exist for first and second levels | High | Medium | 6 | Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation | GC / IH / COR | Closed | Drawing index includes 61H-101 and 61H-102 hazardous material abatement plans.
61 | B33_Assessment | B61-R3 | 137 / 137A | Existing server/demarc equipment may remain active during cutover | Critical | Medium | 8 | Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path | OIT / Telecom | Closed | Existing APC/Fujitsu/rack/patch equipment shown in Room 137 inventory/rack elevations.
61 | B33_Assessment | B61-R4 | All TRs | Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR/server readiness.
61 | B33_Assessment | B61-R5 | All TRs | Panel source, UPS/PDU and rack receptacle coordination could delay energization | Critical | Medium | 8 | Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements | Electrical / GCC | Closed | Multiple telecom panelboards and PD panels shown.
61 | B61_Assessment | B61-R6 | All | Large cable tray scope creates coordination and firestop risk | High | Medium | 6 | Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 890 ft, first 499 ft, second 578 ft.
61 | B61_Assessment | B61-R7 | All | Telecom/fiber cutover could affect active hospital communications and server/demarc services | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | WAO counts and active ports are substantial across B13H-A, 124 and 226.
61 | B61_Assessment | B61-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope building with multiple divisions.
62 | B62_TR_Assessment | B62-R1 | All | Cooling redundancy / emergency power not verified | High | Medium | 6 | Confirm power path for cooling, controls, condensate pump | GCC / VA | Closed | 0
62 | B62_TR_Assessment | B62-R2 | All | Firestopping condition unknown | High | Medium | 6 | Survey penetrations and temporary/permanent firestop plan | GCC | Closed | 0
62 | B62_TR_Assessment | B62-R3 | All | Existing room conditions undocumented | Medium | High | 6 | Create photo record before construction begins | GCC | Closed | 0
62 | B62_TR_Assessment | B62-R4 | All | Condensate leak risk near IT equipment | High | Medium | 6 | Verify condensate routing and alarms | GCC / Contractor | Closed | 0
70 | B70_TR_Assessment | B70-R1 | All | Cooling emergency power / continuity not verified | High | Medium | 6 | Confirm power path for cooling, controls, BACnet adapter, and condensate pump | GCC / VA | Closed | 0
70 | B70_TR_Assessment | B70-R2 | All | 1-hour rated/smoke-rated TR envelope and penetrations not field verified | High | Medium | 6 | Survey walls, doors, sleeves, trays, firestop, and head-of-wall conditions | GCC | Closed | 0
70 | B70_TR_Assessment | B70-R3 | B27 | Existing basement service conditions may constrain routing and access | Medium | High | 6 | Document existing utilities, clearances, and phasing around active systems | GCC | Closed | 0
70 | B70_TR_Assessment | B70-R4 | All | Existing TR/service equipment transfer could affect active operations | High | Medium | 6 | Require phasing plan and maintain analog/low-voltage systems operational | GCC / Contractor | Closed | 0
70 | B70_TR_Assessment | B70-R5 | All | Condensate leak risk near IT equipment | High | Medium | 6 | Verify condensate routing, insulation, pump power, and alarms | GCC / Contractor | Closed | 0
78 | B70_TR_Assessment | B78-R1 | All | Existing conditions and active equipment across six TRs and existing telecom rooms not field verified | High | Medium | 6 | Perform detailed room-by-room existing condition survey with photos and active-service inventory | GCC / Contractor | Closed | B78/78A has six major TR areas and several existing transition rooms.
78 | B70_TR_Assessment | B78-R2 | Basement / Third | Hazardous material abatement plans exist for basement and third level | High | Medium | 6 | Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or MEP installation | GC / IH / COR | Closed | Drawing index includes 78_78AH-100 and 78_78AH-103.
78 | B70_TR_Assessment | B78-R3 | Existing rooms | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, OIT windows, rack inventory, temporary utilities and rollback plan | Telecom / OIT | Closed | Photo references include 15E, 1234, 353, 308A, 408A.
78 | B70_TR_Assessment | B78-R4 | All TRs | Dedicated cooling sequence, emergency power, condensate and alarms not verified | Critical | Medium | 8 | Confirm HVAC equipment serving each TR, emergency source, condensate, controls/BACnet and high-temp alarms | Mechanical / Electrical | Closed | Mechanical sheets are included for basement through fourth level.
78 | B70_TR_Assessment | B78-R5 | All TRs | Panel source, UPS/PDU and rack receptacle coordination could delay energization | Critical | Medium | 8 | Verify telecom panelboards, breakers, rack receptacles, UPS/PDU sources, SPDs, labels and LOTO requirements | Electrical / GCC | Closed | Electrical plans/schedules are extensive; confirm all panel IDs in field.
78 | B78_Assessment | B78-R6 | All | Large cable tray scope creates coordination and firestop risk | High | Medium | 6 | Verify 4,849 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 1,702 ft, first 959 ft, second 804 ft, third 695 ft, fourth 689 ft.
78 | B78_Assessment | B78-R7 | All | Telecom/fiber cutover could affect active hospital communications across B78 and B78A | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | Total scheduled ports exceed 1,300 across the primary schedules.
78 | B78_Assessment | B78-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope 102-sheet IFC package with multiple divisions.
80 | B78_Assessment | B80-R1 | All | Existing conditions for Room 102 and existing 127A/126 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B80 includes new TR plus existing telecom transition point.
80 | B78_Assessment | B80-R2 | 127A / 126 | Existing telecom equipment may remain active during transfer to Room 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing and rollback plan | Telecom / OIT | Closed | Existing rack elevation shows Cisco switches, legacy patch panels, Fiber LIU and APC floor UPS.
80 | B78_Assessment | B80-R3 | 102 / 127A | Room-number mismatch between Tel Closet 127A and photo/rack reference Room 126/127-A | High | Medium | 6 | Track both IDs in PMIS and confirm field room signage/owner mapping before punch list and turnover | GCC / VA / Designer | Closed | 80T-101 calls Tel Closet 127A; 80R-900 photo reference calls existing telecom room 126; 80T-604 lists room 126/127-A.
80 | B78_Assessment | B80-R4 | 102 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
80 | B78_Assessment | B80-R5 | 102 | B80-TR102A/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panel sources BUS-B80-MDP and BUS-B80-E1, breakers, receptacles, SPD, labels, load measurement and LOTO needs | Electrical / GCC | Closed | B80-TR102A/B panel schedules and one-line show normal/emergency source split.
80 | B80_Assessment | B80-R6 | All | 811 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | 80T-701 cable tray schedule: basement 122 ft, first level 688 ft, grand total 811 ft.
80 | B80_Assessment | B80-R7 | All | Telecom/fiber cutover could affect active hospital communications on first-level operations | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | RM102 supports 215 total ports including allowance and existing rack transfer.
80 | B80_Assessment | B80-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope 52-sheet IFC package with mechanical, electrical, FP and telecom work.
82 | B80_Assessment | B82-R1 | All | Existing conditions for new Room 102 TE and existing B01-A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B82 has a compact TE scope but still depends on field conditions and existing equipment transfer.
82 | B80_Assessment | B82-R2 | 102 / B01-A | Existing equipment in B01-A may remain active during transfer to new TE in 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 82T-101 keynotes require phasing plan and transfer of existing devices to new rack/enclosure.
82 | B80_Assessment | B82-R3 | 102 | Cover sheet says TE, but mechanical cooling is included for Room 102 | High | Medium | 6 | Confirm scope interpretation with VA/AE and ensure cooling is commissioned if it serves active TE equipment | GCC / VA / Designer | Closed | Unlike some TE buildings, B82 includes IU-1-01/CU-1-01 mechanical/electrical scope.
82 | B80_Assessment | B82-R4 | 102 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling appears included and must be verified before acceptance.
82 | B80_Assessment | B82-R5 | 102 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding, SPD and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs.
82 | B82_Assessment | B82-R6 | All | 278 feet of first-level cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | 82T-701 cable tray schedule lists first level estimated length of 278 ft.
82 | B82_Assessment | B82-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | Cover excludes fire protection; telecom notes require fire caulk and rated penetrations.
82 | B82_Assessment | B82-R8 | All | Commissioning/test documentation may be overlooked due to TE-only scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification, HVAC startup/controls and owner signoff | GC / Cx Manager | Closed | General notes still require testing, acceptance and documentation.
BCH | B82_Assessment | BCH-R1 | All | Existing conditions for Crescent House Room 107 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | BCH is off-site at 15 Veterans Way, Lowell and requires careful field verification.
BCH | B82_Assessment | BCH-R2 | 107 | Mechanical and fire protection are excluded despite telecom/electronics installation | High | Medium | 6 | Verify existing environmental and life-safety conditions support TE equipment; confirm no dedicated HVAC/FP requirement applies | GCC / VA / AE | Closed | Cover sheet explicitly excludes mechanical and fire protection.
BCH | B82_Assessment | BCH-R3 | 107 / 00 | Rack/elevation conflict: TE 12RU enclosure versus BCH Room 107 new telecom room elevation | High | Medium | 6 | Submit RFI/confirm with AE which elevation governs and map room/equipment in PMIS | Telecom / Designer | Closed | BCHT-604 includes both TE enclosure and BCH 45RU new telecom room/no existing elevations.
BCH | B82_Assessment | BCH-R4 | 107 | Active services and existing devices may require phasing/temporary service | Critical | Medium | 8 | Document active services, maintain existing service, use phasing plan, temporary utilities and OIT cutover windows | Telecom / OIT | Closed | General telecom notes require transfer/phasing and avoiding shutdowns.
BCH | B82_Assessment | BCH-R5 | 107 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | Electrical sheets included but no full mechanical/FP package.
BCH | BCH_Assessment | BCH-R6 | All | Cable tray, sleeve and pathway quantities not scheduled in a BCHT-701 sheet | High | Medium | 6 | Require coordination drawings showing route, supports, fill, penetrations, sleeves and cable counts | Telecom / GC | Closed | Drawing index does not list BCHT-701 telecom schedules.
BCH | BCH_Assessment | BCH-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch sleeves, rated penetrations, fire caulk, temporary firestopping and patching even without FP scope | GC / Firestop | Closed | Telecom plan notes still require fire caulk and rated penetration protection.
BCH | BCH_Assessment | BCH-R8 | All | Turnover documentation may be incomplete due to TE-only/off-site scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification and owner signoff | GC / Cx Manager | Closed | Commissioning/testing requirements still apply to impacted systems.
MCR | BCH_Assessment | MCR-R1 | All | MCR is a new standalone critical facility with 120-sheet multi-discipline scope | Critical | Medium | 8 | Use discipline-by-discipline pre-install checklist, coordination drawings, third-party inspections and commissioning tracker | GCC / VA / Cx | Closed | New MCR cannot depend on another project or funding source to be usable.
MCR | BCH_Assessment | MCR-R2 | Existing 107/137 | Existing MCR/server/core equipment transfer may interrupt hospital network operations | Critical | Medium | 8 | Require detailed OIT cutover plan, temporary fiber/umbilicals, rollback plan, VA activation windows and after-hours phasing | OIT / Telecom | Closed | Notes state MCR activation may need 3-6 months and WAO activation depends on fiber/core connections.
MCR | BCH_Assessment | MCR-R3 | MDA/HDA | A/B fiber path diversity and backbone commissioning not verified | Critical | Medium | 8 | Verify OSP/ISP Path A/B routing, no intermediate splices, test results, labeling and geographic diversity | Telecom / OIT | Closed | New fiber risers require A-side and B-side redundant paths to every TR.
MCR | BCH_Assessment | MCR-R4 | MCR / UPS | UPS-A/B, ATS/generator, panel source and PDU coordination could delay activation | Critical | Medium | 8 | Verify one-line, load banks, breaker settings, panel labels, generator/ATS tests, UPS start-up and A/B power mapping | Electrical / Cx | Closed | Electrical scope includes site electrical, enlarged MCR plans, one-lines and schedules.
MCR | BCH_Assessment | MCR-R5 | MCR | CRAC capacity, redundancy, condensate, BMS/FMS alarms and emergency power not verified | Critical | Medium | 8 | Confirm mechanical schedules, CRAC start-up, controls, alarm points, emergency source, environmental monitoring and hot/cold aisle performance | Mechanical / Cx | Closed | Telecom notes explicitly call for indoor computer room air conditioner CRAC units and BMS coordination.
MCR | MCR_Assessment | MCR-R6 | MCR | Clean-agent/preaction/fire alarm interface and room integrity acceptance risk | Critical | Medium | 8 | Track clean-agent calculations, room integrity test, release/abort stations, FA matrix, sprinkler/preaction tests and AHJ/third-party acceptance | FP / FA / Cx | Closed | MCR receives new fire alarm and clean-agent fire suppression system.
MCR | MCR_Assessment | MCR-R7 | MCR / Site | Civil/site/utility ductbank, drainage, grading and security envelope could affect substantial completion | High | Medium | 6 | Track civil utility plan, stormwater, grading, ductbank, site fiber conduit encasement, access and landscape/hardscape restoration | Civil / Site / GC | Closed | MCR package includes civil, structural and architectural site work.
MCR | MCR_Assessment | MCR-R8 | All | Commissioning/turnover package may be incomplete across all divisions | High | Medium | 6 | Maintain MCR-specific turnover matrix for electrical, mechanical, FP, FA, telecom, security, civil, structural and architectural systems | GC / Cx Manager | Closed | General notes require commissioning/recommissioning, third-party inspections and written reports.
SITE | MCR_Assessment | SITE-R1 | All | Existing utility locations are approximate and field conditions may vary from survey | Critical | High | 9 | Complete utility locate, GPR review, potholing/hand-digging at crossings and VA utility coordination before excavation | GC / Civil / VA | Closed | Multiple sheets repeat that survey conditions may vary and utility location service is required prior to excavation.
SITE | MCR_Assessment | SITE-R2 | All | A/B fiber path separation may not be maintained through common ductbank or congested areas | Critical | Medium | 8 | Verify separate conduits, route diversity, THH labels, T-601 path counts and as-built documentation | Telecom / OIT | Closed | Legend allows A+B in common ductbank but separate conduits; redundancy must be validated.
SITE | MCR_Assessment | SITE-R3 | All | Concrete ductbank could be backfilled before inspection | High | Medium | 6 | Establish inspection hold point; trench remains open until concrete duct inspection and photos are accepted | GC / QA / COR | Closed | Site notes state trench to remain open until inspection of concrete duct.
SITE | MCR_Assessment | SITE-R4 | MCR / Provider | WAN/provider fiber and MCR activation sequence could delay campus cutover | Critical | Medium | 8 | Coordinate Century Link/service provider, temporary fiber, provider extension, MCR readiness and OIT activation plan | OIT / Telecom | Closed | T-601 references WAN fiber, temporary fiber and provider extension.
SITE | MCR_Assessment | SITE-R5 | Roads / Parking / Pedestrian Areas | Trenching/restoration may disrupt accessible parking, fire lanes, public access and campus traffic | High | Medium | 6 | Submit traffic/pedestrian/staging plan, maintain fire lanes/hydrants and restore surfaces to match existing | GC / Site | Closed | General notes require coordination with owner and protection of accessible parking/public access.
SITE | SITE_Assesment | SITE-R6 | All Building Tie-ins | Building entry penetrations/firestopping may not align with building PMIS packages | High | Medium | 6 | Cross-check every site tie-in against building assessment, T-101 continuation sheets and firestop photos | Telecom / Firestop / QA | Closed | Every building continuation references building T-101 and T-601.
SITE | SITE_Assesment | SITE-R7 | Civil Restoration | Asphalt/concrete/landscape restoration quantities and limits may be underestimated | Medium | Medium | 4 | Verify trench patch details, tie bars, concrete/asphalt specs, landscape protection and final surface restoration photo log | GC / Civil | Closed | T-501 includes trenching/restoration details and concrete requirements.
SITE | SITE_Assesment | SITE-R8 | Commissioning / Turnover | Fiber testing, labels, as-builts and site utility commissioning may be incomplete | High | Medium | 6 | Track OTDR/power meter tests, conduit as-builts, THH labels, route photos, redlines, third-party inspections and VA/OIT acceptance | GC / Cx / OIT | Closed | Commissioning and third-party inspection requirements apply to site utilities and communications.
B01_Assessment
MAPPED OPEN QUESTIONS — FORMULA-FED FROM BUILDING SHEETS | B01_Assessment
Building | B01_Assessment | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
01 | B01_Assessment | B01-Q1 | Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
01 | B01_Assessment | B01-Q2 | What active services are currently fed from existing Rooms B02, 138 and 282? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
01 | B01_Assessment | B01-Q3 | What equipment from existing racks transfers to new Room 107 versus remains/decommissions? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0
01 | B01_Assessment | B01-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
01 | B01_Assessment | B01-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
01 | B01_Assessment | B01-Q6 | Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
01 | B01_Assessment | B01-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
01 | B01_Assessment | B01-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
02 | B01_Assessment | B02-Q1 | Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
02 | B01_Assessment | B02-Q2 | What active services are currently fed from existing Rooms B-06, 141 and 236? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
02 | B01_Assessment | B02-Q3 | What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0
02 | B01_Assessment | B02-Q4 | Which IU/CU pair serves each TR and are they on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
02 | B01_Assessment | B02-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
02 | B02_Assessment | B02-Q6 | Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
02 | B02_Assessment | B02-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
02 | B02_Assessment | B02-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
03 | B02_Assessment | B03-Q1 | Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
03 | B02_Assessment | B03-Q2 | What active services are currently fed from existing Room 107 and DMARC Room 101C? | OIT / Contractor / Provider | Closed | 0 | 0 | Potential communications/provider outage | 0 | 0 | 0
03 | B02_Assessment | B03-Q3 | What existing equipment transfers to new Room 101E versus remains/decommissions? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0
03 | B02_Assessment | B03-Q4 | Which IU/CU pair serves Room 101E and is it on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
03 | B02_Assessment | B03-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
03 | B03_Assessment | B03-Q6 | Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
03 | B03_Assessment | B03-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
03 | B03_Assessment | B03-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
04 | B03_Assessment | B04-Q1 | Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? | VA / OIT / Designer | Closed | 0 | 0 | Incomplete room inventory / missed scope | 0 | 0 | 0
04 | B03_Assessment | B04-Q2 | Are B05, 141, and 244A cooling systems on emergency/backup power? | VA / Electrical / Mechanical | Closed | 0 | 0 | Cooling continuity not confirmed | 0 | 0 | 0
04 | B03_Assessment | B04-Q3 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
04 | B03_Assessment | B04-Q4 | What is the approved migration and cutover sequence for active Building 04 services? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
04 | B03_Assessment | B04-Q5 | Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? | GC / COR | Closed | 0 | 0 | Work stoppage or exposure risk | 0 | 0 | 0
04 | B04_Assessment | B04-Q6 | Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? | Electrical / Designer | Closed | 0 | 0 | Electrical delay or overload risk | 0 | 0 | 0
04 | B04_Assessment | B04-Q7 | Are all rated wall/floor penetrations and speed sleeves identified and firestopped? | GC / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
04 | B04_Assessment | B04-Q8 | Which third-party tests, commissioning forms, and acceptance documents are required before VA turnover? | GC / Cx Manager | Closed | 0 | 0 | Incomplete turnover package | 0 | 0 | 0
05 | B04_Assessment | B05-Q1 | Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could be wrong | 0 | 0 | 0
05 | B04_Assessment | B05-Q2 | What active services are currently fed from the existing 153-A TE/legacy patch panels? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
05 | B04_Assessment | B05-Q3 | What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? | OIT / Contractor | Closed | 0 | 0 | Cutover risk | 0 | 0 | 0
05 | B04_Assessment | B05-Q4 | Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? | Electrical / Designer | Closed | 0 | 0 | Power source cannot be verified | 0 | 0 | 0
05 | B05_Assessment | B05-Q5 | Is emergency/backup power required or provided for the TE UPS/PDU source? | VA / Electrical | Closed | 0 | 0 | Continuity requirement unclear | 0 | 0 | 0
05 | B05_Assessment | B05-Q6 | Are firestopping locations and surface raceway/conduit routes shown and coordinated? | GC / Designer | Closed | 0 | 0 | Rated assembly/firestop risk | 0 | 0 | 0
05 | B05_Assessment | B05-Q7 | Does Room 150 or existing Room 153-A require PACS/CCTV modifications, or is existing security adequate? | Security / VA | Closed | 0 | 0 | Security acceptance risk | 0 | 0 | 0
06 | B05_Assessment | B06-Q1 | Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
06 | B05_Assessment | B06-Q2 | What active services are fed from existing B-01 and Room 178 legacy equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
06 | B05_Assessment | B06-Q3 | What is the approved cutover sequence for B-01, 178 and 233? | OIT / Contractor | Closed | 0 | 0 | Cutover risk | 0 | 0 | 0
06 | B05_Assessment | B06-Q4 | Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
06 | B05_Assessment | B06-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
06 | B06_Assessment | B06-Q6 | Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
06 | B06_Assessment | B06-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
06 | B06_Assessment | B06-Q8 | Which commissioning/third-party tests must be complete before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
07 | B06_Assessment | B07-Q1 | Confirm final TR scope: B-18 basement and 228A second floor only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
07 | B06_Assessment | B07-Q2 | Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? | Mechanical / Designer | Closed | 0 | 0 | Cooling scope unclear | 0 | 0 | 0
07 | B06_Assessment | B07-Q3 | Are cooling units and controls on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity not confirmed | 0 | 0 | 0
07 | B06_Assessment | B07-Q4 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
07 | B06_Assessment | B07-Q5 | What active services are currently fed from B-18 and/or existing pathways serving 228A? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
07 | B07_Assessment | B07-Q6 | Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
07 | B07_Assessment | B07-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
07 | B07_Assessment | B07-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
08 | B07_Assessment | B08-Q1 | Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory may miss scope | 0 | 0 | 0
08 | B07_Assessment | B08-Q2 | What active services are currently fed from existing B-15 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
08 | B07_Assessment | B08-Q3 | Is B12B truly a TE/equipment location or only a cabling pathway/service area? | VA / Designer / Contractor | Closed | 0 | 0 | Scope ambiguity | 0 | 0 | 0
08 | B07_Assessment | B08-Q4 | Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
08 | B07_Assessment | B08-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
08 | B08_Assessment | B08-Q6 | Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
08 | B08_Assessment | B08-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
08 | B08_Assessment | B08-Q8 | Which hazardous material/abatement steps apply to Level 2 floor penetrations and flooring removal? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
09 | B08_Assessment | B09-Q1 | Confirm final TR scope: B01 basement, 104B first level, and 206A second level? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory may miss scope | 0 | 0 | 0
09 | B08_Assessment | B09-Q2 | What active services are currently fed from B01 existing equipment/security/network devices? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
09 | B08_Assessment | B09-Q3 | What hazardous/abatement steps apply to B01, 104B and 206A work areas? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
09 | B08_Assessment | B09-Q4 | Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
09 | B08_Assessment | B09-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0
09 | B09_Assessment | B09-Q6 | Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
09 | B09_Assessment | B09-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
09 | B09_Assessment | B09-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
10 | B09_Assessment | B10-Q1 | Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
10 | B09_Assessment | B10-Q2 | What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0
10 | B09_Assessment | B10-Q3 | What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? | GC / IH / COR | Closed | 0 | 0 | Work delay/exposure risk | 0 | 0 | 0
10 | B09_Assessment | B10-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
10 | B09_Assessment | B10-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
10 | B10_Assessment | B10-Q6 | Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
10 | B10_Assessment | B10-Q7 | Are all attic wall/floor/ceiling penetrations, sleeves and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
10 | B10_Assessment | B10-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
12 | B10_Assessment | B12-Q1 | Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? | VA / OIT / Designer | Closed | 0 | 0 | Scope misunderstanding | 0 | 0 | 0
12 | B10_Assessment | B12-Q2 | What exact pathway does the Building 12 fiber take through basement, first and second levels? | Telecom Contractor / OIT | Closed | 0 | 0 | Fiber pull and access risk | 0 | 0 | 0
12 | B10_Assessment | B12-Q3 | Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? | OIT / Contractor | Closed | 0 | 0 | Termination and ownership unclear | 0 | 0 | 0
12 | B10_Assessment | B12-Q4 | Are existing conduits/cable trays available and below fill limits for the new fiber? | Telecom Contractor | Closed | 0 | 0 | Pathway capacity risk | 0 | 0 | 0
12 | B12_Assessment | B12-Q5 | Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? | GC / Firestop | Closed | 0 | 0 | Life safety/firestop risk | 0 | 0 | 0
12 | B12_Assessment | B12-Q6 | What is the approved cutover/testing/acceptance sequence for Building 12 fiber? | OIT / COR / Contractor | Closed | 0 | 0 | Possible outage or acceptance delay | 0 | 0 | 0
12 | B12_Assessment | B12-Q7 | Which fiber test reports, labels, route documentation and as-builts are required for closeout? | Telecom / GCC | Closed | 0 | 0 | Closeout documentation gap | 0 | 0 | 0
13 | B12_Assessment | B13-Q1 | Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
13 | B12_Assessment | B13-Q2 | What active services are currently fed from existing Tel Room 222 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
13 | B12_Assessment | B13-Q3 | What hazardous/abatement steps apply to first-level Room 124 work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
13 | B12_Assessment | B13-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
13 | B12_Assessment | B13-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
13 | B13_Assessment | B13-Q6 | Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
13 | B13_Assessment | B13-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
13 | B13_Assessment | B13-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
14 | B13_Assessment | B14-Q1 | Confirm final telecom scope: new Room 119 and existing basement B.01/B2 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
14 | B13_Assessment | B14-Q2 | What active services are currently fed from existing B.01/B2 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
14 | B13_Assessment | B14-Q3 | What hazardous/abatement steps apply to first-level Room 119 work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
14 | B13_Assessment | B14-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 119? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
14 | B13_Assessment | B14-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 119? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
14 | B14_Assessment | B14-Q6 | Are B14-TR119A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
14 | B14_Assessment | B14-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
14 | B14_Assessment | B14-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
15 | B14_Assessment | B15-Q1 | Confirm final telecom scope: new Room 124A and existing Rooms 222/B01 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
15 | B14_Assessment | B15-Q2 | Why does 15T-701 reference RM 109A while plans and electrical schedules identify Telecom Room 124A? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0
15 | B14_Assessment | B15-Q3 | What active services are currently fed from existing Room 222 and B01 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
15 | B14_Assessment | B15-Q4 | What hazardous/abatement steps apply to first-level Room 124A work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0
15 | B14_Assessment | B15-Q5 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124A? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
15 | B15_Assessment | B15-Q6 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124A? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
15 | B15_Assessment | B15-Q7 | Are B15-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
15 | B15_Assessment | B15-Q8 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
16 | B15_Assessment | B16-Q1 | Confirm final telecom scope: new Room 015 and existing Room 014 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
16 | B15_Assessment | B16-Q2 | What active services are currently fed from existing Room 014 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
16 | B15_Assessment | B16-Q3 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 015? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
16 | B15_Assessment | B16-Q4 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 015? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
16 | B15_Assessment | B16-Q5 | Are B16-TR015A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
16 | B16_Assessment | B16-Q6 | Which existing panel/circuit breaker/feeder demolition and replacement affects Room 015 telecom power? | Electrical / GCC | Closed | 0 | 0 | Panel outage/cutover risk | 0 | 0 | 0
16 | B16_Assessment | B16-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
16 | B16_Assessment | B16-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
17 | B16_Assessment | B17-Q1 | Confirm final telecom scope: new Room 118, existing B35A, and Building 29 served from B17? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
17 | B16_Assessment | B17-Q2 | What active services are currently fed from existing B35A equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
17 | B16_Assessment | B17-Q3 | What exact Building 29 outlets/devices are served through TR17-118-1? | VA / OIT / Designer | Closed | 0 | 0 | Building 29 scope boundary unclear | 0 | 0 | 0
17 | B16_Assessment | B17-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 118? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
17 | B16_Assessment | B17-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 118? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
17 | B17_Assessment | B17-Q6 | Are B17-TR118A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
17 | B17_Assessment | B17-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
17 | B17_Assessment | B17-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
18 | B17_Assessment | B18-Q1 | Confirm final telecom scope: new Room 110 with existing 111B and 213 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
18 | B17_Assessment | B18-Q2 | Why does 18T-701 reference RM 111A while new rack/electrical plans identify Telecom Room 110? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0
18 | B17_Assessment | B18-Q3 | What active services are currently fed from existing 111B and 213 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
18 | B17_Assessment | B18-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 110? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
18 | B17_Assessment | B18-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 110? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
18 | B18_Assessment | B18-Q6 | Are B18-TR110A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
18 | B18_Assessment | B18-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
18 | B18_Assessment | B18-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
20 | B18_Assessment | B20-Q1 | Confirm final scope: new wall-mount TE enclosure in Office 1B and existing Tel/Data Closet 8A transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
20 | B18_Assessment | B20-Q2 | What active services are currently fed from existing 8A open TE cabinet and related equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
20 | B18_Assessment | B20-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Office 1B? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
20 | B18_Assessment | B20-Q4 | Is Office 1B HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0
20 | B18_Assessment | B20-Q5 | Are existing cameras/security devices in Building 20 protected and retained with no VMS/PACS changes? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
20 | B20_Assessment | B20-Q6 | Are all 459 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
20 | B20_Assessment | B20-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0
20 | B20_Assessment | B20-Q8 | Which test records and turnover documents are required for TE-only acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
21 | B20_Assessment | B21-Q1 | Confirm final scope: new TE enclosure at Room 100A/RM 104 and existing B21 B1.TR plus B19 B05TR transition? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
21 | B20_Assessment | B21-Q2 | Why does 21_19T-701 list RM 104 / TR01-104-1 while enlarged plan identifies Room 100A? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0
21 | B20_Assessment | B21-Q3 | What active services are currently fed from existing B21 B1.TR and B19 B05TR equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
21 | B20_Assessment | B21-Q4 | What exactly is meant by '19 serving 21' on the new TE enclosure elevation? | VA / OIT / Designer | Closed | 0 | 0 | Building 19/21 boundary unclear | 0 | 0 | 0
21 | B20_Assessment | B21-Q5 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in 100A? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
21 | B21_Assessment | B21-Q6 | Are all 659 ft of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
21 | B21_Assessment | B21-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0
21 | B21_Assessment | B21-Q8 | Which test records and turnover documents are required for TE-only acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
22 | B21_Assessment | B22-Q1 | Confirm final scope: new wall-mount TE enclosure in Break Room 102 and existing Room 103 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
22 | B21_Assessment | B22-Q2 | What active services are currently fed from existing Room 103 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
22 | B21_Assessment | B22-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
22 | B21_Assessment | B22-Q4 | Is Break Room 102 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0
22 | B21_Assessment | B22-Q5 | Are existing cameras/security devices in Building 22 protected and retained with no VMS/PACS changes? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
22 | B22_Assessment | B22-Q6 | Are all 139 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
22 | B22_Assessment | B22-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0
22 | B22_Assessment | B22-Q8 | What is the operational impact of Room 103 ports 1-24 to Building 19 ports 73-96? | VA / OIT / Designer | Closed | 0 | 0 | B19 dependency/cutover risk | 0 | 0 | 0
33 | B22_Assessment | B33-Q1 | Confirm final scope: new wall-mount TE enclosure in B23 and existing B17 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
33 | B22_Assessment | B33-Q2 | What active services are currently fed from existing B17 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
33 | B22_Assessment | B33-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in B23? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
33 | B22_Assessment | B33-Q4 | Is Office B23 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0
33 | B22_Assessment | B33-Q5 | Are existing cameras/security devices in Building 33 protected and retained with no VMS/PACS disruption? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
33 | B33_Assessment | B33-Q6 | Are all 102 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
33 | B33_Assessment | B33-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0
33 | B33_Assessment | B33-Q8 | What is the operational impact of B17 ports serving Buildings 3, 80 and 82? | VA / OIT / Designer | Closed | 0 | 0 | Cross-building dependency/cutover risk | 0 | 0 | 0
61 | B33_Assessment | B61-Q1 | Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
61 | B33_Assessment | B61-Q2 | What active services and circuits are currently housed in Room 137/137A? | OIT / Contractor | Closed | 0 | 0 | Potential outage/cutover risk | 0 | 0 | 0
61 | B33_Assessment | B61-Q3 | Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? | Electrical / Designer | Closed | 0 | 0 | Electrical PMIS mapping risk | 0 | 0 | 0
61 | B33_Assessment | B61-Q4 | Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
61 | B33_Assessment | B61-Q5 | Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
61 | B61_Assessment | B61-Q6 | Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
61 | B61_Assessment | B61-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and temporary firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
61 | B61_Assessment | B61-Q8 | Which third-party inspections, commissioning forms and OIT acceptance records are required before turnover? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
62 | B62_TR_Assessment | B62-Q1 | Are cooling units emergency powered? | VA / Designer | Closed | 0 | 0 | Cannot confirm continuity of operations | 0 | 0 | 0
62 | B62_TR_Assessment | B62-Q2 | Are future rack loads included in HVAC sizing? | Designer | Closed | 0 | 0 | Cooling may be undersized after expansion | 0 | 0 | 0
62 | B62_TR_Assessment | B62-Q3 | Is extinguisher location identified within 75 feet? | Contractor / COR | Closed | 0 | 0 | Life safety / acceptance risk | 0 | 0 | 0
62 | B62_TR_Assessment | B62-Q4 | Are all penetrations fully documented and firestopped? | Contractor / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q1 | Are cooling units and controls on emergency/backup power? | VA / Designer | Closed | 0 | 0 | Cannot confirm continuity of operations | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q2 | Are future rack loads included in HVAC sizing for B27, 125A, and 262A? | Designer | Closed | 0 | 0 | Cooling may be undersized after expansion | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q3 | Are extinguisher cabinet locations identified within 75 feet of each TR? | Contractor / COR | Closed | 0 | 0 | Acceptance / life safety risk | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q4 | Are all wall/floor penetrations and speed sleeves shown and firestopped? | Contractor / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
70 | B70_TR_Assessment | B70-Q5 | What phasing is required to keep existing low-voltage/analog systems operational? | Contractor / OIT | Closed | 0 | 0 | Potential communications interruption | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q1 | Confirm final telecom room list and PMIS mapping: B30, B35, 1232, 227A, 342, 401 plus existing rooms 15E/1234/353/308A/408A? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q2 | What active services currently remain in each existing telecom room/photo reference location? | OIT / Contractor | Closed | 0 | 0 | Potential outage/cutover risk | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q3 | Are Room 1232 and existing Room 1234 separate rooms or naming/mapping references for the same telecom space? | VA / Designer / OIT | Closed | 0 | 0 | PMIS mapping risk | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q4 | Which dedicated cooling units serve each TR and are they on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
78 | B70_TR_Assessment | B78-Q5 | Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
78 | B78_Assessment | B78-Q6 | Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
78 | B78_Assessment | B78-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and temporary firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
78 | B78_Assessment | B78-Q8 | Which third-party inspections, commissioning forms and OIT acceptance records are required before turnover? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
80 | B78_Assessment | B80-Q1 | Confirm final telecom scope: new Room 102 with existing 127A/126 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0
80 | B78_Assessment | B80-Q2 | What active services are currently fed from existing Room 127A/126 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
80 | B78_Assessment | B80-Q3 | Are Room 127A and Room 126 the same telecom room, or separate locations? | VA / Designer / OIT | Closed | 0 | 0 | PMIS mapping and turnover risk | 0 | 0 | 0
80 | B78_Assessment | B80-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
80 | B78_Assessment | B80-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 102? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
80 | B80_Assessment | B80-Q6 | Are B80-TR102A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
80 | B80_Assessment | B80-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0
80 | B80_Assessment | B80-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
82 | B80_Assessment | B82-Q1 | Confirm final scope: new 12RU wall-mount TE enclosure in Room 102 and existing B01-A transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0
82 | B80_Assessment | B82-Q2 | What active services are currently fed from existing B01-A equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0
82 | B80_Assessment | B82-Q3 | Is Room 102 officially a TE-only scope or a conditioned telecom room with mechanical support? | VA / AE / COR | Closed | 0 | 0 | Scope and commissioning responsibility unclear | 0 | 0 | 0
82 | B80_Assessment | B82-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0
82 | B80_Assessment | B82-Q5 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
82 | B82_Assessment | B82-Q6 | Are all 278 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
82 | B82_Assessment | B82-Q7 | Are existing cameras/security devices protected and retained with no VMS/PACS disruption? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
82 | B82_Assessment | B82-Q8 | Which test records, HVAC startup records and turnover documents are required for TE acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q1 | Confirm final BCH scope: Room 107 TE enclosure only, or a new telecom room/rack buildout? | VA / AE / OIT | Closed | 0 | 0 | PMIS scope and acceptance criteria unclear | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q2 | Why does BCHT-604 show a T78 12RU TE enclosure and a separate BCH Crescent House Room 107 new telecom room elevation? | VA / Designer | Closed | 0 | 0 | Rack/equipment mapping conflict | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q3 | What active services currently serve Crescent House and where are existing terminations located? | OIT / Contractor | Closed | 0 | 0 | Cutover/outage risk | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q4 | What is the approved power source, receptacle type and circuit capacity for the new UPS/PDU? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
BCH | B82_Assessment | BCH-Q5 | Is existing HVAC/ambient condition acceptable for TE/network equipment since mechanical scope is excluded? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk | 0 | 0 | 0
BCH | BCH_Assessment | BCH-Q6 | Are cable tray route, sleeve locations, supports and firestopping details shown/field verified without a BCHT-701 schedule? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0
BCH | BCH_Assessment | BCH-Q7 | Are camera/security devices required, protected and integrated into VMS for Room 107? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0
BCH | BCH_Assessment | BCH-Q8 | Which test records and turnover documents are required for BCH TE/off-site acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
MCR | BCH_Assessment | MCR-Q1 | Confirm final room naming and PMIS mapping: MCR Room 107, Fiber Entrance Room 031, Existing 107/137 server/MCR references. | VA / OIT / Designer | Closed | 0 | 0 | Room inventory and turnover mapping could be wrong | 0 | 0 | 0
MCR | BCH_Assessment | MCR-Q2 | What existing core/server/rack equipment is being relocated from the existing MCR/server rooms, and what remains? | OIT / Contractor | Closed | 0 | 0 | Cutover and outage risk | 0 | 0 | 0
MCR | BCH_Assessment | MCR-Q3 | What is the approved MCR activation sequence and required VA/OIT hold points? | VA / OIT / COR | Closed | 0 | 0 | Schedule/cutover impact | 0 | 0 | General phasing notes mention 3-6 month MCR activation and split core operation.
MCR | BCH_Assessment | MCR-Q4 | Are UPS-A/B, generator/ATS and emergency power paths commissioned and mapped to each rack/PDU? | Electrical / Cx | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0
MCR | BCH_Assessment | MCR-Q5 | Are CRAC units fully commissioned with BMS/FMS alarms, redundancy and emergency power? | Mechanical / Cx | Closed | 0 | 0 | Cooling continuity risk | 0 | 0 | 0
MCR | MCR_Assessment | MCR-Q6 | Are clean-agent/preaction/fire alarm systems fully designed, tested and accepted? | FP / FA / AHJ | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0
MCR | MCR_Assessment | MCR-Q7 | Are redundant Path A/B fiber routes geographically diverse, tested, labeled and accepted? | Telecom / OIT | Closed | 0 | 0 | Backbone redundancy risk | 0 | 0 | 0
MCR | MCR_Assessment | MCR-Q8 | Which third-party inspections, commissioning reports and OIT validation records are required before turnover/activation? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q1 | Confirm final list of all site fiber buildings and whether Buildings 1-22, 33, 61, 62, 70, 78/78A, 80, 81, 82, Crescent House and MCR are included in one site backbone turnover package. | VA / OIT / Designer | Closed | 0 | 0 | Scope and turnover package mapping unclear | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q2 | Which THH/manhole numbers are new versus existing, and which require locking cover replacement only? | Telecom / Civil | Closed | 0 | 0 | Structure inventory and inspection scope unclear | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q3 | Are all A and B routes physically diverse enough and in separate conduit wherever common ductbank is used? | OIT / Designer | Closed | 0 | 0 | Redundancy risk | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q4 | What are the approved utility-locate/potholing requirements before excavation at each crossing? | GC / VA / Civil | Closed | 0 | 0 | Utility strike risk | 0 | 0 | 0
SITE | MCR_Assessment | SITE-Q5 | What inspection hold points are required for ductbank forms, conduit placement, concrete pour, pull string, mandrel and backfill? | QA / COR / Civil | Closed | 0 | 0 | QA acceptance risk | 0 | 0 | 0
SITE | SITE_Assesment | SITE-Q6 | Are directional boring alternatives allowed anywhere, or is all base-bid work trenching unless separately approved by Government? | VA / COR | Closed | 0 | 0 | Means/methods and cost/schedule risk | 0 | 0 | 0
SITE | SITE_Assesment | SITE-Q7 | What exact fiber test package is required for each path and building tie-in before connection to active operations? | OIT / Telecom / Cx | Closed | 0 | 0 | Acceptance/activation risk | 0 | 0 | 0
SITE | SITE_Assesment | SITE-Q8 | How will MCR/provider temporary fiber, new fiber and campus building activation be sequenced to limit shutdowns to one at a time? | OIT / GC / COR | Closed | 0 | 0 | Operational outage risk | 0 | 0 | 0
MAPPED ROOMS / TELECOM SPACES — FORMULA-FED FROM BUILDING SHEETS
Building | Sheet | Source Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
01 | B01_Assessment | 01 | 107 | First | New Telecom Room build area | Telecom Room | 1 | 1 | Verify | 01A-401 / 01E-101 / 01E-601 / 01E-701 / 01T-101 / 01T-604 / 01T-605 / 01T-701 | Primary Building 01 TR. Plans identify Room 107 as new TR with Rack ID TR01-107-1, one new 4-post rack plus future rack, 5kW UPS, future/zone PDU, network switches, 48-port Cat6A patch panels, 24-port Cat5e patch panel, Fiber LIU, panels B01-TR107A/B, IU-1-01/CU-1-01 cooling, camera 107-CAM-1, and 161 total ports with 10% allowance.
01 | B01_Assessment | 01 | B02 | Basement | Existing telecom room / racks | Existing telecom transition point | 3 | 0 | Verify | 01T-100 / 01T-604 / 01R-900 | Existing Basement Telecom Room B02 with two 2-post floor racks and one wall TE. Existing equipment includes open rack, UPS on floor, Tripp Lite Smart Pro UPS, Tera Max/Nokia/Baseband/IRU equipment, Corning LANscape, Cisco, and Ortronics 24-port patch panels. Protect active services and transfer devices as required.
01 | B01_Assessment | 01 | 138 | First | Existing telecom room / patch panels | Existing telecom transition point | 3 | 0 | Verify | 01T-101 / 01T-604 / 01R-900 | Existing First-Level Telecom Room 138 with existing patch panels, APC UPS floor, Cisco, Corning LANscape and Ortronics 24/48-port patch panels. Protect active services and verify migration to Room 107.
01 | B01_Assessment | 01 | 282 | Second | Existing telecom room / racks | Existing telecom transition point | 2 | 0 | Verify | 01T-101 / 01T-605 / 01R-900 | Existing Second-Level Telecom Room 282 with two 2-post floor racks, Cisco switches, cable managers, legacy Ortronics 24/48-port patch panels, Corning LANscape and APC 12-port equipment. Protect active services during Room 107 cutover.
02 | B02_Assessment | 02 | 141 | First | Existing first-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-401 / 02E-101 / 02E-401 / 02E-601 / 02E-701 / 02T-101 / 02T-401 / 02T-604 / 02T-701 | Primary first-level TR. Schedules identify RM141 with 211 WAO total, 215 active ports, 322 scheduled ports and 354 total ports with 10% allowance. Rack IDs TR01-141-01/02. Enlarged plan shows Room 141 new and demo scope, 174-CAM-01, existing patch panels/fire alarm cabinet relocated to RM141 and future rack space.
02 | B02_Assessment | 02 | 236 | Second | Existing second-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-401 / 02E-102 / 02E-402 / 02E-701 / 02T-102 / 02T-401 / 02T-604 / 02T-702 | Second-level TR. Schedules identify RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approximately 345 ports with 10% allowance. Rack IDs TR01-236-01/02. Enlarged plans show 236-CAM-01 and new/demolition work at Room 236 / existing Room 282.
02 | B02_Assessment | 02 | 342 | Third | Third-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-402 / 02E-103 / 02E-402 / 02E-701 / 02T-103 / 02T-401 / 02T-604 / 02T-703 | Third-level TR. Schedules identify RM342 with 274 WAO total, 96 active ports, 353 scheduled ports and 388 total ports with 10% allowance. Rack IDs TR01-342-01/02. Enlarged plans show 342-CAM-01, 342A-CK-A and new rack scope.
02 | B02_Assessment | 02 | B-06 | Basement | Existing telecom room / legacy rack equipment | Existing telecom transition point | 1 | 0 | Verify | 02T-100 / 02T-604 / 02R-900 | Existing Basement Telecom Room B-06 with legacy Ortronics 48-port patch panels. Photo reference identifies B-06 existing telecom room. Protect active services and verify transfer/abandonment scope.
02 | B02_Assessment | 02 | Existing 141 / 236 | First / Second | Existing telecom room equipment / transition points | Existing telecom transition points | 4 | 0 | Verify | 02T-604 / 02R-900 | Existing First-Level Telecom Room 141 and Second-Level Existing Telecom Room 236 shown in photo references/rack elevations. Existing devices and racks are to be protected or transferred per notes.
03 | B03_Assessment | 03 | 101E | First | New telecom room buildout / relocated TR function | Telecom Room | 2 | 1 | Verify | 03A-401 / 03E-101 / 03E-401 / 03E-601 / 03E-701 / 03T-101 / 03T-401 / 03T-604 / 03T-701 | Primary Building 03 TR. Schedules identify RM101E with 143 WAO total, 213 active ports, 187 scheduled ports, 206 total ports with 10% allowance, Rack IDs TR01-101E-1 and TR01-101E-2, 5kW UPS, Zone PDU, fiber LIU, Cat6A patch panels, and future rack/switch capacity.
03 | B03_Assessment | 03 | 107 | Basement | Existing telecom room / legacy rack equipment | Existing telecom transition point | 1 | 0 | Verify | 03T-100 / 03T-403 / 03T-604 / 03R-900 | Existing Basement Telecom Room 107. Rack elevation identifies Building 3 existing B3-LB-B13-TC-FIBER rack with UPS on floor, Cisco switch, legacy 48-port patch panels, and fiber LIU wall-mounted. 03T-403 provides Room 107 inventory list for reference.
03 | B03_Assessment | 03 | 101C | First | Existing DMARC / telecom room | Existing DMARC transition point | 1 | 0 | Verify | 03T-101 / 03T-401 / 03T-604 / 03R-900 | First-floor existing DMARC Room 101C / telecom room. Enlarged plan shows existing/removal patch panels, existing branch panel, telecom cabinet, 101C-CAM-01, 101C-CK-A, 101C-A/B/C/D and AP locations. Protect active DMARC/fiber until new service is operational.
03 | B03_Assessment | 03 | 108 / 107A / 101C related WAO areas | First | Work area outlets and WAP/camera locations | WAO recabling / device support | 0 | 0 | Verify | 03T-101 / 03T-701 | WAO schedule includes first-level outlets such as 108-A/B/C, 108-CK-A, 108-AP-A, 107A-AP-A, 101C-CAM-01, 101C-A/B/C/D and AP locations served from TR01-101E-1/2.
04 | B04_Assessment | 04 | B05 | Basement | Existing telecom / service area | TR | 2 | 0 | Verify | 04A-400 / 04T-604 / 04E-701 | Rack elevations show B05 with Rack 1 of 2 and Rack 2 of 2; new B04-TRB05A/B panels and NPA-TR feed shown.
04 | B04_Assessment | 04 | 141 | First | Existing room to be converted / upgraded | TR | 1 | 1 | Verify | 04A-401 / 04T-604 / 04E-701 | Architectural enlarged views identify Room 141; new 45-minute rated door/frame, 1-hour/smoke-rated envelope, open-to-deck TR, and future rack.
04 | B04_Assessment | 04 | 244A | Second | Existing or renovated telecom area | TR | 1 | 1 | Verify | 04T / 04E-701 | Panel schedule identifies B04-TR244A; room requires field verification of rack count, cooling, pathways, fire protection, and PACS/CCTV requirements.
05 | B05_Assessment | 05 | 150 | First | Telecom / equipment location | Telecom Enclosure (TE) | 1 | 0 | Verify | 05T-604 / 05T-401 / 05E-401 | New elevation identifies Room 150 with one 12RU Telecom Enclosure; includes APC UPS, PDUs, cable managers, 48-port patch panels, Cat6A patch panel, and Fiber LIU.
05 | B05_Assessment | 05 | 153-A | First | Existing wall-mounted TE / existing rack area | Existing equipment / transition point | 1 | 0 | Verify | 05T-604 | Existing elevation shows wall or wall-mount TE at Room 153-A with Cisco switches and multiple legacy 24-port patch panels; existing floor UPS shown.
06 | B06_Assessment | 06 | B-01 | Basement | Existing wall/wall-mount TE and floor UPS | Existing equipment / transition point | 1 | 0 | Verify | 06T-604 | Existing basement wall/wall-mount TE with Cisco switches, legacy Ortronics 48-port patch panels, and floor UPS.
06 | B06_Assessment | 06 | 178 | First | Existing telecom room / group therapy area adjacent | Telecom Room | 2 | 0 | Verify | 06A-401 / 06E-401 / 06T-604 / 06E-701 | Room 178 shown as 114 SF Telecom Room; existing 2-post racks and new B06-TR178A/B panel work with IU-1-01 cooling.
06 | B06_Assessment | 06 | 233 | Second | Data closet / patient toilet area conversion | Telecom Room | 1 | 1 | Verify | 06A-402 / 06E-401 / 06T-604 / 06E-701 | Room 233 shown as 119 SF Telecom Room/Data Closet; future rack elevation, B06-TR233A/B panels, and IU-2-01 cooling.
07 | B07_Assessment | 07 | B-18 | Basement | Existing office / telecom-service area | Telecom Room | 1 | 1 | Verify | 07A-400 / 07E-401 / 07T-604 / 07M-701 | Rack elevation shows B-18 as 1 of 1 + future, 4-post floor rack, UPS, future Zone PDU, network switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
07 | B07_Assessment | 07 | 228A | Second | Social worker shared / adjacent OPM storage and DOM MSA area | Telecom Room | 1 | 1 | Verify | 07A-401 / 07E-401 / 07T-604 / 07M-701 | Architectural enlarged view identifies Telecom Room 228A at 236 SF; includes fire-rated door/wall work, FEC requirement, exterior furring wall/window enclosure and temporary dust barrier.
08 | B08_Assessment | 08 | B-15 | Basement | Existing wall/wall-mounted TE and floor UPS | Existing equipment / transition point | 2 | 0 | Verify | 08T-604 | Existing rack elevation identifies Building 08 basement Room B-15 with wall/wall-mounted TE, legacy patch panels, legacy Fiber LIU, and floor UPS.
08 | B08_Assessment | 08 | B12B | Basement | Office / basement cabling area | Telecom enclosure / TE cabling service area | 1 | 0 | Verify | 08A-401 / 08E-701 / 08T-701 | Door schedule identifies B12B as Office with 45-minute door; telecom schedule and electrical schedule reference TE01-B12B-1 and TE receptacle Room B12B. Field verify actual TE/equipment scope.
08 | B08_Assessment | 08 | 2065A | Second | Existing copy/office/storage area converted | Telecom Room | 2 | 0 | Verify | 08A-401 / 08E-701 / 08T-604 / 08M-701 | Telecom Room 2065A, 127 SF; new rack elevation shows two 4-post floor racks, UPS, Zone PDU, network switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
09 | B09_Assessment | 09 | B01 | Basement | Storage / existing telecom equipment area | Telecom Room | 2 | 0 | Verify | 09A-400 / 09E-402 / 09T-604 / 09E-701 | Telecom Room B01, 200 SF; existing/new telecom equipment shown with panels B09-TRB01A/B and cooling circuits CU-0-1, CU-1-1, CU-2-1 in electrical schedule/enlarged plans.
09 | B09_Assessment | 09 | 104B | First | Interview room / existing area converted | Telecom Room | 2 | 0 | Verify | 09A-401 / 09E-401 / 09T-604 / 09E-701 | Telecom Room 104B, 85 SF; panels B09-TR104BA/B shown; first-level enlarged plans identify access control/security devices, IU-1-01, and TR receptacle/rack circuiting.
09 | B09_Assessment | 09 | 206A | Second | Nursing service / adjacent office area | Telecom Room | 2 | 0 | Verify | 09A-401 / 09E-401 / 09T-604 / 09E-701 | Telecom Room 206A, 120 SF; panels B09-TR206AA/B shown; second-level enlarged plans identify IU-2-01, TR circuits, security devices, and room layout adjacent to Nursing Service 206.
10 | B10_Assessment | 10 | 200A | Attic | Existing attic telecom/equipment area | Telecom Room | 2 | 1 | Verify | 10A-401 / 10E-401 / 10T-604 / 10M-701 | Primary Building 10 TR. Drawings identify attic-level Room 200A with existing wall-mounted rack/equipment, new telecom rack equipment, panels B10-TR200AA/AB, IU-1-01, CU-1-01, rack receptacles and future rack space.
10 | B10_Assessment | 10 | B24 | Basement | Existing electrical room - normal power | Electrical source / coordination room | 0 | 0 | Verify | 10E-401 / 10E-701 | Basement existing electrical room normal power referenced on electrical enlarged plan; coordinate B10-MDP/B10-L10-E feeders and load measurement.
10 | B10_Assessment | 10 | B25 | Basement | Existing electrical room - emergency power | Emergency electrical source / coordination room | 0 | 0 | Verify | 10E-401 / 10E-601 / 10E-701 | Basement existing electrical room emergency power referenced on electrical enlarged plan; coordinate ATS-B10-LSD, emergency source and TR equipment continuity.
12 | B12_Assessment | 12 | 00 / existing fiber path | B/1/2 | Existing building fiber pathway / pull-through route | Fiber-only pull-through scope | 0 | 0 | Verify | 12G-000 / 12T-100 / 12T-101 / 12T-604 | Cover sheet states Building 12 receives fiber only. Rack elevation sheet identifies Building 12 as existing rack elevation/fiber only with no rack mounting and no new TR buildout.
12 | B12_Assessment | 12 | Existing rack/demarc - field verify | Field verify | Existing service point / serving closet | Protect-in-place / fiber transition point | 0 | 0 | Verify | 12T-604 / 12T-601 / 12T-602 / 12T-603A/B | 12T-604 identifies building level B/1/2 and mounting type NONE/FIBER ONLY. Field verification required to document where fiber enters, passes through, and terminates.
13 | B13_Assessment | 13 | 124 | First | Telecom Room / new TR build area | Telecom Room | 2 | 1 | Verify | 13A-401 / 13E-401 / 13T-100 / 13T-701 | Primary Building 13 TR. Plans identify Telecom Room 124 at 119 SF, served by Rack ID TR01-124-1, panels B13-TR124AA/AB, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, and a future rack allowance.
13 | B13_Assessment | 13 | 222 | Second | Existing Tel Room / existing rack and patching area | Existing telecom transition point | 1 | 0 | Verify | 13T-100 / 13R-900 | Existing second-level Tel Room 222 shown with existing telco patch, plywood backboard, indoor AC unit, wall-mounted rack, patch panel, and security cabinet. Protect active services and verify what is transferred to Room 124.
14 | B14_Assessment | 14 | 119 | First | Telecom Room / new TR build area | Telecom Room | 1 | 1 | Verify | 14A-401 / 14E-100 / 14T-100 / 14T-604 / 14T-701 | Primary Building 14 TR. Plans identify Telecom Room 119 at 124 SF, served by Rack ID TR01-119-1, panels B14-TR119A/B, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, 56 feet of first-level cable tray, and a future rack allowance.
14 | B14_Assessment | 14 | B.01 | Basement | Existing Tel/F Panel room / telecom equipment area | Existing telecom transition point | 1 | 0 | Verify | 14T-100 / 14T-604 / 14R-900 | Existing basement Tel/F Panel B.01 shown at 165 SF with existing wall-mounted TE, patch panels, telco patch, plywood backboards, and legacy fiber/equipment. Protect active services and verify what transfers to Room 119.
14 | B14_Assessment | 14 | B2 | Basement | Existing telecom room reference | Existing telecom transition point | 1 | 0 | Verify | 14R-900 | Photo reference sheet identifies basement existing telecom room B2. Field verify whether B2 is same/related to B.01 or separate legacy telecom space.
15 | B15_Assessment | 15 | 124A | First | Office/room converted to Telecom Room | Telecom Room | 1 | 1 | Verify | 15A-401 / 15E-401 / 15T-100 / 15T-604 / 15T-701 | Primary Building 15 TR. Plans identify Telecom Room 124A at 121 SF, served by Rack ID TR15-109A-01, panels B15-TR124AA/AB, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, and a future rack allowance.
15 | B15_Assessment | 15 | 222 | Second | Existing Tel Room / wall-mounted rack and support equipment | Existing telecom transition point | 1 | 0 | Verify | 15T-100 / 15T-604 / 15R-900 | Existing second-level Tel Room 222 shown at 65 SF with existing/remain indoor AC unit, security cabinet, ground bar, plywood backboard, wall-mounted rack, existing Cisco switches, legacy patch panels, and floor UPS; protect active services and verify transfer to Room 124A.
15 | B15_Assessment | 15 | B01 | Basement | Existing telecom/crossover area | Existing telecom transition point | 1 | 0 | Verify | 15T-604 / 15R-900 | Rack elevations identify existing B-01 crossover wall/wall-mount TE with legacy 24-port patch panel. Photo reference identifies basement existing telecom room B01.
16 | B16_Assessment | 16 | 015 | Basement | Vacant / new telecom room build area | Telecom Room | 1 | 1 | Verify | 16A-400 / 16E-100 / 16T-100 / 16T-604 / 16T-701 | Primary Building 16 TR. Plans identify Telecom Room 015 at 79 SF, served by Rack ID TR01-015-A-1, panels B16-TR015A/B, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, 96 feet total cable tray, and future rack allowance.
16 | B16_Assessment | 16 | 014 | Basement | Existing telecom room / stair-adjacent legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 16T-100 / 16T-604 / 16R-900 | Existing basement Telecom Room 014 shown with wall-mounted rack, plywood backboard, patch panel, security cabinet, telco patch, existing floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU/wall; protect active services and verify transfer to Room 015.
17 | B17_Assessment | 17 | 118 | First | New telecom room build area | Telecom Room | 1 | 1 | Verify | 17_29A-401 / 17_29E-401 / 17_29T-100 / 17_29T-604 / 17_29T-701 | Primary Building 17 TR. Plans identify Telecom Room 118 at 157 SF, Rack ID TR17-118-1, panels B17-TR118A/B, 208V rack UPS/PDU equipment, IU-1-01/CU-1-01 cooling, 517 feet total cable tray, and future rack allowance. Rack elevation notes Room 118 serves Building 29.
17 | B17_Assessment | 17 | B35A | Basement | Existing telecom closet / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 17_29T-100 / 17_29T-604 / 17_29R-900 | Existing basement Telecom Closet B35A shown at 12 SF with wall-mounted TE, patch panel, security cabinet, plywood backboard, indoor AC unit, floor UPS, Cisco switches, legacy Ortronics 24/48-port patch panels and SERTEX utility service ports. Protect active services and verify transfer to Room 118.
17 | B17_Assessment | 29 | Building 29 path | First / served from B17 | Building 29 service extension | Served from B17 TR 118 | 0 | 0 | Verify | 17_29T-100 / 17_29T-604 / 17_29T-701 | Building 29 is shown served from B17, with path to B29 via 4-inch PVC and fiber extending from Building 17 to Building 29. Field verify pathway, service boundary, and active outlets included in TR17-118-1 schedule.
18 | B18_Assessment | 18 | 110 | First | New telecom room build area | Telecom Room | 1 | 1 | Verify | 18A-401 / 18E-101 / 18T-100 / 18T-401 / 18T-604 / 18T-701 | Primary Building 18 TR. Plans identify Telecom Room 110 at 168 SF, Rack ID TR01-111A-1, panels B18-TR110A/B, 208V rack UPS/PDU equipment, IU-1-01/CU-1-01 cooling, 315 feet total cable tray, and future rack allowance. Room 110 is the new rack room even though the schedule labels RM 111A.
18 | B18_Assessment | 18 | 111B | First | Existing TE / stair-adjacent legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 18T-401 / 18T-604 / 18R-900 | Existing first-level TE 111B shown at 13 SF with wall-mounted rack, plywood backboard, patch panel, security cabinet, existing floor UPS, and 5RU fiber optic housing. Protect active services and verify transfer to Room 110.
18 | B18_Assessment | 18 | 213 | Second | Existing telecom closet / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 18T-401 / 18T-604 / 18R-900 | Existing second-level Closet 213 shown at 8 SF with wall-mounted rack, plywood backboard, patch panel, security cabinet, APC floor UPS, SERTEX utility service ports, Cisco switch and legacy Ortronics patch panels. Protect active services and verify transfer to Room 110.
20 | B20_Assessment | 20 | 1B | First | Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 20T-101 / 20T-701 / 20E-101 / 20E-601 | Primary Building 20 TE. Plans identify Office 1B at 110 SF with new wall-mount telecom enclosure Rack ID TE01-1B-1, 12RU enclosure, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and 33 total ports with 10% allowance.
20 | B20_Assessment | 20 | 8A | First | Existing Tel/Data Closet / open TE cabinet | Existing telecom transition point | 2 | 0 | Verify | 20T-101 / 20T-701 / 20R-900 | Existing Tel/Data Closet 8A at 17 SF with existing open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy Ortronics 48-port patch panel, floor UPS and Fiber LIU. Protect active services and transfer to Office 1B TE.
21 | B21_Assessment | 21 | 100A | First | M&O Foreman Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 21_19T-101 / 21_19T-604 / 21_19T-701 / 21_19E-101 | Primary Building 21/B19 TE. Plans identify M&O Foreman Office 100A at 202 SF with new 12RU telecom enclosure, shown as 19 serving 21, Room 100-A, and schedule Rack ID TR01-104-1 / RM 104. Includes APC UPS, two PDUs, network switches B20 and B19, 48-port Cat6A patch panel, Fiber LIU, and 131 total ports with 10% allowance.
21 | B21_Assessment | 21 | B1.TR | Basement | Existing telecom room / wall-mount TE | Existing telecom transition point | 1 | 0 | Verify | 21_19T-100 / 21_19T-604 | Existing Building 21 basement B1.TR shown with legacy Ortronics 24/48-port patch panels, UPS on ground, Cisco switch, multiple legacy 24-port patch panels, Fiber LIU, and APC floor UPS. Protect active services and verify transfer/cutover to new TE.
21 | B21_Assessment | 19 | B05TR | Basement / First | Existing telecom room / wall-mount TE | Existing telecom transition point serving B19/B21 | 2 | 0 | Verify | 21_19T-100 / 21_19T-604 / 21_19R-900 | Existing Building 19 B05TR shown with basement and first-level existing elevations, legacy Ortronics patch panels, Cisco switch, Fiber LIU, APC floor UPS, and photo reference for basement B05. New enclosure is marked '19 serving 21'.
22 | B22_Assessment | 22 | 102 | First | Break Room / new TE location | Telecom Enclosure | 1 | 0 | Verify | 22T-101 / 22T-701 / 22E-101 / 22E-701 | Primary Building 22 TE. Plans identify Break Room 102 at 358 SF with new 12RU telecom enclosure Rack ID TR01-102-1, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and 8 total ports with 10% allowance.
22 | B22_Assessment | 22 | 103 | First | Existing wall/wall-mount TE / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 22T-101 / 22T-701 / 22R-900 | Existing Room 103 first-level wall/wall-mount TE shown with APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall, and ports 1-24 to Building 19 ports 73-96. Protect active services and transfer to Room 102 TE.
33 | B33_Assessment | 33 | B23 | Basement | EEO Manager Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 33T-100 / 33T-604 / 33T-701 / 33E-100 / 33E-701 | Primary Building 33 TE. Plans identify EEO Manager Office B23 at 175 SF with new 12RU telecom enclosure Rack ID TE01-B23-1, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, 55 WAO total, and 97 total ports with 10% allowance.
33 | B33_Assessment | 33 | B17 | Basement / First photo reference | Existing Tel Closet / open TE cabinet and legacy equipment | Existing telecom transition point | 2 | 0 | Verify | 33T-100 / 33T-604 / 33R-900 | Existing Tel Closet B17 shown at 13 SF with existing open TE cabinet, network door controller, indoor AC unit, plywood backboard, keypad, patch panel, ground bar, equipment box, Cisco switches, legacy patch panels, Fiber LIU, SERTEX utility service, and UPS on floor. Protect active services and verify transfer to Room B23 TE.
61 | B61_Assessment | 61 | B13H-A | Basement | Basement telecom / support area | Telecom Room | 1 | 1 | Pass | 61A-400 / 61E-401 / 61T-100 / 61T-401 / 61T-604 / 61T-701 | Basement TR identified as RM B13H-A with Rack ID TR01-B13H-A-1. Schedules identify 88 WAO total, 74 active ports, 129 scheduled ports, 142 ports with 10% allowance. Electrical panels include B61-TRB13A/B. Mechanical cooling includes IU-0-01/CU-0-01.
61 | B61_Assessment | 61 | 124 | First | First-level telecom area | Telecom Room | 1 | 1 | Pass | 61A-400 / 61E-402 / 61T-101 / 61T-401 / 61T-604 / 61T-701 | First-level TR identified as Room 124 / Rack ID TR01-124-1. Electrical panels include B61-TR124A/B. Mechanical cooling includes IU-1-01/CU-1-01. Verify room naming against electrical schedule references that also call out RM137B rack receptacles.
61 | B61_Assessment | 61 | 226 | Second | Second-level telecom area | Telecom Room | 1 | 1 | Pass | 61A-401 / 61E-402 / 61T-102 / 61T-401 / 61T-605 / 61T-702 | Second-level TR identified as Room 226 / Rack ID TR01-226-1. Schedules identify 109 WAO total, 126 active ports, 156 scheduled ports, 172 ports with 10% allowance. Electrical panels include B61-TR226A/B. Mechanical cooling includes IU-2-01/CU-2-01.
61 | B61_Assessment | 61 | 137 / 137A | First | Existing server/demarc/telecom equipment rooms | Existing demarc / server transition point | 11 | 0 | Pass | 61T-402 / 61T-606 / 61T-607 / 61R-900 | Existing Room 137/137A rack inventory and demarc/server equipment include existing 4-post racks, PACS/equipment racks, APC UPS/PDU equipment, Fujitsu FLM equipment, wall-mounted patch panels, and local elevations. Protect active services and verify what remains, transfers, or is modified.
62 | B62_TR_Assessment | 62 | B24A | Basement | Restroom / Storage | TR | 1 | 1 | Verify | B62 IFC | 0
62 | B62_TR_Assessment | 62 | 125 | First | Medication Room | TR | 1 | 1 | Verify | B62 IFC | 0
62 | B62_TR_Assessment | 62 | 225 | Second | Office | TR | 1 | 1 | Verify | B62 IFC | 0
70 | B70_TR_Assessment | 70 | B27 | Basement | Telecom Room / existing service area | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room B27; rack elevation references B-27 with 1 rack + future.
70 | B70_TR_Assessment | 70 | 125A | First | Telecom Room / existing or renovated space | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room 125A; rack elevation references 125-A with 1 rack + future.
70 | B70_TR_Assessment | 70 | 262A | Second | Telecom Room / existing or renovated space | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room 262A; rack elevation references 262-A with 1 rack + future.
78 | B70_TR_Assessment | 78/78A | B30 | Basement | Basement telecom area / existing rack transfer | Telecom Room | 2 | 1 | Verify | 78_78AA-400 / 78_78AE-401 / 78_78AT-100 / 78_78AT-604 / 78_78AT-701 | Basement primary TR. Schedule identifies RM B30 with 210 WAO total, 23 active ports, 311 scheduled ports, 342 total ports with 10% allowance. Rack IDs include TR01-B30-1 and TR01-B30-2.
78 | B70_TR_Assessment | 78/78A | B35 | Basement | Basement telecom area / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AT-100 / 78_78AT-605 / 78_78AT-702 | Basement TR/closet. Schedule identifies RM B35 with 53 WAO total, 23 active ports, 64 scheduled ports, 70 total ports with 10% allowance. Verify relationship to existing basement telecom room 15E photo reference.
78 | B70_TR_Assessment | 78/78A | 1232 | First | First-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-401 / 78_78AE-402 / 78_78AT-101 / 78_78AT-606 / 78_78AT-702/703 | First-level TR. Schedule identifies RM 1232 with 301 WAO total, 388 active ports, 404 scheduled ports, 444 total ports with 10% allowance. Existing photo references show first-level existing telecom room 1234; verify room-name mapping.
78 | B70_TR_Assessment | 78/78A | 227A | Second | Second-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-401 / 78_78AE-402 / 78_78AT-102 / 78_78AT-606 / 78_78AT-703/704 | Second-level TR. Schedule identifies RM 227A with 256 WAO total, 153 active ports, 348 scheduled ports, 383 total ports with 10% allowance. Existing photo references show second-level existing telecom room 1234; verify field room ID.
78 | B78_Assessment | 78/78A | 342 | Third | Third-level telecom room / existing rack transfer | Telecom Room | 2 | 1 | Verify | 78_78AA-402 / 78_78AE-403 / 78_78AT-103 / 78_78AT-607 / 78_78AT-704 | Third-level TR. Schedule identifies RM 342 with 158 WAO total, 163 active ports, 289 scheduled ports, 318 total ports with 10% allowance. Rack IDs include TR01-342-1 and TR01-342-2.
78 | B78_Assessment | 78/78A | 401 | Fourth | Fourth-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-402 / 78_78AE-404 / 78_78AT-104 / 78_78AT-607 / 78_78AT-705 | Fourth-level TR. Schedule identifies RM 401 with 89 WAO total, 65 active ports, 123 scheduled ports, 135 total ports with 10% allowance.
78 | B78_Assessment | 78/78A | 15E / 1234 / 353 / 308A / 408A | Existing levels | Existing telecom rooms / photo references | Existing telecom transition points | 5 | 0 | Verify | 78_78AR-900 / 901 / 902 / 903 | Photo references identify existing telecom rooms: basement 15E, first-level 1234, second-level 1234, third-level 353, fourth-level 308A and 408A. Protect active equipment and verify transfer/abandonment scope.
80 | B80_Assessment | 80 | 102 | First | Telecom Room / new TR build area | Telecom Room | 1 | 1 | Verify | 80A-401 / 80E-101 / 80E-401 / 80T-101 / 80T-604 / 80T-701 | Primary Building 80 TR. Plans identify Telecom Room 102 at 140 SF, new Rack ID TR01-102-1 plus future rack, panels B80-TR102A/B, 5kW 208V UPS/PDU rack power, IU-1-01/CU-1-01 dedicated cooling, camera 102-CAM-1, and 215 total ports with 10% allowance.
80 | B80_Assessment | 80 | 127A / 126 | First | Existing Tel Closet / existing telecom room photo reference | Existing telecom transition point | 1 | 0 | Verify | 80T-101 / 80T-604 / 80R-900 | Existing Tel Closet 127A shown at 9 SF with existing plywood backboard, ground bar, patch panel, equipment box and two-post TR. Rack elevation/photo reference identify existing room 126/127-A with existing wall/wall-mount TE, Cisco switches, legacy optical Fiber LIU, multiple legacy Ortronics patch panels, Cat5e patch panel and APC floor UPS. Verify room-number mapping and active services.
82 | B82_Assessment | 82 | 102 | First | Telecom Room / new TE location | Telecom Enclosure | 1 | 0 | Verify | 82A-401 / 82M-101 / 82E-101 / 82T-101 / 82T-604 / 82T-701 | Primary Building 82 TE. Plans identify Telecom Room 102 at 86 SF with new 12RU telecom enclosure, Rack ID TR01-102-01, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, IU-1-01/CU-1-01 cooling, and 40 total ports with 10% allowance.
82 | B82_Assessment | 82 | B01-A | First | Existing telecom room / wall rack and patch panels | Existing telecom transition point | 1 | 0 | Verify | 82T-101 / 82T-604 / 82R-900 | Existing first-level telecom room B01-A shown with existing wall rack, Cisco switches, cable management, Ortronics 24-port patch panels, APC floor UPS, and photo reference. Protect active services and verify transfer to Room 102 TE.
BCH | B82_Assessment | BCH | 107 | First | Existing Crescent House room area / telecom work area | Telecom Enclosure / Telecom Room | 1 | 0 | Verify | BCHGA-401 / BCHE-101 / BCHT-101 / BCHT-604 | Primary BCH telecom location. Architectural/electrical/telecom plans reference first-level Room 107. BCHT-101 enlarged plan identifies RM 107 new telecom work. BCHT-604 shows BCH Crescent House Room 107 as new telecom room / no existing elevations.
BCH | B82_Assessment | BCH | 00 / 107 | First | Rack/elevation reference location | Telecom Enclosure | 1 | 0 | Verify | BCHT-604 | Rack elevation shows 12RU telecom enclosure with APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and first-level mounting. Also includes separate BCH Crescent House Room 107 / new telecom room elevation; field confirm correct configuration.
MCR | B82_Assessment | MCR | 107 / MCR | Ground | New Main Computer Room / MCR building | Main Computer Room | 12 | 0 | Verify | MCRA-101 / MCRT-100 / MCRT-101 / MCRT-401 / MCRT-607-609 / MCRT-701 | Primary new MCR space. Telecom plans show MDA-A1/A2/A3, MDA-B1/B2/B3, HDA-A, HDA-B, UPS-A and UPS-B. Rack elevations identify MDA A/B racks, HDA A/B server cabinets, existing server cabinet transfer references, 10 WAO total and 359 ft cable tray.
MCR | B82_Assessment | MCR | 031 / Fiber Entrance Room 1 | Ground | Fiber entrance / telecom pathway space | Fiber Entrance / support room | 1 | 0 | Verify | MCRT-401 / MCRT-701 | MCRT-701 schedule is titled Data Device and Circuit Schedule - Fiber Entrance Room 1 and identifies Rack ID TR01-031-1, four data outlets 31-A/B/C/D and security camera/data devices 07-CAM-03/04/07/08/11.
MCR | B82_Assessment | MCR | MDA-A1/A2/A3 | Ground | New MDA row A | Main Distribution Area A | 3 | 0 | Verify | MCRT-607 | New MDA A racks: MDA-A-1, MDA-A-2, MDA-A-3. MDA A-2 includes 1RU LIU for hybrid FOC to HDA and 48x Cat6A to HDA. MDA A-1/A-3 reserved for LAN elements/leaf/access or spine/aggregation.
MCR | B82_Assessment | MCR | MDA-B1/B2/B3 | Ground | New MDA row B | Main Distribution Area B | 3 | 0 | Verify | MCRT-607 | New MDA B racks: MDA-B-1, MDA-B-2, MDA-B-3. MDA B-2 includes 1RU LIU for hybrid FOC to HDA and 48x Cat6A to HDA. Supports redundant B-side backbone/distribution.
MCR | MCR_Assessment | MCR | HDA-A | Ground | New HDA A row | Horizontal Distribution Area A | 1 | 0 | Verify | MCRT-608 | HDA A-1 new server cabinet front/rear elevation, 48-port Cat6A patch panels, HD fiber LIUs, HD Cat6A patch panel to MDA-A2, and backbone side A/B LIU. Also includes existing B61 server cabinet transfer references.
MCR | MCR_Assessment | MCR | HDA-B | Ground | New HDA B row | Horizontal Distribution Area B | 1 | 0 | Verify | MCRT-609 | HDA B-1 new server cabinet front/rear elevation, 48-port Cat6A patch panels, HD fiber LIUs, HD Cat6A patch panel to MDA-B2, and duplicate existing B61 server cabinet transfer references.
MCR | MCR_Assessment | MCR | Existing 107 / 137 Server MCR | Existing / transition | Existing MCR/server/core equipment | Existing equipment transition point | 20 | 0 | Verify | MCRT-604 / MCRT-605 / MCRT-606 / MCRT-608 / MCRT-609 | Existing MCR elevations include Rows 1-3 and existing server cabinet B61 equipment, Cisco core, WAN aggregation, NetScout, Canoga Perkins, Cisco switches, legacy Ortronics patch panels, LIUs, APC/Chatsworth/HP PDUs and UPS equipment. Protect and phase transfer.
B01_Assessment
MAPPED PHOTO / DOCUMENTATION NEEDS — FORMULA-FED FROM BUILDING SHEETS | B01_Assessment
Building | B01_Assessment | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
01 | B01_Assessment | B01-P001 | 107 | Existing / New Condition | Room 107 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, fiber path A/B, cable tray and penetrations | 0 | Paul | 0 | B01-R1/B01-R3 | Closed | 0
01 | B01_Assessment | B01-P002 | B02 | Existing Equipment | Basement existing telecom room B02 racks, wall TE, Cisco/Nokia/Baseband/IRU/Corning/Ortronics equipment, UPS and cable entries | 0 | Paul | 0 | B01-R1/B01-R2 | Closed | 0
01 | B01_Assessment | B01-P003 | 138 | Existing Equipment | First-level existing telecom room 138 racks, patch panels, Cisco, Corning, APC UPS and active service labels | 0 | Paul | 0 | B01-R2/B01-R6 | Closed | 0
01 | B01_Assessment | B01-P004 | 282 | Existing Equipment | Second-level existing telecom room 282 racks, Cisco switches, Ortronics patch panels, cable managers and active service labels | 0 | Paul | 0 | B01-R2/B01-R6 | Closed | 0
01 | B01_Assessment | B01-P005 | 107 | HVAC | IU-1-01/CU-1-01, condensate pump/line, thermostat, BACnet adapter, disconnects, FMS alarm points and power source | 0 | Paul | 0 | B01-R3 | Closed | 0
01 | B01_Assessment | B01-P006 | 107 | Electrical | B01-TR107A/B panels, rack receptacles, breakers, SPD, PACS power supply, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B01-R4/B01-R7 | Closed | 0
01 | B01_Assessment | B01-P007 | All | Cable Tray / Firestop | Basement/first/second cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B01-R5 | Closed | 0
01 | B01_Assessment | B01-P008 | 107 / Existing Rooms | Telecom / Security | New rack/future rack, Fiber LIU, Cat6A, patch panels, labels/test records, 107-CAM-1, PACS and existing rack transfer work | 0 | Paul | 0 | B01-R6/B01-R8 | Closed | 0
02 | B01_Assessment | B02-P001 | 141 | Existing / New Condition | Room 141 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 174-CAM-01, penetrations and demo/relocation conditions | 0 | Paul | 0 | B02-R1/B02-R3 | Closed | 0
02 | B01_Assessment | B02-P002 | 236 | Existing / New Condition | Room 236 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 236-CAM-01, penetrations and existing transfer conditions | 0 | Paul | 0 | B02-R1/B02-R6 | Closed | 0
02 | B01_Assessment | B02-P003 | 342 | Existing / New Condition | Room 342 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 342-CAM-01, penetrations and 342A-CK-A | 0 | Paul | 0 | B02-R1/B02-R7 | Closed | 0
02 | B01_Assessment | B02-P004 | B-06 | Existing Equipment | Basement existing telecom room B-06 legacy rack/patch panels, active service labels and cable entries | 0 | Paul | 0 | B02-R2 | Closed | 0
02 | B01_Assessment | B02-P005 | Existing 141 / 236 | Existing Equipment | Existing first/second-level telecom rooms 141 and 236, existing patch panels, relocated/removed equipment and fire alarm cabinet conditions | 0 | Paul | 0 | B02-R2/B02-R6 | Closed | 0
02 | B02_Assessment | B02-P006 | All TRs | Electrical / HVAC | B02-TR141/236/342 A/B panels, rack receptacles, breakers, SPD, UPS/PDU, CU/IU equipment, condensate, disconnects and labels | 0 | Paul | 0 | B02-R3/B02-R4 | Closed | 0
02 | B02_Assessment | B02-P007 | All | Cable Tray / Firestop | Basement/first/second/third/fourth cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B02-R5 | Closed | 0
02 | B02_Assessment | B02-P008 | All TRs | Telecom / Security | Racks, Fiber LIU, Cat6A, patch panels, labels/test records, cameras, PACS and existing rack transfer work | 0 | Paul | 0 | B02-R6/B02-R8 | Closed | 0
03 | B02_Assessment | B03-P001 | 101E | Existing / New Condition | Room 101E walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, penetrations, PACS and final TR layout | 0 | Paul | 0 | B03-R1/B03-R3 | Closed | 0
03 | B02_Assessment | B03-P002 | 107 | Existing Equipment | Basement existing telecom room 107 rack, UPS on floor, Cisco switch, legacy patch panels, fiber LIU, active service labels and cable entries | 0 | Paul | 0 | B03-R1/B03-R2 | Closed | 0
03 | B02_Assessment | B03-P003 | 101C | Existing DMARC | First-floor existing DMARC Room 101C, patch panels, telecom cabinet, branch panel, provider/fiber equipment, 101C-CAM-01 and active service labels | 0 | Paul | 0 | B03-R2/B03-R6 | Closed | 0
03 | B02_Assessment | B03-P004 | 101E / 101C | Electrical / Security | B03-TR101CA/B panels, rack receptacles, breakers, SPD, UPS/PDU, access controller, CU-01, 101C-CAM-01 and labels | 0 | Paul | 0 | B03-R4/B03-R7 | Closed | 0
03 | B02_Assessment | B03-P005 | 101E | HVAC | IU/CU-01, condensate route, thermostat, BACnet adapter, disconnects, alarm points and emergency power source | 0 | Paul | 0 | B03-R3 | Closed | 0
03 | B03_Assessment | B03-P006 | All | Cable Tray / Firestop | Basement and first-level cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B03-R5 | Closed | 0
03 | B03_Assessment | B03-P007 | WAO Areas | Telecom Devices | Representative outlets/WAPs/Centrak/clock/camera locations including 108-A/B/C, 108-CK-A, 107A-AP-A, 101C-CAM-01 and related labels | 0 | Paul | 0 | B03-R6 | Closed | 0
03 | B03_Assessment | B03-P008 | 101E / Existing Rooms | Telecom Acceptance | New racks TR01-101E-1/2, Fiber LIU, Cat6A, patch panels, labels/test records and existing rack transfer work | 0 | Paul | 0 | B03-R6/B03-R8 | Closed | 0
04 | B03_Assessment | B04-P001 | B05 | Existing Condition | Basement TR B05 existing conditions, racks, utilities, penetrations, panels | 0 | Paul | 0 | B04-R1/B04-R2 | Closed | 0
04 | B03_Assessment | B04-P002 | 141 | Existing Condition | Room 141 existing conditions, door/walls/ceiling/window/floor conditions | 0 | Paul | 0 | B04-R3 | Closed | 0
04 | B03_Assessment | B04-P003 | 244A | Existing Condition | Room 244A TR existing condition and panel/rack area | 0 | Paul | 0 | B04-R1 | Closed | 0
04 | B03_Assessment | B04-P004 | All | Firestop | All floor/wall/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B04-R7 | Closed | 0
04 | B03_Assessment | B04-P005 | All | HVAC | Cooling units, condensate routing, controls, high-temp alarms | 0 | Paul | 0 | B04-R4 | Closed | 0
04 | B04_Assessment | B04-P006 | All | Electrical | Panels, breakers, UPS/PDU receptacles, SPD, grounding/bonding | 0 | Paul | 0 | B04-R5 | Closed | 0
04 | B04_Assessment | B04-P007 | All | Telecom | Racks, ladder tray, fiber, Cat6A, labels, LIU, cable managers | 0 | Paul | 0 | B04-R6 | Closed | 0
04 | B04_Assessment | B04-P008 | All | Security | PACS, card reader, electric strike, camera, motion sensor rough-in | 0 | Paul | 0 | B04-R3 | Closed | 0
05 | B04_Assessment | B05-P001 | 150 | Existing Condition | Room 150 wall/TE location, mounting surface, clearances, power, pathway | 0 | Paul | 0 | B05-R1/B05-R4 | Closed | 0
05 | B04_Assessment | B05-P002 | 153-A | Existing Condition | Existing wall/wall-mount TE, Cisco switches, legacy patch panels, floor UPS | 0 | Paul | 0 | B05-R2 | Closed | 0
05 | B04_Assessment | B05-P003 | All | Firestop | All new/reused penetrations and surface raceway/conduit routes | 0 | Paul | 0 | B05-R5 | Closed | 0
05 | B05_Assessment | B05-P004 | 150 | Electrical | UPS/PDU outlet, circuit label, panel source, grounding/bonding | 0 | Paul | 0 | B05-R4 | Closed | 0
05 | B05_Assessment | B05-P005 | All | Telecom | TE, patch panels, Fiber LIU, labels, testing records, as-built conditions | 0 | Paul | 0 | B05-R6 | Closed | 0
05 | B05_Assessment | B05-P006 | All | Security | Door/security/CCTV/PACS conditions at TE location | 0 | Paul | 0 | B05-R6 | Closed | 0
06 | B05_Assessment | B06-P001 | B-01 | Existing Condition | Existing basement wall/wall-mount TE, Cisco switches, legacy patch panels, floor UPS | 0 | Paul | 0 | B06-R1/B06-R2 | Closed | 0
06 | B05_Assessment | B06-P002 | 178 | Existing Condition | Room 178 TR, existing 2-post racks, panels, card reader/security, HVAC location | 0 | Paul | 0 | B06-R1/B06-R3 | Closed | 0
06 | B05_Assessment | B06-P003 | 233 | Existing Condition | Room 233/Data Closet, adjacent toilet/bath areas, walls/door/ceiling/penetrations | 0 | Paul | 0 | B06-R4 | Closed | 0
06 | B05_Assessment | B06-P004 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B06-R6 | Closed | 0
06 | B05_Assessment | B06-P005 | 178/233 | HVAC | IU/CU equipment, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm | 0 | Paul | 0 | B06-R5 | Closed | 0
06 | B06_Assessment | B06-P006 | All | Electrical | B06-NP-TR, B06-EP-TR, B06-TR178A/B, B06-TR233A/B, breakers, SPD, labels | 0 | Paul | 0 | B06-R3/B06-R6 | Closed | 0
06 | B06_Assessment | B06-P007 | All | Telecom | Racks, ladder tray, fiber, Cat6A, LIU, patch panels, labels, test records | 0 | Paul | 0 | B06-R7 | Closed | 0
06 | B06_Assessment | B06-P008 | All | Security | Card readers, electric strikes, door position, motion sensors, CCTV/PACS integration | 0 | Paul | 0 | B06-R4 | Closed | 0
07 | B06_Assessment | B07-P001 | B-18 | Existing Condition | Basement TR B-18 existing room, walls, ceiling, floor, utilities, penetrations and pathway | 0 | Paul | 0 | B07-R1/B07-R2 | Closed | 0
07 | B06_Assessment | B07-P002 | 228A | Existing Condition | Second-floor TR 228A, door/wall/furring/window conditions, adjacent spaces and pathway | 0 | Paul | 0 | B07-R1/B07-R3 | Closed | 0
07 | B06_Assessment | B07-P003 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B07-R7 | Closed | 0
07 | B06_Assessment | B07-P004 | B-18/228A | HVAC | IU/CU units, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B07-R4 | Closed | 0
07 | B07_Assessment | B07-P005 | All | Electrical | B07-TRB18A/B and B07-TR228A/B panels, breakers, SPD, rack receptacles and labels | 0 | Paul | 0 | B07-R5 | Closed | 0
07 | B07_Assessment | B07-P006 | All | Telecom | Racks, ladder tray, fiber, Cat6A, patch panels, LIU, labels and test records | 0 | Paul | 0 | B07-R6 | Closed | 0
07 | B07_Assessment | B07-P007 | All | Security | Card reader, electric strike, door position, CCTV/PACS and motion sensors | 0 | Paul | 0 | B07-R3 | Closed | 0
08 | B07_Assessment | B08-P001 | B-15 | Existing Condition | Existing basement TE, legacy patch panels, Fiber LIU, floor UPS and pathways | 0 | Paul | 0 | B08-R1/B08-R2 | Closed | 0
08 | B07_Assessment | B08-P002 | B12B | Existing Condition | Basement B12B office/TE location, door, pathways, receptacles, panel source and penetrations | 0 | Paul | 0 | B08-R3 | Closed | 0
08 | B07_Assessment | B08-P003 | 2065A | Existing Condition | Second-floor TR 2065A room, door/walls/ceiling/floor, exterior furring/window, penetrations | 0 | Paul | 0 | B08-R4 | Closed | 0
08 | B07_Assessment | B08-P004 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B08-R7 | Closed | 0
08 | B07_Assessment | B08-P005 | 2065A | HVAC | IU-2-01/CU-2-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power | 0 | Paul | 0 | B08-R5 | Closed | 0
08 | B08_Assessment | B08-P006 | All | Electrical | B08-TR2065AA/AB panels, breakers, SPD, rack receptacles, TE receptacle B12B and labels | 0 | Paul | 0 | B08-R6 | Closed | 0
08 | B08_Assessment | B08-P007 | All | Telecom | B-15 legacy equipment, B12B TE schedule, 2065A racks, fiber, Cat6A, patch panels, LIU, labels and test records | 0 | Paul | 0 | B08-R2/B08-R8 | Closed | 0
08 | B08_Assessment | B08-P008 | All | Security | Card reader, electric strike, door position, CCTV/PACS and motion sensors | 0 | Paul | 0 | B08-R4 | Closed | 0
09 | B08_Assessment | B09-P001 | B01 | Existing Condition | Basement TR B01 existing telecom/security/network equipment, storage conditions, panels, ceiling, walls and pathways | 0 | Paul | 0 | B09-R1/B09-R2 | Closed | 0
09 | B08_Assessment | B09-P002 | 104B | Existing Condition | First-level TR 104B, walls/door/ceiling/floor, security devices, IU-1-01 location and pathways | 0 | Paul | 0 | B09-R1/B09-R4 | Closed | 0
09 | B08_Assessment | B09-P003 | 206A | Existing Condition | Second-level TR 206A, walls/door/ceiling/floor, adjacent Nursing Service 206, IU-2-01 location and pathways | 0 | Paul | 0 | B09-R1/B09-R4 | Closed | 0
09 | B08_Assessment | B09-P004 | All | Hazardous Materials | Flooring, ceilings, pipe insulation, penetrations and abatement-related locations before disturbance | 0 | Paul | 0 | B09-R3 | Closed | 0
09 | B08_Assessment | B09-P005 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B09-R7 | Closed | 0
09 | B09_Assessment | B09-P006 | All | HVAC | IU/CU equipment, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B09-R5 | Closed | 0
09 | B09_Assessment | B09-P007 | All | Electrical | B09 TR panels, breakers, SPD, rack receptacles, access controllers, lighting and labels | 0 | Paul | 0 | B09-R6 | Closed | 0
09 | B09_Assessment | B09-P008 | All | Telecom/Security | Racks, fiber, Cat6A, LIU, patch panels, labeling/testing, cameras, access control and VMS/PACS integration | 0 | Paul | 0 | B09-R8 | Closed | 0
10 | B09_Assessment | B10-P001 | 200A | Existing Condition | Attic TR 200A existing rack/equipment, floor/deck, walls, access route, pathways and clearances | 0 | Paul | 0 | B10-R1/B10-R3 | Closed | 0
10 | B09_Assessment | B10-P002 | 200A | Hazardous Materials | Attic abatement-related materials, flooring/penetrations, ceiling/deck and disturbance areas | 0 | Paul | 0 | B10-R2 | Closed | 0
10 | B09_Assessment | B10-P003 | B24 | Electrical | Existing normal electrical room panels, B10-MDP/B10-L10-E, feeder route and working clearances | 0 | Paul | 0 | B10-R5 | Closed | 0
10 | B09_Assessment | B10-P004 | B25 | Electrical | Existing emergency electrical room, ATS-B10-LSD/emergency distribution and access constraints | 0 | Paul | 0 | B10-R5 | Closed | 0
10 | B09_Assessment | B10-P005 | 200A | Firestop | All attic wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B10-R6 | Closed | 0
10 | B10_Assessment | B10-P006 | 200A | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B10-R4 | Closed | 0
10 | B10_Assessment | B10-P007 | 200A | Telecom | Racks, UPS/PDU, fiber, Cat6A, patch panels, LIU, bonding, labels and test records | 0 | Paul | 0 | B10-R7 | Closed | 0
10 | B10_Assessment | B10-P008 | 200A | Security | Card reader, electric strike, door position, CCTV/PACS, motion sensor and VMS/PACS integration | 0 | Paul | 0 | B10-R8 | Closed | 0
12 | B12_Assessment | B12-P001 | Fiber path B/1/2 | Existing Condition | Existing conduit/cable tray/pathway from entry through basement/first/second levels | 0 | Paul | 0 | B12-R2 | Closed | 0
12 | B12_Assessment | B12-P002 | Existing rack/demarc - field verify | Existing Condition | Existing rack, demarc, serving closet or fiber termination/pass-through point | 0 | Paul | 0 | B12-R5 | Closed | 0
12 | B12_Assessment | B12-P003 | All | Firestop | All floor/wall/sleeve penetrations before pull, during work, and after permanent firestop | 0 | Paul | 0 | B12-R4 | Closed | 0
12 | B12_Assessment | B12-P004 | All | Telecom | Fiber reels, pull route, pull boxes, labels, slack loops, termination points and test records | 0 | Paul | 0 | B12-R3/B12-R6 | Closed | 0
12 | B12_Assessment | B12-P005 | All | Closeout | Fiber certification/OTDR screenshots, labeling, as-built route and VA/OIT acceptance evidence | 0 | Paul | 0 | B12-R6 | Closed | 0
13 | B12_Assessment | B13-P001 | 124 | Existing Condition | Room 124 walls, ceiling/deck, floor, door, adjacent Telehealth 124A/109, rack location, pathways and penetrations | 0 | Paul | 0 | B13-R1/B13-R6 | Closed | 0
13 | B12_Assessment | B13-P002 | 222 | Existing Condition | Existing Tel Room 222 wall rack, telco patch, plywood backboard, AC unit, patch panel and security cabinet | 0 | Paul | 0 | B13-R1/B13-R3 | Closed | 0
13 | B12_Assessment | B13-P003 | 124 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B13-R2 | Closed | 0
13 | B12_Assessment | B13-P004 | 124 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B13-R6 | Closed | 0
13 | B12_Assessment | B13-P005 | 124 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B13-R4 | Closed | 0
13 | B13_Assessment | B13-P006 | 124 | Electrical | B13-TR124AA/AB panels, rack receptacles, breakers, SPD, access controller, lighting and labels | 0 | Paul | 0 | B13-R5 | Closed | 0
13 | B13_Assessment | B13-P007 | 124/222 | Telecom | New racks, fiber path A/B, Cat6A, patch panels, LIU, labels/test records and existing Room 222 transfer work | 0 | Paul | 0 | B13-R7 | Closed | 0
13 | B13_Assessment | B13-P008 | 124/222 | Security | 124-CAM-01, card reader, electric strike, door position, motion sensor, existing security cabinet and VMS/PACS integration | 0 | Paul | 0 | B13-R8 | Closed | 0
14 | B13_Assessment | B14-P001 | 119 | Existing Condition | Room 119 walls, ceiling/deck, floor, door, adjacent conference/restroom/office spaces, rack location, pathways and penetrations | 0 | Paul | 0 | B14-R1/B14-R6 | Closed | 0
14 | B13_Assessment | B14-P002 | B.01 | Existing Condition | Existing basement Tel/F Panel B.01, wall-mounted TE, patch panels, telco patch, plywood backboards, legacy Fiber LIU and pathways | 0 | Paul | 0 | B14-R1/B14-R3 | Closed | 0
14 | B13_Assessment | B14-P003 | B2 | Existing Condition | Existing basement telecom room B2 photo reference, equipment, pathways, power and protection-in-place needs | 0 | Paul | 0 | B14-R1/B14-R3 | Closed | 0
14 | B13_Assessment | B14-P004 | 119 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B14-R2 | Closed | 0
14 | B13_Assessment | B14-P005 | 119 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B14-R6 | Closed | 0
14 | B14_Assessment | B14-P006 | 119 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B14-R4 | Closed | 0
14 | B14_Assessment | B14-P007 | 119 | Electrical | B14-TR119A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B14-R5 | Closed | 0
14 | B14_Assessment | B14-P008 | 119/B.01 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 119-CAM-01 and existing B.01/B2 transfer work | 0 | Paul | 0 | B14-R7/B14-R8 | Closed | 0
15 | B14_Assessment | B15-P001 | 124A | Existing Condition | Room 124A walls, ceiling/deck, floor, door, adjacent Office 124/Office 109/HAC 123, rack location, pathways and penetrations | 0 | Paul | 0 | B15-R1/B15-R6 | Closed | 0
15 | B14_Assessment | B15-P002 | 222 | Existing Condition | Existing Tel Room 222 wall rack, Cisco switches, legacy patch panels, indoor AC unit, security cabinet, ground bar, plywood backboard and floor UPS | 0 | Paul | 0 | B15-R1/B15-R3 | Closed | 0
15 | B14_Assessment | B15-P003 | B01 | Existing Condition | Existing basement telecom/crossover B01, legacy 24-port patch panel, pathway, power and protection-in-place needs | 0 | Paul | 0 | B15-R1/B15-R3 | Closed | 0
15 | B14_Assessment | B15-P004 | 124A | Hazardous Materials | First-level abatement-related materials, lead-based paint/door frames, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B15-R2 | Closed | 0
15 | B14_Assessment | B15-P005 | 124A | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B15-R6 | Closed | 0
15 | B15_Assessment | B15-P006 | 124A | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B15-R4 | Closed | 0
15 | B15_Assessment | B15-P007 | 124A | Electrical | B15-TR124AA/AB panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B15-R5 | Closed | 0
15 | B15_Assessment | B15-P008 | 124A/222/B01 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 124A-CAM-1 and existing 222/B01 transfer work | 0 | Paul | 0 | B15-R7/B15-R8 | Closed | 0
16 | B15_Assessment | B16-P001 | 015 | Existing Condition | Room 015 walls, ceiling/deck, floor, door, adjacent Vacant 011/012/013, Stair 014, Water Heater 010, rack location, pathways and penetrations | 0 | Paul | 0 | B16-R1/B16-R3 | Closed | 0
16 | B15_Assessment | B16-P002 | 014 | Existing Condition | Existing Telecom Room 014 wall rack/TE, Cisco switch, legacy 12-port patch panel, Fiber LIU, floor UPS, plywood backboard and security cabinet | 0 | Paul | 0 | B16-R1/B16-R2 | Closed | 0
16 | B15_Assessment | B16-P003 | 015 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B16-R6 | Closed | 0
16 | B15_Assessment | B16-P004 | 015 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B16-R4 | Closed | 0
16 | B15_Assessment | B16-P005 | 015 | Electrical | B16-TR015A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B16-R5 | Closed | 0
16 | B16_Assessment | B16-P006 | 015/014 | Telecom | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records and existing Room 014 transfer work | 0 | Paul | 0 | B16-R7 | Closed | 0
16 | B16_Assessment | B16-P007 | 015/014 | Security | 015-CAM-1, card reader, electric strike, door position, motion sensor, existing security cabinet and VMS/PACS integration | 0 | Paul | 0 | B16-R8 | Closed | 0
16 | B16_Assessment | B16-P008 | All | Cable Tray / Pathway | Basement and first-level cable tray/pathway route, supports, fill, firestopping and seismic bracing | 0 | Paul | 0 | B16-R3/B16-R7 | Closed | 0
17 | B16_Assessment | B17-P001 | 118 | Existing Condition | Room 118 walls, ceiling/deck, floor, door, adjacent Lab/Freezer/Research/Corridor areas, rack location, pathways and penetrations | 0 | Paul | 0 | B17-R1/B17-R2 | Closed | 0
17 | B16_Assessment | B17-P002 | B35A | Existing Condition | Existing Telecom Closet B35A wall TE, SERTEX service ports, legacy patch panels, Cisco switches, security cabinet, plywood backboard, indoor AC and floor UPS | 0 | Paul | 0 | B17-R1/B17-R3 | Closed | 0
17 | B16_Assessment | B17-P003 | B29 Path | Pathway | Path to B29 4-inch PVC, fiber route, penetrations, handoff points and labeling | 0 | Paul | 0 | B17-R6/B17-R7 | Closed | 0
17 | B16_Assessment | B17-P004 | 118 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B17-R2 | Closed | 0
17 | B16_Assessment | B17-P005 | 118/B29 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop, including B29 pathway | 0 | Paul | 0 | B17-R6 | Closed | 0
17 | B17_Assessment | B17-P006 | 118 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B17-R4 | Closed | 0
17 | B17_Assessment | B17-P007 | 118 | Electrical | B17-TR118A/B panels, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B17-R5 | Closed | 0
17 | B17_Assessment | B17-P008 | 118/B35A/B29 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 118-CAM-01 and existing B35A transfer work | 0 | Paul | 0 | B17-R7/B17-R8 | Closed | 0
18 | B17_Assessment | B18-P001 | 110 | Existing Condition | Room 110 walls, ceiling/deck, floor, door, adjacent Corridor 121/Stair 122/Office 112, rack location, pathways and penetrations | 0 | Paul | 0 | B18-R1/B18-R2 | Closed | 0
18 | B17_Assessment | B18-P002 | 111B | Existing Condition | Existing TE 111B wall rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber housing | 0 | Paul | 0 | B18-R1/B18-R3 | Closed | 0
18 | B17_Assessment | B18-P003 | 213 | Existing Condition | Existing Closet 213 wall rack/TE, SERTEX service ports, Cisco switch, legacy Ortronics patch panels, security cabinet, plywood backboard and APC floor UPS | 0 | Paul | 0 | B18-R1/B18-R3 | Closed | 0
18 | B17_Assessment | B18-P004 | 110 | Hazardous Materials | First-level abatement/lead-paint areas, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B18-R2 | Closed | 0
18 | B17_Assessment | B18-P005 | 110 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B18-R6 | Closed | 0
18 | B18_Assessment | B18-P006 | 110 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B18-R4 | Closed | 0
18 | B18_Assessment | B18-P007 | 110 | Electrical | B18-TR110A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B18-R5 | Closed | 0
18 | B18_Assessment | B18-P008 | 110/111B/213 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 111A-CAM-01 and existing 111B/213 transfer work | 0 | Paul | 0 | B18-R7/B18-R8 | Closed | 0
20 | B18_Assessment | B20-P001 | 1B | Existing Condition | Office 1B wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B20-R1/B20-R3 | Closed | 0
20 | B18_Assessment | B20-P002 | 8A | Existing Condition | Existing Tel/Data Closet 8A open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard and cable entries | 0 | Paul | 0 | B20-R1/B20-R2 | Closed | 0
20 | B18_Assessment | B20-P003 | 8A | Existing Equipment | BIX blocks, Cisco switch, legacy Ortronics 48-port patch panel, UPS on ground and Fiber LIU on wall | 0 | Paul | 0 | B20-R2/B20-R5 | Closed | 0
20 | B18_Assessment | B20-P004 | 1B/8A | Pathway | 459 ft Level 1 cable tray route, sleeves, wall penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B20-R6/B20-R7 | Closed | 0
20 | B18_Assessment | B20-P005 | 1B | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and disconnect/access | 0 | Paul | 0 | B20-R5 | Closed | 0
20 | B20_Assessment | B20-P006 | 1B/8A | Telecom | TE01-1B-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B20-R2/B20-R8 | Closed | 0
20 | B20_Assessment | B20-P007 | All | Firestop | 4-inch speed sleeve, wall penetrations and fire caulk before/after photos | 0 | Paul | 0 | B20-R7 | Closed | 0
20 | B20_Assessment | B20-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B20-R8 | Closed | 0
21 | B20_Assessment | B21-P001 | 100A | Existing Condition | M&O Foreman Office 100A wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B21-R1/B21-R3 | Closed | 0
21 | B20_Assessment | B21-P002 | B1.TR | Existing Condition | Existing B21 basement B1.TR wall TE, legacy patch panels, Cisco switch, Fiber LIU, UPS on ground and cable entries | 0 | Paul | 0 | B21-R1/B21-R2 | Closed | 0
21 | B20_Assessment | B21-P003 | B05TR | Existing Condition | Existing B19 B05TR basement and first-level TE/equipment, APC floor UPS, Cisco switch, patch panels, Fiber LIU and pathways | 0 | Paul | 0 | B21-R1/B21-R4 | Closed | 0
21 | B20_Assessment | B21-P004 | 100A/B05TR/B1.TR | Pathway | 659 ft cable tray route, sleeves, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B21-R6/B21-R7 | Closed | 0
21 | B20_Assessment | B21-P005 | 100A | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B21-R5 | Closed | 0
21 | B21_Assessment | B21-P006 | 100A/B1.TR/B05TR | Telecom | TR01-104-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B21-R2/B21-R8 | Closed | 0
21 | B21_Assessment | B21-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B21-R7 | Closed | 0
21 | B21_Assessment | B21-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B21-R8 | Closed | 0
22 | B21_Assessment | B22-P001 | 102 | Existing Condition | Break Room 102 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B22-R1/B22-R3 | Closed | 0
22 | B21_Assessment | B22-P002 | 103 | Existing Condition | Existing Room 103 wall/wall-mount TE, APC UPS, Cisco switch, SERTEX utility service, legacy patch panel, Fiber LIU and cable entries | 0 | Paul | 0 | B22-R1/B22-R2 | Closed | 0
22 | B21_Assessment | B22-P003 | 103 / B19 | Existing Equipment | Ports 1-24 to Building 19 ports 73-96, active service labeling, utility service and handoff condition | 0 | Paul | 0 | B22-R8 | Closed | 0
22 | B21_Assessment | B22-P004 | 102/103 | Pathway | 139 ft first-floor cable tray route, sleeves, wall penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B22-R6/B22-R7 | Closed | 0
22 | B21_Assessment | B22-P005 | 102 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B22-R5 | Closed | 0
22 | B22_Assessment | B22-P006 | 102/103 | Telecom | TR01-102-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B22-R2/B22-R8 | Closed | 0
22 | B22_Assessment | B22-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B22-R7 | Closed | 0
22 | B22_Assessment | B22-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B22-R8 | Closed | 0
33 | B22_Assessment | B33-P001 | B23 | Existing Condition | EEO Manager Office B23 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B33-R1/B33-R3 | Closed | 0
33 | B22_Assessment | B33-P002 | B17 | Existing Condition | Existing Tel Closet B17 open TE cabinet, network door controller, indoor AC unit, plywood backboard, keypad, patch panel, ground bar and equipment box | 0 | Paul | 0 | B33-R1/B33-R2 | Closed | 0
33 | B22_Assessment | B33-P003 | B17 | Existing Equipment | Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, Fiber LIU, UPS on floor and cross-building port labels | 0 | Paul | 0 | B33-R2/B33-R8 | Closed | 0
33 | B22_Assessment | B33-P004 | B23/B17 | Pathway | 102 ft basement cable tray route, 4-inch sleeve, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B33-R6/B33-R7 | Closed | 0
33 | B22_Assessment | B33-P005 | B23 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B33-R5 | Closed | 0
33 | B33_Assessment | B33-P006 | B23/B17 | Telecom | TE01-B23-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing B17 equipment transfer | 0 | Paul | 0 | B33-R2/B33-R8 | Closed | 0
33 | B33_Assessment | B33-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B33-R7 | Closed | 0
33 | B33_Assessment | B33-P008 | B17/B23 | Security / Existing Devices | Existing cameras, network door controller, keypad and equipment box to remain/protect or be recabled | 0 | Paul | 0 | B33-R8 | Closed | 0
61 | B33_Assessment | B61-P001 | B13H-A | Existing Condition | Basement TR B13H-A walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B61-R1/B61-R2 | Closed | 0
61 | B33_Assessment | B61-P002 | 124 | Existing Condition | First-level TR 124 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B61-R1/B61-R4 | Closed | 0
61 | B33_Assessment | B61-P003 | 226 | Existing Condition | Second-level TR 226 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and riser penetrations | 0 | Paul | 0 | B61-R1/B61-R4 | Closed | 0
61 | B33_Assessment | B61-P004 | 137 / 137A | Existing Equipment | Existing server/demarc racks, APC UPS/PDU, Fujitsu equipment, patch panels, PACS/equipment racks and cable entries | 0 | Paul | 0 | B61-R3/B61-R7 | Closed | 0
61 | B33_Assessment | B61-P005 | All TRs | HVAC | IU/CU-0-01, IU/CU-1-01, IU/CU-2-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B61-R4 | Closed | 0
61 | B61_Assessment | B61-P006 | All TRs | Electrical | B61 telecom panels, PD panels, rack receptacles, UPS/PDU, breakers, SPDs, labels and grounding/bonding | 0 | Paul | 0 | B61-R5 | Closed | 0
61 | B61_Assessment | B61-P007 | All | Cable Tray / Firestop | Basement/first/second cable tray route, supports, seismic bracing, penetrations and before/after firestopping | 0 | Paul | 0 | B61-R6 | Closed | 0
61 | B61_Assessment | B61-P008 | All | Telecom / Security | Racks, Fiber LIU, Cat6A, patch panels, labels/test records, CCTV, PACS and existing equipment transfer work | 0 | Paul | 0 | B61-R7/B61-R8 | Closed | 0
62 | B62_TR_Assessment | B62-P001 | B24A | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0
62 | B62_TR_Assessment | B62-P002 | 125 | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0
62 | B62_TR_Assessment | B62-P003 | 225 | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0
62 | B62_TR_Assessment | B62-P004 | All | Firestop | Penetration/firestopping photo | 0 | Paul | 0 | B62-R2 | Closed | 0
70 | B70_TR_Assessment | B70-P001 | B27 | Existing Condition | Existing basement TR / utility condition | 0 | Paul | 0 | B70-R3 | Closed | 0
70 | B70_TR_Assessment | B70-P002 | 125A | Existing Condition | Existing first-floor TR condition | 0 | Paul | 0 | 0 | Closed | 0
70 | B70_TR_Assessment | B70-P003 | 262A | Existing Condition | Existing second-floor TR condition | 0 | Paul | 0 | 0 | Closed | 0
70 | B70_TR_Assessment | B70-P004 | All | Firestop | Penetration/firestopping photo | 0 | Paul | 0 | B70-R2 | Closed | 0
70 | B70_TR_Assessment | B70-P005 | All | HVAC | Cooling unit/condensate photo | 0 | Paul | 0 | B70-R1/B70-R5 | Closed | 0
78 | B70_TR_Assessment | B78-P001 | B30 | Existing Condition | Basement RM B30 walls, ceiling/deck, floor, door, racks/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B78-R1/B78-R6 | Closed | 0
78 | B70_TR_Assessment | B78-P002 | B35 | Existing Condition | Basement RM B35 and relationship to existing telecom room 15E; rack/equipment, pathway, power, HVAC and penetrations | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B70_TR_Assessment | B78-P003 | 1232 / 1234 | Existing Condition | First-level RM 1232/new TR and existing telecom room 1234 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B70_TR_Assessment | B78-P004 | 227A / 1234 | Existing Condition | Second-level RM 227A/new TR and existing telecom room 1234 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B70_TR_Assessment | B78-P005 | 342 / 353 | Existing Condition | Third-level RM 342/new TR and existing telecom room 353 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B78_Assessment | B78-P006 | 401 / 308A / 408A | Existing Condition | Fourth-level RM 401 and existing telecom rooms 308A/408A photo references, active equipment, cable paths and transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0
78 | B78_Assessment | B78-P007 | All | Cable Tray / Firestop | Basement through fourth-level cable tray routes, supports, seismic bracing, penetrations and before/after firestopping | 0 | Paul | 0 | B78-R6 | Closed | 0
78 | B78_Assessment | B78-P008 | All | Telecom / Security / HVAC | Racks, Fiber LIU, Cat6A, patch panels, UPS/PDU, labels/test records, CCTV, PACS, HVAC units and existing transfer work | 0 | Paul | 0 | B78-R4/B78-R7/B78-R8 | Closed | 0
80 | B78_Assessment | B80-P001 | 102 | Existing Condition | Room 102 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, fiber path A/B, cable tray and penetrations | 0 | Paul | 0 | B80-R1/B80-R4 | Closed | 0
80 | B78_Assessment | B80-P002 | 127A / 126 | Existing Condition | Existing Tel Closet/telecom room with plywood backboard, ground bar, patch panel, equipment box, two-post rack/wall TE and cable entries | 0 | Paul | 0 | B80-R1/B80-R2 | Closed | 0
80 | B78_Assessment | B80-P003 | 127A / 126 | Existing Equipment | Cisco switches, legacy Fiber LIU, Ortronics patch panels, Cat5e patch panel, APC floor UPS and active service labels | 0 | Paul | 0 | B80-R2/B80-R3 | Closed | 0
80 | B78_Assessment | B80-P004 | 102 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B80-R4 | Closed | 0
80 | B78_Assessment | B80-P005 | 102 | Electrical | B80-TR102A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B80-R5 | Closed | 0
80 | B80_Assessment | B80-P006 | All | Cable Tray / Firestop | Basement and first-level cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B80-R6 | Closed | 0
80 | B80_Assessment | B80-P007 | 102 / 127A | Telecom | New rack/future rack, Fiber LIU, Cat6A, patch panels, labels/test records and existing rack transfer work | 0 | Paul | 0 | B80-R7 | Closed | 0
80 | B80_Assessment | B80-P008 | 102 | Security | 102-CAM-1, card reader, electric strike, door position, motion sensor, existing security devices and VMS/PACS integration | 0 | Paul | 0 | B80-R8 | Closed | 0
82 | B80_Assessment | B82-P001 | 102 | Existing Condition | Room 102 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B82-R1/B82-R3 | Closed | 0
82 | B80_Assessment | B82-P002 | B01-A | Existing Condition | Existing first-level telecom room B01-A wall rack, Cisco switches, cable management, Ortronics patch panels, APC floor UPS and cable entries | 0 | Paul | 0 | B82-R1/B82-R2 | Closed | 0
82 | B80_Assessment | B82-P003 | 102 / B01-A | Pathway | 278 ft first-level cable tray route, 4-inch sleeve, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B82-R6/B82-R7 | Closed | 0
82 | B80_Assessment | B82-P004 | 102 | HVAC | IU-1-01/CU-1-01, condensate pump/path, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B82-R4 | Closed | 0
82 | B80_Assessment | B82-P005 | 102 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, B82-MDP/B82-P-EMER connections, grounding/bonding, SPD, labels and access | 0 | Paul | 0 | B82-R5 | Closed | 0
82 | B82_Assessment | B82-P006 | 102 / B01-A | Telecom | TR01-102-01 enclosure, cross-connect/cutover cabling, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B82-R2/B82-R8 | Closed | 0
82 | B82_Assessment | B82-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B82-R7 | Closed | 0
82 | B82_Assessment | B82-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B82-R8 | Closed | 0
BCH | B82_Assessment | BCH-P001 | 107 | Existing Condition | Room 107 walls, ceiling, floor, wall backing, clearances, existing devices, power source, cable path, and proposed TE/rack location | 0 | Paul | 0 | BCH-R1/BCH-R3 | Closed | 0
BCH | B82_Assessment | BCH-P002 | 107 | Electrical | Panel/source, receptacles, UPS/PDU location, grounding/bonding bar, labels and access clearance | 0 | Paul | 0 | BCH-R5 | Closed | 0
BCH | B82_Assessment | BCH-P003 | 107 | Telecom | 12RU enclosure or rack location, Fiber LIU, patch panel, network switch, Cat6A terminations, labels and test records | 0 | Paul | 0 | BCH-R3/BCH-R8 | Closed | 0
BCH | B82_Assessment | BCH-P004 | 107 | Pathway | Cable tray route, 4-inch sleeves, wall/floor penetrations, support points and 40% fill concerns | 0 | Paul | 0 | BCH-R6/BCH-R7 | Closed | 0
BCH | B82_Assessment | BCH-P005 | 107 | Firestop | Rated penetrations, fire caulk and temporary/final firestopping before/after photos | 0 | Paul | 0 | BCH-R7 | Closed | 0
BCH | BCH_Assessment | BCH-P006 | 107 | HVAC / Existing Environment | Existing room cooling/ventilation and ambient condition for TE equipment | 0 | Paul | 0 | BCH-R2/BCH-R5 | Closed | 0
BCH | BCH_Assessment | BCH-P007 | 107 | Security / CCTV | Camera location, existing/security devices, VMS integration, access conditions and protection-in-place | 0 | Paul | 0 | BCH-R8 | Closed | 0
BCH | BCH_Assessment | BCH-P008 | All | Off-site Coordination | Site access, staging, ICRA/dust control, work area barriers and temporary service conditions | 0 | Paul | 0 | BCH-R1/BCH-R4 | Closed | 0
MCR | BCH_Assessment | MCR-P001 | MCR 107 | Existing / New Condition | Full room envelope, doors, rated walls, ceiling/roof, floors, row layout, UPS-A/B, MDA/HDA, access points and cameras | 0 | Paul | 0 | MCR-R1/MCR-R6 | Closed | 0
MCR | BCH_Assessment | MCR-P002 | 031 | Fiber Entrance | Fiber Entrance Room 1, outlet locations 31-A/B/C/D, rack/cabinet location, sleeve/firestop and service entrance pathways | 0 | Paul | 0 | MCR-R3 | Closed | 0
MCR | BCH_Assessment | MCR-P003 | MDA-A/B | Rack / Fiber | MDA-A1/A2/A3 and MDA-B1/B2/B3 rack fronts/rears, LIUs, hybrid FOC, Cat6A to HDA, grounding and cable management | 0 | Paul | 0 | MCR-R3/MCR-R4 | Closed | 0
MCR | BCH_Assessment | MCR-P004 | HDA-A/B | Rack / Server Cabinets | HDA-A1/HDA-B1 front/rear, patch panels, HD LIUs, cabinet blanking panels, server cabinet airflow and labels | 0 | Paul | 0 | MCR-R3/MCR-R5 | Closed | 0
MCR | BCH_Assessment | MCR-P005 | Existing 107/137 | Existing Equipment | Existing rows 1-3 and B61 server cabinet transfer equipment, Cisco core, WAN aggregation, NetScout, Canoga, Ortronics, LIUs, UPS/PDU labels | 0 | Paul | 0 | MCR-R2 | Closed | 0
MCR | MCR_Assessment | MCR-P006 | MCR / Electrical | Electrical / UPS | UPS-A/B, switchboards, panels, ATS, generator tie, PDUs, rack receptacles, grounding, SPDs and load measurement labels | 0 | Paul | 0 | MCR-R4 | Closed | 0
MCR | MCR_Assessment | MCR-P007 | MCR / Mechanical | HVAC / Controls | CRAC units, condensate, controls/BACnet/BMS/FMS points, alarms, environmental monitoring and emergency power source | 0 | Paul | 0 | MCR-R5 | Closed | 0
MCR | MCR_Assessment | MCR-P008 | MCR / Life Safety | Fire / Security | Clean-agent cylinders/piping/nozzles, preaction/sprinkler, fire alarm, release/abort devices, cameras 07-CAM series, PACS/controller and door hardware | 0 | Paul | 0 | MCR-R6/MCR-R8 | Closed | 0
SITE | MCR_Assessment | SITE-P001 | Overall Site | Existing Conditions | Campus-wide route photos before excavation, including pavement, sidewalks, landscaping, parking, fire lanes and building entry areas | 0 | 0 | 0 | SITE-R1/SITE-R5 | Closed | 0
SITE | MCR_Assessment | SITE-P002 | THH #1-#19 | Structures | Each handhole/manhole/pullbox location, cover, label, depth, drainage, conduit entry, and final installed condition | 0 | 0 | 0 | SITE-R2/SITE-R8 | Closed | 0
SITE | MCR_Assessment | SITE-P003 | Ductbank | Pre-pour Inspection | Conduit count, separation, supports/spacers, depth, utility crossings, warning tape, pull strings and concrete encasement before pour | 0 | 0 | 0 | SITE-R1/SITE-R3 | Closed | 0
SITE | MCR_Assessment | SITE-P004 | Utility Crossings | Existing Utilities | Potholing/hand-dig photos showing electric, storm, sanitary, water, gas/unknown utilities and clearance to new ductbank | 0 | 0 | 0 | SITE-R1 | Closed | 0
SITE | MCR_Assessment | SITE-P005 | Building Tie-ins | Penetrations / Firestop | Exterior entry points, wall/floor penetrations, sleeves, firestop, weatherproofing and interior continuation to building TR/TE | 0 | 0 | 0 | SITE-R6 | Closed | 0
SITE | SITE_Assesment | SITE-P006 | Fiber Pull / Testing | Telecom | Fiber reels, pull setup, mandrel/rope, splice/termination points, labels, OTDR/power meter screenshots and OIT acceptance | 0 | 0 | 0 | SITE-R8 | Closed | 0
SITE | SITE_Assesment | SITE-P007 | Restoration | Civil | Asphalt/concrete trench patches, sidewalk panels, landscaping, turf, drainage, curb/edge details and final cleanup | 0 | 0 | 0 | SITE-R5/SITE-R7 | Closed | 0
SITE | SITE_Assesment | SITE-P008 | MCR / Provider Entrance | Critical Cutover | Provider handoff, WAN fiber route, temporary fiber, Path A/B into MCR and activation/cutover coordination photos | 0 | 0 | 0 | SITE-R4/SITE-R8 | Closed | 0
MAPPED READINESS SCORES — FORMULA-FED FROM BUILDING SHEETS
Building | Sheet | Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
01 | B01_Assessment | 107 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Green | New first-level TR with 161 total ports including allowance, dedicated cooling, UPS/PDU, B01-TR107A/B panels, cable tray, PACS/CCTV and fire/life-safety scope.
01 | B01_Assessment | B02 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Green | Existing basement telecom transition point; protect active services until transfer/cutover complete.
01 | B01_Assessment | 138 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Green | Existing first-level telecom transition point; protect active services and verify final condition.
01 | B01_Assessment | 282 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Green | Existing second-level telecom transition point; protect active services and verify final condition.
02 | B02_Assessment | 141 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with 354 total ports including allowance, 2 rack IDs, B02-TR141A/B panels, high cable tray volume and existing room transfer scope.
02 | B02_Assessment | 236 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR with approx. 345 total ports including allowance, B02-TR236A/B panels, camera/PACS and existing transition scope.
02 | B02_Assessment | 342 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Third-level TR with 388 total ports including allowance, B02-TR342A/B panels, camera/security and high WAO count.
02 | B02_Assessment | B-06 / existing rooms | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing telecom transition points; protect active services until transfer/cutover complete.
03 | B03_Assessment | 101E | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Primary first-level TR with 206 total ports including allowance, two rack IDs, B03-TR101CA/B panels, CU-01, 961 ft cable tray and existing 107/101C transfer scope.
03 | B03_Assessment | 107 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom transition point; protect active services until transfer/cutover complete.
03 | B03_Assessment | 101C | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing first-floor DMARC/telecom transition point; protect provider/fiber/active services and verify final condition.
03 | B03_Assessment | WAO Areas | 50% | 50% | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement and first-level WAO/WAP/camera recabling served from Room 101E.
04 | B04_Assessment | B05 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Two-rack basement TR; full field verification required.
04 | B04_Assessment | 141 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-floor TR with rated wall/door and future rack.
04 | B04_Assessment | 244A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-floor TR/panel scope; verify rack/equipment locations.
05 | B05_Assessment | 150 | 50% | 50% | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New 12RU TE; field verification required.
05 | B05_Assessment | 153-A | 50% | 50% | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing TE/legacy equipment transition point.
06 | B06_Assessment | B-01 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing equipment transition point; protect active services.
06 | B06_Assessment | 178 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-floor TR with new cooling and electrical scope.
06 | B06_Assessment | 233 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-floor TR/Data Closet with rated construction and future rack scope.
07 | B07_Assessment | B-18 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR; field verification required.
07 | B07_Assessment | 228A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-floor TR; rated wall/door and cooling coordination required.
08 | B08_Assessment | B-15 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing equipment transition point; protect active services.
08 | B08_Assessment | B12B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement office/TE ambiguity requires field verification.
08 | B08_Assessment | 2065A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New second-floor TR with two racks, cooling, rated work and possible abatement.
09 | B09_Assessment | B01 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR with existing equipment and multiple panel/cooling dependencies.
09 | B09_Assessment | 104B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with security/access control, cooling and rated wall/door coordination.
09 | B09_Assessment | 206A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR adjacent to Nursing Service with cooling, electrical and fire/life-safety coordination.
10 | B10_Assessment | 200A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Attic TR with rack/equipment, cooling, electrical, fire/life-safety and abatement coordination.
10 | B10_Assessment | B24 | 50% | 50% | N/A | 0.5 | N/A | Verify | 0.5 | Partial / Yellow | Normal electrical source coordination only.
10 | B10_Assessment | B25 | 50% | 50% | N/A | 0.5 | N/A | Verify | 0.5 | Partial / Yellow | Emergency electrical source coordination only.
12 | B12_Assessment | Fiber path B/1/2 | 60% | 50% | N/A | N/A | 0.6 | Verify | 0.55 | Partial / Yellow | Fiber-only pathway and cutover must be field verified.
12 | B12_Assessment | Existing rack/demarc - field verify | 50% | 50% | N/A | N/A | 0.6 | Verify | 0.53 | Partial / Yellow | Existing service point/termination requires field confirmation.
13 | B13_Assessment | 124 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with two racks, future rack, 240V UPS, cooling, access control and fire/life-safety coordination.
13 | B13_Assessment | 222 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing second-level tel room and transition point; protect active services until cutover complete.
14 | B14_Assessment | 119 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 240V UPS, cooling, access control, cable tray and fire/life-safety coordination.
14 | B14_Assessment | B.01 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement tel/fiber panel room and transition point; protect active services until cutover complete.
14 | B14_Assessment | B2 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom room reference; field verify scope and active status.
15 | B15_Assessment | 124A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 240V UPS, heat-pump cooling, access control, cable tray and fire/life-safety coordination.
15 | B15_Assessment | 222 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing second-level tel room and transition point; protect active services until cutover complete.
15 | B15_Assessment | B01 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom/crossover room; field verify scope and active status.
16 | B16_Assessment | 015 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New basement TR with one rack plus future rack, 240V UPS, cooling, access control, cable tray and fire/life-safety coordination.
16 | B16_Assessment | 014 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom room and transition point; protect active services until cutover complete.
17 | B17_Assessment | 118 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 208V UPS, cooling, access control, 517 ft cable tray and B29 service coordination.
17 | B17_Assessment | B35A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom closet and transition point; protect active services until cutover complete.
17 | B17_Assessment | B29 Path | 50% | 50% | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Building 29 served from B17; verify pathway, fiber, labeling, test records and PMIS mapping.
18 | B18_Assessment | 110 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 208V UPS, cooling, access control, 315 ft cable tray and fire/life-safety coordination.
18 | B18_Assessment | 111B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing first-level TE and transition point; protect active services until cutover complete.
18 | B18_Assessment | 213 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing second-level telecom closet and transition point; protect active services until cutover complete.
20 | B20_Assessment | 1B | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level Office TE with 12RU wall enclosure, UPS/PDU, 459 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
20 | B20_Assessment | 8A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Tel/Data Closet and transition point; protect active services until cutover complete.
21 | B21_Assessment | 100A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TE with 12RU wall enclosure, UPS/PDU, 659 ft cable tray, fiber/copper cutover and B19/B21 room naming coordination.
21 | B21_Assessment | B1.TR | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Building 21 basement telecom transition point; protect active services until cutover complete.
21 | B21_Assessment | B05TR | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Building 19 telecom transition point tied into Building 21 scope; confirm shared service boundary.
22 | B22_Assessment | 102 | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level Break Room TE with 12RU wall enclosure, UPS/PDU, 139 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
22 | B22_Assessment | 103 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing wall/wall-mount TE and transition point; protect active services until cutover complete.
33 | B33_Assessment | B23 | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New basement office TE with 12RU wall enclosure, UPS/PDU, 102 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
33 | B33_Assessment | B17 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Tel Closet and transition point; protect active services until cutover complete.
61 | B61_Assessment | B13H-A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR with 142 total ports including allowance, dedicated cooling, UPS/PDU, cable tray and fire/life-safety scope.
61 | B61_Assessment | 124 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with dedicated cooling, UPS/PDU, cable tray and potential electrical room-name mapping issue.
61 | B61_Assessment | 226 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR with 172 total ports including allowance, dedicated cooling, UPS/PDU and riser/firestop coordination.
61 | B61_Assessment | 137 / 137A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing demarc/server room inventory; protect active services until cutover and acceptance complete.
62 | B62_TR_Assessment | B24A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
62 | B62_TR_Assessment | 125 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
62 | B62_TR_Assessment | 225 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
70 | B62_TR_Assessment | B27 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
70 | B62_TR_Assessment | 125A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
70 | B62_TR_Assessment | 262A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0
70 | B62_TR_Assessment | SOURCE / DRAWING REVIEW NOTES | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Source package | 518-22-700.Bedford.EHRM.IFC.B70.20260316.pdf | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | TR locations identified | B27 basement, 125A first floor, 262A second floor based on architectural, fire protection, mechanical, and telecom drawing references. | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Fire protection basis | Building 70 is fully sprinklered. TRs require sprinkler modifications, fire alarm devices, extinguisher coverage within 75 feet, and firestopping at penetrations. | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | HVAC basis | New indoor units, condensate routing, thermostat, and BACnet adapter are noted for TR spaces; emergency power and operational continuity should be field verified. | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Telecom basis | TR rack elevations show 1 rack plus future rack at B-27, 125-A, and 262-A with UPS/PDU/cable management/grounding requirements. | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Based on the Building 70 IFC review, the telecom scope is very similar to Building 62, but Building 70 appears to have three TRs (B27, 125A, and 262A) instead of a single room. The project introduces new racks, UPS equipment, dedicated cooling, fire alarm modifications, sprinkler modifications, grounding, cable management, and access control while maintaining hospital operations. | Telecom Room Build | Not Started | 0 | 0 | 🟡 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Building 70 – Telecom Room Infrastructure Scope | UPS Installation | Not Started | 1 | 0 | 🟢 | -1 | 0 | 0 | 0
70 | B62_TR_Assessment | Existing Conditions Survey | Firestopping | Not Started | 1 | 0 | 🟢 | -1 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify existing conditions of TR-B27, TR-125A, and TR-262A. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Document existing racks, power, HVAC, fire protection, grounding, and pathway systems. | 13. OIT ACTIVATION READINESS | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Photograph all existing conditions. | Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref. | 0 | 0
70 | B62_TR_Assessment | Verify existing active services and identify systems requiring uninterrupted operation. | Telecom Room Complete | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify room dimensions and equipment clearances. | Rack Installed | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Architectural | UPS Operational | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Prepare rooms for new telecom infrastructure. | National OIT Approval | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Patch and repair walls, ceilings, and penetrations as required. | Local OIT Ready | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Maintain or restore all fire-rated assemblies. | Activation Scheduled | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify door hardware, access control, and room security. | OIT Readiness | 0% |  | 0 | Success: Required OIT activation prerequisites are complete or formally coordinated. | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Label rooms and equipment per VA standards. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Fire Protection | Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence | 0 | 0
70 | B62_TR_Assessment | Verify sprinkler coverage within each TR. | Cable Tray | Not Started | No | No | No | Pending | 0 | 0 | 0
70 | B62_TR_Assessment | Reconfigure sprinkler piping and heads where required. | Firestop System | Not Started | No | No | No | Pending | 0 | 0 | 0
70 | B62_TR_Assessment | Verify no obstructions to sprinkler discharge. | HVAC Equipment | Not Started | No | No | No | Pending | 0 | 0 | 0
70 | B62_TR_Assessment | Provide fire extinguisher cabinet and clean-agent or CO₂ extinguisher within 75 feet of each TR. | Electrical Equipment | Not Started | No | No | No | Pending | 0 | 0 | 0
70 | B62_TR_Assessment | Firestop all penetrations through rated assemblies. | Inspection Compliance | 0% | 0 | 0 | Success: Installed materials match approved submittals and deficiencies are documented. | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify compliance with NFPA 13 and VA Fire Protection Design Manual requirements. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Fire Alarm | Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause | 0 | 0
70 | B62_TR_Assessment | Verify smoke detection coverage. | Telecom | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0
70 | B62_TR_Assessment | Verify horn/strobe coverage. | Mechanical | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0
70 | B62_TR_Assessment | Coordinate relocation or addition of devices as required. | Firestop | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0
70 | B62_TR_Assessment | Verify monitoring and reporting through existing fire alarm systems. | Contractor Performance | 0% | 0 | 0 | Success: Actual production is on or above baseline, or delay cause is documented. | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Test and document final operation. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Mechanical / HVAC | Requirement | Status | Required | Complete | Score | Comments | Evidence Ref. | 0 | 0
70 | B62_TR_Assessment | Verify dedicated cooling units serving each telecom room. | QA/QC Complete | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify thermostat installation. | Deficiencies Closed | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify BACnet integration and controls. | OIT Ready | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify condensate routing and drainage. | Documentation Complete | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify emergency power requirements for cooling equipment. | Recommended for Acceptance | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify continuous cooling capability during hospital operations. | Acceptance Readiness | 0% | 0 | 0 | Success: Building is ready for turnover when all required gates are complete. | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Perform startup and commissioning. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Electrical | Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify new electrical distribution serving telecom equipment. | Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify dedicated panel assignments. | Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify UPS installation and ratings. | Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify rack power distribution units. | Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify emergency power source. | Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify grounding and bonding requirements. | Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Verify circuit identification and labeling. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Telecommunications | Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Install and/or verify new equipment racks. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B62_TR_Assessment | Install vertical and horizontal cable management. | Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal | 0
70 | B62_TR_Assessment | Install grounding busbars. | Approved Submittals | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Install fiber termination shelves. | ICRA / PCRA | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Install patch panels. | QA/QC Reports | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Verify Cat6A and fiber terminations. | Firestopping | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Verify cable labeling. | Cable Tests | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B62_TR_Assessment | Test and certify all copper and fiber cabling. | OIT Acceptance | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B70_TR_Assessment | Verify compliance with OIT standards. | Photos | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0
70 | B70_TR_Assessment | Security | Requirement | What it Means | 0 | 0 | Verification | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify PACS access control for all TR doors. | ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. | 0 | 0 | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify card reader operation. | QA/QC Reports | Contractor quality inspections have been completed and documented. | 0 | 0 | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify door position monitoring. | Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. | 0 | 0 | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify camera coverage where required. | Cable Tests | All network, fiber, and communication cabling has passed required testing. | 0 | 0 | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify integration with existing VA security systems. | OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. | 0 | 0 | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Operational Risk Review | Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. | 0 | 0 | Walk the space and confirm all critical deficiencies have been corrected prior to turnover. | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Identify systems requiring uninterrupted operation. | Open Gate Count | 800% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Develop cutover strategy. | Gate Completion | 0 / 8 Complete | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Review outage requirements with VA OIT. | Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN. | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Review shutdown requirements with facilities staff. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Verify no active services are removed before migration. | Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW") | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Commissioning & Acceptance | Recommended Payment | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | HVAC commissioning. | ☐ Full | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Electrical commissioning. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Telecom testing and certification. | ☐ Partial | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Fire alarm testing. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Fire protection testing. | ☐ Withhold | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Security testing. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Final owner acceptance walkthrough. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Turnover documentation. | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | Owner Risks Identified | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | B70_TR_Assessment | High Risk | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | B70_TR_Assessment | B30 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR with 342 total ports including allowance, dedicated cooling, UPS/PDU and 1,702 ft basement cable tray scope.
78 | B70_TR_Assessment | B35 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR/closet with 70 total ports including allowance and active transition scope.
78 | B70_TR_Assessment | 1232 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with 444 total ports including allowance and high active port count.
78 | B70_TR_Assessment | 227A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR with 383 total ports including allowance and riser/firestop coordination.
78 | B78_Assessment | 342 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Third-level TR with 318 total ports including allowance and two-rack configuration.
78 | B78_Assessment | 401 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Fourth-level TR with 135 total ports including allowance and existing 308A/408A transition points.
78 | B78_Assessment | Existing rooms | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing telecom room inventory; protect active services until cutover and acceptance complete.
80 | B80_Assessment | 102 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with 215 total ports including allowance, dedicated cooling, UPS/PDU, cable tray, PACS/CCTV and fire/life-safety scope.
80 | B80_Assessment | 127A / 126 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing telecom transition point; protect active services until cutover complete and confirm room-number mapping.
82 | B82_Assessment | 102 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TE/telecom room with 12RU wall enclosure, UPS/PDU, dedicated cooling shown, 278 ft cable tray and 40 total ports including allowance.
82 | B82_Assessment | B01-A | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing first-level telecom room and transition point; protect active services until cutover complete.
BCH | BCH_Assessment | 107 | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | BCH first-level Room 107 telecom scope; verify final TE versus telecom room configuration, power, pathway, firestopping and active service transition.
BCH | BCH_Assessment | 00 / 107 | 50% | 50% | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Rack/elevation reference requiring confirmation before turnover and PMIS import.
MCR | MCR_Assessment | 107 / MCR | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New critical MCR facility with full architectural/civil/structural/MEP/FP/telecom/security scope; not construction-ready until coordination and commissioning plan are verified.
MCR | MCR_Assessment | 031 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Fiber Entrance Room 1 schedule and camera/data points require field verification and firestop/pathway coordination.
MCR | MCR_Assessment | MDA-A/B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New main distribution rows; A/B fiber diversity and rack/PDU mapping are critical.
MCR | MCR_Assessment | HDA-A/B | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New horizontal distribution/server cabinet rows; airflow, patching, labeling and redundancy must be validated.
MCR | MCR_Assessment | Existing 107/137 | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing MCR/server equipment transition point; protect active service until final activation.
SITE | SITE_Assesment | Overall Site | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Campus-wide fiber backbone is not construction-ready until utility locates, path routing, inspection holds and phasing plan are confirmed.
SITE | SITE_Assesment | Path A/B Backbone | 50% | 50% | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Redundant A/B path separation, conduit counts and T-601 one-line coordination require field verification.
SITE | SITE_Assesment | THH / Manholes | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | THH #1-#19 and locking manholes/pullboxes need inventory, labels, photos and acceptance.
SITE | SITE_Assesment | Building Tie-ins | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Building T-101 continuation, penetration/firestop and fiber acceptance must match each building assessment.
SITE | SITE_Assesment | MCR / Provider Entrance | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Provider fiber, temporary fiber and new MCR activation sequence are critical path items.
B01_Assessment
MAPPED DISCIPLINE STATUS ITEMS — FORMULA-FED FROM BUILDING SHEETS | B01_Assessment
Building | B01_Assessment | Discipline | Room | Overall | Notes | Source Row
01 | B01_Assessment | Fire | 107 | Verify | Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems. | B01_Assessment!A24:J24
01 | B01_Assessment | Fire | B02 | Verify | Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | B01_Assessment!A25:J25
01 | B01_Assessment | Fire | 138 | Verify | Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes. | B01_Assessment!A26:J26
01 | B01_Assessment | Fire | 282 | Verify | Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place. | B01_Assessment!A27:J27
01 | B01_Assessment | HVAC | 107 | Verify | Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup. | B01_Assessment!A31:J31
01 | B01_Assessment | HVAC | B02 | Verify | Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration. | B01_Assessment!A32:J32
01 | B01_Assessment | HVAC | 138 | Verify | Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear. | B01_Assessment!A33:J33
01 | B01_Assessment | HVAC | 282 | Verify | Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating. | B01_Assessment!A34:J34
01 | B01_Assessment | Electrical | 107 | Verify | Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation. | B01_Assessment!A38:J38
01 | B01_Assessment | Electrical | B02 | Verify | Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements. | B01_Assessment!A39:J39
01 | B01_Assessment | Electrical | 138 | Verify | Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition. | B01_Assessment!A40:J40
01 | B01_Assessment | Electrical | 282 | Verify | Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope. | B01_Assessment!A41:J41
01 | B01_Assessment | Telecom | 107 | Verify | 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1. | B01_Assessment!A45:J45
01 | B01_Assessment | Telecom | B02 | Verify | Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan. | B01_Assessment!A46:J46
01 | B01_Assessment | Telecom | 138 | Verify | Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence. | B01_Assessment!A47:J47
01 | B01_Assessment | Telecom | 282 | Verify | Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway. | B01_Assessment!A48:J48
01 | B01_Assessment | Security | 107 | Verify | Electrical/telecom plans show new access control, power supply/battery backup for PACS, HDP12/FIPS-compliant PIV-ready card reader with PIN pad, and camera 107-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration and door hardware coordination. | B01_Assessment!A52:J52
01 | B01_Assessment | Security | B02 | Verify | Verify existing security/CCTV equipment and any retained cameras. Maintain camera angles where existing security cameras are recabled. | B01_Assessment!A53:J53
01 | B01_Assessment | Security | 138 | Verify | Verify existing security/access conditions and protection-in-place during rack transfer. | B01_Assessment!A54:J54
01 | B01_Assessment | Security | 282 | Verify | Verify second-level existing security/CCTV impacts during cabling and equipment transfer. | B01_Assessment!A55:J55
02 | B01_Assessment | Fire | 141 | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. | B02_Assessment!A25:J25
02 | B01_Assessment | Fire | 236 | Verify | Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping. | B02_Assessment!A26:J26
02 | B01_Assessment | Fire | 342 | Verify | Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping. | B02_Assessment!A27:J27
02 | B01_Assessment | Fire | B-06 / existing rooms | Verify | Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | B02_Assessment!A28:J28
02 | B01_Assessment | HVAC | 141 | Verify | Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms. | B02_Assessment!A32:J32
02 | B01_Assessment | HVAC | 236 | Verify | Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm. | B02_Assessment!A33:J33
02 | B01_Assessment | HVAC | 342 | Verify | Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration. | B02_Assessment!A34:J34
02 | B01_Assessment | HVAC | B-06 / existing rooms | Verify | Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete. | B02_Assessment!A35:J35
02 | B01_Assessment | Electrical | 141 | Verify | Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels. | B02_Assessment!A39:J39
02 | B01_Assessment | Electrical | 236 | Verify | Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping. | B02_Assessment!A40:J40
02 | B01_Assessment | Electrical | 342 | Verify | Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits. | B02_Assessment!A41:J41
02 | B01_Assessment | Electrical | B-06 / existing rooms | Verify | Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs. | B02_Assessment!A42:J42
02 | B01_Assessment | Telecom | 141 | Verify | 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray. | B02_Assessment!A46:J46
02 | B01_Assessment | Telecom | 236 | Verify | 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope. | B02_Assessment!A47:J47
02 | B01_Assessment | Telecom | 342 | Verify | 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count. | B02_Assessment!A48:J48
02 | B01_Assessment | Telecom | B-06 / existing rooms | Verify | Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover. | B02_Assessment!A49:J49
02 | B01_Assessment | Security | 141 | Verify | Plans show 174-CAM-01 associated with the first-level TR area and PACS/security requirements. Verify camera/VMS integration, access controller/power supply, CR/RX/DC/ES/MD and door hardware. | B02_Assessment!A53:J53
02 | B02_Assessment | Security | 236 | Verify | Plans show 236-CAM-01. Verify camera/VMS integration, access control, door hardware, motion/detection devices and power. | B02_Assessment!A54:J54
02 | B02_Assessment | Security | 342 | Verify | Plans show 342-CAM-01 and 342A-CK-A. Verify camera/VMS integration and access control/security rough-in. | B02_Assessment!A55:J55
02 | B02_Assessment | Security | B-06 / existing rooms | Verify | Maintain existing camera angles when re-cabling and protect existing PACS/equipment racks during transfer. | B02_Assessment!A56:J56
03 | B02_Assessment | Fire | 101E | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. | B03_Assessment!A24:J24
03 | B02_Assessment | Fire | 107 | Verify | Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse. | B03_Assessment!A25:J25
03 | B02_Assessment | Fire | 101C | Verify | Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer. | B03_Assessment!A26:J26
03 | B02_Assessment | Fire | WAO Areas | Verify | Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations. | B03_Assessment!A27:J27
03 | B02_Assessment | HVAC | 101E | Verify | Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm. | B03_Assessment!A31:J31
03 | B02_Assessment | HVAC | 107 | Verify | Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete. | B03_Assessment!A32:J32
03 | B02_Assessment | HVAC | 101C | Verify | Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains. | B03_Assessment!A33:J33
03 | B02_Assessment | HVAC | WAO Areas | N/A | No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements. | B03_Assessment!A34:J34
03 | B02_Assessment | Electrical | 101E | Verify | Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements. | B03_Assessment!A38:J38
03 | B02_Assessment | Electrical | 107 | Verify | Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements. | B03_Assessment!A39:J39
03 | B02_Assessment | Electrical | 101C | Verify | Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer. | B03_Assessment!A40:J40
03 | B02_Assessment | Electrical | WAO Areas | Verify | Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations. | B03_Assessment!A41:J41
03 | B02_Assessment | Telecom | 101E | Verify | 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2. | B03_Assessment!A45:J45
03 | B02_Assessment | Telecom | 107 | Verify | Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover. | B03_Assessment!A46:J46
03 | B02_Assessment | Telecom | 101C | Verify | Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted. | B03_Assessment!A47:J47
03 | B02_Assessment | Telecom | WAO Areas | Verify | Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced. | B03_Assessment!A48:J48
03 | B02_Assessment | Security | 101E | Verify | Plans require PACS for TR doors and electrical details include access-controlled door rough-in. Verify access controller, power supply/battery backup, CR/RX/DC/ES/MD devices, reader, strike and door hardware coordination. | B03_Assessment!A52:J52
03 | B03_Assessment | Security | 101C | Verify | Enlarged plan and schedule identify 101C-CAM-01 and 101C-CK-A. Verify camera/VMS integration, existing camera angles and protection-in-place. | B03_Assessment!A53:J53
03 | B03_Assessment | Security | 107 | Verify | Verify existing security/CCTV/PACS impacts during basement telecom room transfer. | B03_Assessment!A54:J54
03 | B03_Assessment | Security | WAO Areas | Verify | Maintain existing camera angles when re-cabling; verify WAP/security/clock/Centrak devices are relabeled and tested. | B03_Assessment!A55:J55
04 | B03_Assessment | Fire | B05 | Verify | Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning. | B04_Assessment!A22:J22
04 | B03_Assessment | Fire | 141 | Verify | FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies. | B04_Assessment!A23:J23
04 | B03_Assessment | Fire | 244A | Verify | Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations. | B04_Assessment!A24:J24
04 | B03_Assessment | HVAC | B05 | Verify | Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up. | B04_Assessment!A28:J28
04 | B03_Assessment | HVAC | 141 | Verify | Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control. | B04_Assessment!A29:J29
04 | B03_Assessment | HVAC | 244A | Verify | Verify cooling unit, routing, condensate, controls, and emergency/backup power path. | B04_Assessment!A30:J30
04 | B03_Assessment | Electrical | B05 | Verify | Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits. | B04_Assessment!A34:J34
04 | B03_Assessment | Electrical | 141 | Verify | Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting. | B04_Assessment!A35:J35
04 | B03_Assessment | Electrical | 244A | Verify | Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source. | B04_Assessment!A36:J36
04 | B03_Assessment | Telecom | B05 | Verify | New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. | B04_Assessment!A40:J40
04 | B03_Assessment | Telecom | 141 | Verify | New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. | B04_Assessment!A41:J41
04 | B03_Assessment | Telecom | 244A | Verify | TR/panel identified; verify rack elevation and pathway details against 04T sheets. | B04_Assessment!A42:J42
04 | B04_Assessment | Security | B05 | Verify | Verify access-controlled TR door, camera, and VMS/PACS integration. | B04_Assessment!A46:J46
04 | B04_Assessment | Security | 141 | Verify | Architectural notes require door/access control coordination; verify card reader/electric strike rough-in. | B04_Assessment!A47:J47
04 | B04_Assessment | Security | 244A | Verify | Verify room security details and device integration with VA systems. | B04_Assessment!A48:J48
05 | B04_Assessment | Fire | 150 | Verify | Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts. | B05_Assessment!A20:J20
05 | B04_Assessment | Fire | 153-A | Verify | Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling. | B05_Assessment!A21:J21
05 | B04_Assessment | HVAC | 150 | N/A | Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling. | B05_Assessment!A25:J25
05 | B04_Assessment | HVAC | 153-A | N/A | Existing wall/wall-mount TE area; verify existing environmental conditions during field survey. | B05_Assessment!A26:J26
05 | B04_Assessment | Electrical | 150 | Verify | 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source. | B05_Assessment!A30:J30
05 | B04_Assessment | Electrical | 153-A | Verify | Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover. | B05_Assessment!A31:J31
05 | B04_Assessment | Telecom | 150 | Verify | New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU. | B05_Assessment!A35:J35
05 | B05_Assessment | Telecom | 153-A | Verify | Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records. | B05_Assessment!A36:J36
05 | B05_Assessment | Security | 150 | Verify | Project general scope includes CCTV and PACS for telecom spaces; verify whether TE location receives camera/access control or is served by existing room controls. | B05_Assessment!A40:J40
05 | B05_Assessment | Security | 153-A | Verify | Verify existing security protection and whether access-control work is needed for existing TE area. | B05_Assessment!A41:J41
06 | B05_Assessment | Fire | B-01 | Verify | Existing equipment area; verify no cabling penetrations are left unsealed. | B06_Assessment!A22:J22
06 | B05_Assessment | Fire | 178 | Verify | Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs. | B06_Assessment!A23:J23
06 | B05_Assessment | Fire | 233 | Verify | Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft. | B06_Assessment!A24:J24
06 | B05_Assessment | HVAC | B-01 | Verify | Verify basement equipment environmental condition and any heat/load issues during cutover. | B06_Assessment!A28:J28
06 | B05_Assessment | HVAC | 178 | Verify | Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route. | B06_Assessment!A29:J29
06 | B05_Assessment | HVAC | 233 | Verify | Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls. | B06_Assessment!A30:J30
06 | B05_Assessment | Electrical | B-01 | Verify | Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements. | B06_Assessment!A34:J34
06 | B05_Assessment | Electrical | 178 | Verify | Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation. | B06_Assessment!A35:J35
06 | B05_Assessment | Electrical | 233 | Verify | Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power. | B06_Assessment!A36:J36
06 | B05_Assessment | Telecom | B-01 | Verify | Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS. | B06_Assessment!A40:J40
06 | B05_Assessment | Telecom | 178 | Verify | Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification. | B06_Assessment!A41:J41
06 | B05_Assessment | Telecom | 233 | Verify | Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | B06_Assessment!A42:J42
06 | B06_Assessment | Security | B-01 | Verify | Verify existing basement access/security while protecting active equipment. | B06_Assessment!A46:J46
06 | B06_Assessment | Security | 178 | Verify | Electrical enlarged plan references existing card reader to remain/protect in place and new tri-tech motion sensor; verify PACS/CCTV integration. | B06_Assessment!A47:J47
06 | B06_Assessment | Security | 233 | Verify | Verify door hardware/access control, motion sensor, camera, and VA security integration. | B06_Assessment!A48:J48
07 | B06_Assessment | Fire | B-18 | Verify | Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination. | B07_Assessment!A20:J20
07 | B06_Assessment | Fire | 228A | Verify | Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications. | B07_Assessment!A21:J21
07 | B06_Assessment | HVAC | B-18 | Verify | Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm. | B07_Assessment!A25:J25
07 | B06_Assessment | HVAC | 228A | Verify | Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route. | B07_Assessment!A26:J26
07 | B06_Assessment | Electrical | B-18 | Verify | Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement. | B07_Assessment!A30:J30
07 | B06_Assessment | Electrical | 228A | Verify | Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels. | B07_Assessment!A31:J31
07 | B06_Assessment | Telecom | B-18 | Verify | 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU. | B07_Assessment!A35:J35
07 | B07_Assessment | Telecom | 228A | Verify | TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover. | B07_Assessment!A36:J36
07 | B07_Assessment | Security | B-18 | Verify | Verify access control, door hardware and CCTV/PACS integration for basement TR. | B07_Assessment!A40:J40
07 | B07_Assessment | Security | 228A | Verify | Architectural notes require access control hardware modifications at new rated door; verify card reader, electric strike, door position switch, motion sensor and camera. | B07_Assessment!A41:J41
08 | B07_Assessment | Fire | B-15 | Verify | Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected. | B08_Assessment!A22:J22
08 | B07_Assessment | Fire | B12B | Verify | Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers. | B08_Assessment!A23:J23
08 | B07_Assessment | Fire | 2065A | Verify | Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades. | B08_Assessment!A24:J24
08 | B07_Assessment | HVAC | B-15 | Verify | Verify existing environmental conditions and whether active legacy equipment remains during cutover. | B08_Assessment!A28:J28
08 | B07_Assessment | HVAC | B12B | Verify | Field verify whether TE equipment load requires cooling or if served by existing building HVAC. | B08_Assessment!A29:J29
08 | B07_Assessment | HVAC | 2065A | Verify | Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls. | B08_Assessment!A30:J30
08 | B07_Assessment | Electrical | B-15 | Verify | Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements. | B08_Assessment!A34:J34
08 | B07_Assessment | Electrical | B12B | Verify | Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel. | B08_Assessment!A35:J35
08 | B07_Assessment | Electrical | 2065A | Verify | Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope. | B08_Assessment!A36:J36
08 | B07_Assessment | Telecom | B-15 | Verify | Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS. | B08_Assessment!A40:J40
08 | B07_Assessment | Telecom | B12B | Verify | Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance. | B08_Assessment!A41:J41
08 | B07_Assessment | Telecom | 2065A | Verify | New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS. | B08_Assessment!A42:J42
08 | B08_Assessment | Security | B-15 | Verify | Verify existing basement access/security while protecting active equipment. | B08_Assessment!A46:J46
08 | B08_Assessment | Security | B12B | Verify | 45-minute door shown; verify access-control hardware applicability and whether TE is secured. | B08_Assessment!A47:J47
08 | B08_Assessment | Security | 2065A | Verify | Door schedule/hardware note requires coordination with electrical/access control; verify card reader, electric strike, door position, motion sensor, camera and VA integration. | B08_Assessment!A48:J48
09 | B08_Assessment | Fire | B01 | Verify | Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR. | B09_Assessment!A22:J22
09 | B08_Assessment | Fire | 104B | Verify | Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft. | B09_Assessment!A23:J23
09 | B08_Assessment | Fire | 206A | Verify | Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations. | B09_Assessment!A24:J24
09 | B08_Assessment | HVAC | B01 | Verify | Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms. | B09_Assessment!A28:J28
09 | B08_Assessment | HVAC | 104B | Verify | Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power. | B09_Assessment!A29:J29
09 | B08_Assessment | HVAC | 206A | Verify | Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power. | B09_Assessment!A30:J30
09 | B08_Assessment | Electrical | B01 | Verify | Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes. | B09_Assessment!A34:J34
09 | B08_Assessment | Electrical | 104B | Verify | Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits. | B09_Assessment!A35:J35
09 | B08_Assessment | Electrical | 206A | Verify | Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits. | B09_Assessment!A36:J36
09 | B08_Assessment | Telecom | B01 | Verify | Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover. | B09_Assessment!A40:J40
09 | B08_Assessment | Telecom | 104B | Verify | Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | B09_Assessment!A41:J41
09 | B08_Assessment | Telecom | 206A | Verify | Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | B09_Assessment!A42:J42
09 | B09_Assessment | Security | B01 | Verify | Enlarged plans show existing/new security boxes, network door controller, camera/security scope; verify PACS/CCTV integration and protection of active security systems. | B09_Assessment!A46:J46
09 | B09_Assessment | Security | 104B | Verify | First-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 104B camera designation; verify card reader, electric strike, door contact, motion and camera. | B09_Assessment!A47:J47
09 | B09_Assessment | Security | 206A | Verify | Second-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 206A camera designation; verify PACS/VMS integration and commissioning. | B09_Assessment!A48:J48
10 | B09_Assessment | Fire | 200A | Verify | Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping. | B10_Assessment!A22:J22
10 | B09_Assessment | Fire | B24 | Verify | Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place. | B10_Assessment!A23:J23
10 | B09_Assessment | Fire | B25 | Verify | Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment. | B10_Assessment!A24:J24
10 | B09_Assessment | HVAC | 200A | Verify | Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm. | B10_Assessment!A28:J28
10 | B09_Assessment | HVAC | B24 | N/A | No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work. | B10_Assessment!A29:J29
10 | B09_Assessment | HVAC | B25 | N/A | No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted. | B10_Assessment!A30:J30
10 | B09_Assessment | Electrical | 200A | Verify | Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels. | B10_Assessment!A34:J34
10 | B09_Assessment | Electrical | B24 | Verify | Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing. | B10_Assessment!A35:J35
10 | B09_Assessment | Electrical | B25 | Verify | Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required. | B10_Assessment!A36:J36
10 | B09_Assessment | Telecom | 200A | Verify | 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover. | B10_Assessment!A40:J40
10 | B09_Assessment | Telecom | B24 | Verify | Coordinate telecom power pathways through/source from basement electrical room if applicable. | B10_Assessment!A41:J41
10 | B09_Assessment | Telecom | B25 | Verify | Coordinate emergency source/backup power pathways for telecom equipment and cooling. | B10_Assessment!A42:J42
10 | B10_Assessment | Security | 200A | Verify | General scope requires PACS/CCTV for TR doors; verify door hardware, access controller, camera/VMS integration and any existing attic access/security constraints. | B10_Assessment!A46:J46
10 | B10_Assessment | Security | B24 | Verify | Verify security impact only if electrical source room access or devices are modified. | B10_Assessment!A47:J47
10 | B10_Assessment | Security | B25 | Verify | Verify emergency electrical room security impact if work requires access control changes. | B10_Assessment!A48:J48
12 | B10_Assessment | Fire | Fiber path B/1/2 | Verify | No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route. | B12_Assessment!A20:J20
12 | B10_Assessment | Fire | Existing rack/demarc - field verify | Verify | No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work. | B12_Assessment!A21:J21
12 | B10_Assessment | HVAC | Fiber path B/1/2 | N/A | No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment. | B12_Assessment!A25:J25
12 | B10_Assessment | HVAC | Existing rack/demarc - field verify | N/A | Field verify existing environmental conditions only if existing service point/equipment is accessed. | B12_Assessment!A26:J26
12 | B10_Assessment | Electrical | Fiber path B/1/2 | Verify | No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown. | B12_Assessment!A30:J30
12 | B10_Assessment | Electrical | Existing rack/demarc - field verify | Verify | Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling. | B12_Assessment!A31:J31
12 | B10_Assessment | Telecom | Fiber path B/1/2 | Verify | Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing. | B12_Assessment!A35:J35
12 | B12_Assessment | Telecom | Existing rack/demarc - field verify | Verify | 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only. | B12_Assessment!A36:J36
12 | B12_Assessment | Security | Fiber path B/1/2 | N/A / Verify | No new TR door or PACS/CCTV package shown for Building 12; verify security access only for work areas and existing equipment rooms. | B12_Assessment!A40:J40
12 | B12_Assessment | Security | Existing rack/demarc - field verify | N/A / Verify | Confirm access requirements to existing closet/demarc while protecting active operations. | B12_Assessment!A41:J41
13 | B12_Assessment | Fire | 124 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | B13_Assessment!A20:J20
13 | B12_Assessment | Fire | 222 | Verify | Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B13_Assessment!A21:J21
13 | B12_Assessment | HVAC | 124 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B13_Assessment!A25:J25
13 | B12_Assessment | HVAC | 222 | Verify | Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | B13_Assessment!A26:J26
13 | B12_Assessment | Electrical | 124 | Verify | Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements. | B13_Assessment!A30:J30
13 | B12_Assessment | Electrical | 222 | Verify | Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | B13_Assessment!A31:J31
13 | B12_Assessment | Telecom | 124 | Verify | 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B. | B13_Assessment!A35:J35
13 | B13_Assessment | Telecom | 222 | Verify | Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124. | B13_Assessment!A36:J36
13 | B13_Assessment | Security | 124 | Verify | Electrical enlarged plan shows security/access-control device callouts at Room 124 and 124-CAM-01 camera designation; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B13_Assessment!A40:J40
13 | B13_Assessment | Security | 222 | Verify | Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B13_Assessment!A41:J41
14 | B13_Assessment | Fire | 119 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | B14_Assessment!A22:J22
14 | B13_Assessment | Fire | B.01 | Verify | Existing basement tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B14_Assessment!A23:J23
14 | B13_Assessment | Fire | B2 | Verify | Existing basement telecom room; verify no unsealed penetrations remain after cable transfer or reuse. | B14_Assessment!A24:J24
14 | B13_Assessment | HVAC | 119 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 119 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B14_Assessment!A28:J28
14 | B13_Assessment | HVAC | B.01 | Verify | Existing Tel/F Panel room; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B14_Assessment!A29:J29
14 | B13_Assessment | HVAC | B2 | Verify | Existing telecom room reference; field verify cooling/ventilation and active equipment condition. | B14_Assessment!A30:J30
14 | B13_Assessment | Electrical | 119 | Verify | Electrical plan/schedules identify B14-TR119A/B, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and panel load measurement requirements. | B14_Assessment!A34:J34
14 | B13_Assessment | Electrical | B.01 | Verify | Existing basement wall-mounted TE/equipment area; verify power source, active equipment, UPS/PDU status, and transition requirements before disconnect or removal. | B14_Assessment!A35:J35
14 | B13_Assessment | Electrical | B2 | Verify | Existing telecom room photo reference; confirm power sources and any cutover requirements. | B14_Assessment!A36:J36
14 | B13_Assessment | Telecom | 119 | Verify | 14T-701 identifies Room 119 schedule: 44 WAO total, 29 active ports per survey, 76 total ports per schedule, and 84 total ports with 10% allowance. New Rack ID TR01-119-1 serves first and second level outlets with Fiber Path A/B. | B14_Assessment!A40:J40
14 | B13_Assessment | Telecom | B.01 | Verify | Existing Room B.01 equipment includes wall-mounted TE, Cisco switch/legacy patch panel, telco patch, plywood backboards, and legacy Fiber LIU; verify active services and transfer plan to Room 119. | B14_Assessment!A41:J41
14 | B13_Assessment | Telecom | B2 | Verify | Existing basement telecom room B2 is identified by photo reference; verify active devices, routing, and relation to B.01. | B14_Assessment!A42:J42
14 | B14_Assessment | Security | 119 | Verify | Telecom/electrical plans show 119-CAM-01 and security/access-control scope for Room 119; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B14_Assessment!A46:J46
14 | B14_Assessment | Security | B.01 | Verify | Verify whether existing security equipment remains, is relocated, or requires temporary protection during cutover. | B14_Assessment!A47:J47
14 | B14_Assessment | Security | B2 | Verify | Verify security/access conditions and whether any legacy security equipment is present. | B14_Assessment!A48:J48
15 | B14_Assessment | Fire | 124A | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | B15_Assessment!A22:J22
15 | B14_Assessment | Fire | 222 | Verify | Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B15_Assessment!A23:J23
15 | B14_Assessment | Fire | B01 | Verify | Existing basement telecom/crossover room; verify no unsealed penetrations remain after cable transfer or reuse. | B15_Assessment!A24:J24
15 | B14_Assessment | HVAC | 124A | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 124A and CU-1-01 outdoor heat-pump/A/C unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B15_Assessment!A28:J28
15 | B14_Assessment | HVAC | 222 | Verify | Existing Tel Room 222 is shown with existing/remain indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | B15_Assessment!A29:J29
15 | B14_Assessment | HVAC | B01 | Verify | Existing basement telecom/crossover space; verify environmental conditions and whether active equipment remains during cutover. | B15_Assessment!A30:J30
15 | B14_Assessment | Electrical | 124A | Verify | Electrical enlarged plans and schedules identify B15-TR124AA/AB, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and 30-day load measurement requirements. | B15_Assessment!A34:J34
15 | B14_Assessment | Electrical | 222 | Verify | Existing rack/equipment area; verify power source, active equipment, APC floor UPS status, and transition requirements before disconnect or removal. | B15_Assessment!A35:J35
15 | B14_Assessment | Electrical | B01 | Verify | Existing B-01 crossover; verify power sources and cutover needs for legacy patch panel/crossover. | B15_Assessment!A36:J36
15 | B14_Assessment | Telecom | 124A | Verify | 15T-701 identifies Room 109A schedule but field plan/electrical room callouts identify Telecom Room 124A; schedule has 62 WAO total, 76 active ports per survey, 101 total ports per schedule, and 111 total ports with 10% allowance. New Rack ID TR15-109A-01 serves basement, first and second level outlets. | B15_Assessment!A40:J40
15 | B14_Assessment | Telecom | 222 | Verify | Existing Room 222 equipment includes wall/wall-mounted TE, Cisco switches, legacy 48-port patch panels, ground bar, plywood backboard, security cabinet, and floor UPS; verify active services and transfer plan to Room 124A. | B15_Assessment!A41:J41
15 | B14_Assessment | Telecom | B01 | Verify | Existing B-01 crossover includes legacy 24-port patch panel; verify active devices, routing, and relation to Room 222 and Room 124A. | B15_Assessment!A42:J42
15 | B15_Assessment | Security | 124A | Verify | Telecom/electrical plans show 124A-CAM-1 and security/access-control scope for Room 124A; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B15_Assessment!A46:J46
15 | B15_Assessment | Security | 222 | Verify | Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B15_Assessment!A47:J47
15 | B15_Assessment | Security | B01 | Verify | Verify security/access conditions and whether any legacy security equipment is present. | B15_Assessment!A48:J48
16 | B15_Assessment | Fire | 015 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | B16_Assessment!A20:J20
16 | B15_Assessment | Fire | 014 | Verify | Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B16_Assessment!A21:J21
16 | B15_Assessment | HVAC | 015 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 015 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B16_Assessment!A25:J25
16 | B15_Assessment | HVAC | 014 | Verify | Existing Telecom Room 014; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B16_Assessment!A26:J26
16 | B15_Assessment | Electrical | 015 | Verify | Electrical plans/schedules identify B16-TR015A/B, 240V rack UPS requirements, rack receptacles, TR receptacles, lighting, access controller, CU-1-01, SPD requirements, existing panel demolition/replacement, and 30-day load measurement requirements. | B16_Assessment!A30:J30
16 | B15_Assessment | Electrical | 014 | Verify | Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | B16_Assessment!A31:J31
16 | B15_Assessment | Telecom | 015 | Verify | 16T-701 identifies Room 015-A schedule: 25 WAO total, 25 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. New Rack ID TR01-015-A-1 serves basement, first, second and attic level outlets. | B16_Assessment!A35:J35
16 | B16_Assessment | Telecom | 014 | Verify | Existing Room 014 equipment includes wall/TE rack, floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU; verify active services and transfer plan to Room 015. | B16_Assessment!A36:J36
16 | B16_Assessment | Security | 015 | Verify | Telecom/electrical plans show 015-CAM-1 and security/access-control scope for Room 015; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B16_Assessment!A40:J40
16 | B16_Assessment | Security | 014 | Verify | Existing security cabinet shown in Room 014; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B16_Assessment!A41:J41
17 | B16_Assessment | Fire | 118 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | B17_Assessment!A22:J22
17 | B16_Assessment | Fire | B35A | Verify | Existing telecom closet; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | B17_Assessment!A23:J23
17 | B16_Assessment | Fire | B29 Path | Verify | Verify firestopping at pathway penetrations between Building 17 and Building 29 and any rated floor/wall assemblies. | B17_Assessment!A24:J24
17 | B16_Assessment | HVAC | 118 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 118 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B17_Assessment!A28:J28
17 | B16_Assessment | HVAC | B35A | Verify | Existing B35A is shown with existing indoor AC unit; verify whether it remains active, is abandoned, or needs temporary protection during cutover. | B17_Assessment!A29:J29
17 | B16_Assessment | HVAC | B29 Path | N/A | No dedicated cooling expected for pathway; verify any equipment cabinets or active service locations in Building 29 if applicable. | B17_Assessment!A30:J30
17 | B16_Assessment | Electrical | 118 | Verify | Electrical plans/schedules identify B17-TR118A fed from BUS-B17-NPB1-R and B17-TR118B fed from BUS-B17-EQDP, with TR RM118 rack receptacles, 208V UPS/PDU equipment, CU-1-01, SPD requirements, and 30-day load measurement requirements. | B17_Assessment!A34:J34
17 | B16_Assessment | Electrical | B35A | Verify | Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. | B17_Assessment!A35:J35
17 | B16_Assessment | Electrical | B29 Path | Verify | Verify whether any Building 29 equipment or extension path requires power, grounding, bonding, or labeling tied back to B17 TR 118. | B17_Assessment!A36:J36
17 | B16_Assessment | Telecom | 118 | Verify | 17_29T-701 identifies Room 118 schedule: 113 WAO total, 67 active ports per survey, 154 total ports per schedule, and 169 total ports with 10% allowance. Rack ID TR17-118-1 serves basement, first, second-level outlets and Building 29 path. | B17_Assessment!A40:J40
17 | B16_Assessment | Telecom | B35A | Verify | Existing Room B35A equipment includes SERTEX utility service ports, legacy Ortronics patch panels, Cisco switches, wall-mounted TE, Fiber/legacy equipment, security cabinet, and floor UPS; verify active services and transfer plan to Room 118. | B17_Assessment!A41:J41
17 | B16_Assessment | Telecom | B29 Path | Verify | Building 29 is shown served from B17; verify fiber from Building 17 to Building 29, path to B29 4-inch PVC, outlet labels, test records and as-builts. | B17_Assessment!A42:J42
17 | B17_Assessment | Security | 118 | Verify | Telecom/electrical plans show 118-CAM-01 and security/access-control scope for Room 118; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B17_Assessment!A46:J46
17 | B17_Assessment | Security | B35A | Verify | Existing security cabinet shown in B35A; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B17_Assessment!A47:J47
17 | B17_Assessment | Security | B29 Path | Verify | Verify Building 29 pathway and any security scope tied into B17 TR 118/VMS/PACS. | B17_Assessment!A48:J48
18 | B17_Assessment | Fire | 110 | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | B18_Assessment!A22:J22
18 | B17_Assessment | Fire | 111B | Verify | Existing TE room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | B18_Assessment!A23:J23
18 | B17_Assessment | Fire | 213 | Verify | Existing second-level closet; verify protection-in-place and firestopping after transfer or abandonment. | B18_Assessment!A24:J24
18 | B17_Assessment | HVAC | 110 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 110 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | B18_Assessment!A28:J28
18 | B17_Assessment | HVAC | 111B | Verify | Existing TE 111B; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B18_Assessment!A29:J29
18 | B17_Assessment | HVAC | 213 | Verify | Existing Closet 213; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B18_Assessment!A30:J30
18 | B17_Assessment | Electrical | 110 | Verify | Electrical plans/schedules identify B18-TR110A/B, 208V rack UPS requirements, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and telecom panelboard schedule requirements. | B18_Assessment!A34:J34
18 | B17_Assessment | Electrical | 111B | Verify | Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. | B18_Assessment!A35:J35
18 | B17_Assessment | Electrical | 213 | Verify | Existing rack/equipment area; verify active equipment, APC UPS status, source circuits, SERTEX utility service and transfer requirements before disconnect/removal. | B18_Assessment!A36:J36
18 | B17_Assessment | Telecom | 110 | Verify | 18T-701 identifies RM 111A schedule: 86 WAO total, 61 active ports per survey, 122 ports per schedule, and 134 total ports with 10% allowance. New rack elevation is Room 110, 1 rack plus future, with UPS, Future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | B18_Assessment!A40:J40
18 | B17_Assessment | Telecom | 111B | Verify | Existing Room 111B equipment includes wall-mounted rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber optic housing; verify active services and transfer plan to Room 110. | B18_Assessment!A41:J41
18 | B17_Assessment | Telecom | 213 | Verify | Existing Room 213 equipment includes SERTEX utility service ports, Cisco switch, multiple legacy Ortronics patch panels, wall/wall-mount TE and APC floor UPS; verify active services and transfer plan to Room 110. | B18_Assessment!A42:J42
18 | B18_Assessment | Security | 110 | Verify | Telecom/electrical plans show 111A-CAM-01 and security/access-control scope for the new TR area; verify room naming, CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | B18_Assessment!A46:J46
18 | B18_Assessment | Security | 111B | Verify | Existing security cabinet shown in 111B; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B18_Assessment!A47:J47
18 | B18_Assessment | Security | 213 | Verify | Existing security cabinet shown in 213; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | B18_Assessment!A48:J48
20 | B18_Assessment | Fire | 1B | Verify | Cover sheet states Building 20 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. | B20_Assessment!A20:J20
20 | B18_Assessment | Fire | 8A | Verify | Existing closet; verify protection-in-place and firestopping after cable transfer or reuse. | B20_Assessment!A21:J21
20 | B18_Assessment | HVAC | 1B | N/A | Cover sheet states mechanical scope is excluded. Verify whether Office 1B ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | B20_Assessment!A25:J25
20 | B18_Assessment | HVAC | 8A | Verify | Existing Tel/Data Closet 8A includes indoor AC unit to remain/protect in place; verify operation during cutover and whether equipment remains after transition. | B20_Assessment!A26:J26
20 | B18_Assessment | Electrical | 1B | Verify | 20T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | B20_Assessment!A30:J30
20 | B18_Assessment | Electrical | 8A | Verify | Existing 8A elevation shows UPS on ground, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | B20_Assessment!A31:J31
20 | B18_Assessment | Telecom | 1B | Verify | 20T-701 identifies TE01-1B-1: 21 WAO total, 24 active ports per survey, 30 ports per schedule, 33 total ports with 10% allowance. Provide new wall-mount TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. | B20_Assessment!A35:J35
20 | B20_Assessment | Telecom | 8A | Verify | Existing Tel/Data Closet 8A contains open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy 48-port patch panel and Fiber LIU. Field verify all active services. | B20_Assessment!A36:J36
20 | B20_Assessment | Security | 1B | Verify | Building 20 does not appear to create a new TR door/PACS package. Verify any existing cameras/security devices in Office 1B and ensure no camera angle or VMS integration is disrupted. | B20_Assessment!A40:J40
20 | B20_Assessment | Security | 8A | Verify | Keynotes indicate existing cameras are to be retained and re-used/protected in place; verify existing security equipment and cabinet impacts during cutover. | B20_Assessment!A41:J41
21 | B20_Assessment | Fire | 100A | Verify | Cover sheet states Building 21_19 receives a Telecom Enclosure and fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. | B21_Assessment!A22:J22
21 | B20_Assessment | Fire | B1.TR | Verify | Existing B21 basement TR; verify protection-in-place and firestopping after cable transfer or reuse. | B21_Assessment!A23:J23
21 | B20_Assessment | Fire | B05TR | Verify | Existing B19 B05TR; verify protection-in-place and firestopping after cable transfer or reuse. | B21_Assessment!A24:J24
21 | B20_Assessment | HVAC | 100A | Verify | Mechanical sheets exist in index. Verify whether new TE heat load in Office 100A is supported by existing/new HVAC and whether any mechanical scope applies despite TE designation. | B21_Assessment!A28:J28
21 | B20_Assessment | HVAC | B1.TR | Verify | Existing B21 B1.TR; verify environmental conditions during cutover and whether legacy equipment remains active. | B21_Assessment!A29:J29
21 | B20_Assessment | HVAC | B05TR | Verify | Existing B19 B05TR; verify environmental conditions and whether equipment remains active during/after Building 21 transfer. | B21_Assessment!A30:J30
21 | B20_Assessment | Electrical | 100A | Verify | 21_19T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switches, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | B21_Assessment!A34:J34
21 | B20_Assessment | Electrical | B1.TR | Verify | Existing B21 B1.TR elevation shows UPS on ground, Cisco switch, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements. | B21_Assessment!A35:J35
21 | B20_Assessment | Electrical | B05TR | Verify | Existing B19 B05TR elevations show APC floor UPS, legacy patch panels, Cisco switch and Fiber LIU; verify power source, active equipment and transfer/retention requirements. | B21_Assessment!A36:J36
21 | B20_Assessment | Telecom | 100A | Verify | 21_19T-701 identifies RM 104 schedule: 90 WAO total, 67 active ports per survey, 119 ports per schedule, and 131 total ports with 10% allowance. 659 ft cable tray total: 63 ft basement and 596 ft first level. | B21_Assessment!A40:J40
21 | B20_Assessment | Telecom | B1.TR | Verify | Existing B21 B1.TR equipment includes multiple legacy patch panels, Cisco switch, UPS on ground, Fiber LIU and APC floor UPS; verify active services and transfer plan to new TE. | B21_Assessment!A41:J41
21 | B20_Assessment | Telecom | B05TR | Verify | Existing B19 B05TR equipment includes legacy Ortronics patch panels, Cisco switch, Fiber LIU and APC floor UPS; verify active services and whether B19/B21 devices are served from new enclosure. | B21_Assessment!A42:J42
21 | B21_Assessment | Security | 100A | Verify | Building 21_19 appears to create a TE enclosure rather than a full TR door/PACS package. Verify any existing cameras/security devices in Room 100A and ensure no camera angle or VMS integration is disrupted. | B21_Assessment!A46:J46
21 | B21_Assessment | Security | B1.TR | Verify | Verify any existing security device/cabinet impacts during cutover. | B21_Assessment!A47:J47
21 | B21_Assessment | Security | B05TR | Verify | Verify existing security/camera protection-in-place and any impact from B19/B21 shared telecom equipment. | B21_Assessment!A48:J48
22 | B21_Assessment | Fire | 102 | Verify | Cover sheet states Building 22 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. | B22_Assessment!A20:J20
22 | B21_Assessment | Fire | 103 | Verify | Existing TE room; verify protection-in-place and firestopping after cable transfer or reuse. | B22_Assessment!A21:J21
22 | B21_Assessment | HVAC | 102 | N/A | Cover sheet states mechanical scope is excluded. Verify whether Break Room 102 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | B22_Assessment!A25:J25
22 | B21_Assessment | HVAC | 103 | Verify | Existing Room 103 equipment area; verify existing environmental conditions during cutover and whether legacy equipment remains active. | B22_Assessment!A26:J26
22 | B21_Assessment | Electrical | 102 | Verify | 22T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | B22_Assessment!A30:J30
22 | B21_Assessment | Electrical | 103 | Verify | Existing 103 elevation shows APC UPS, Cisco switch, SERTEX utility service, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | B22_Assessment!A31:J31
22 | B21_Assessment | Telecom | 102 | Verify | 22T-701 identifies TR01-102-1: 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total port quantities, and 8 total ports with 10% allowance. Provide new wall-mount 12RU TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. | B22_Assessment!A35:J35
22 | B22_Assessment | Telecom | 103 | Verify | Existing Room 103 contains APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall and ports 1-24 to Bldg 19 ports 73-96. Field verify all active services and B19 handoff. | B22_Assessment!A36:J36
22 | B22_Assessment | Security | 102 | Verify | Building 22 does not appear to create a new full TR door/PACS package. Verify any existing cameras/security devices in Break Room 102 and ensure no camera angle or VMS integration is disrupted. | B22_Assessment!A40:J40
22 | B22_Assessment | Security | 103 | Verify | Verify security/access conditions and whether any legacy security equipment is present at existing TE location. | B22_Assessment!A41:J41
33 | B22_Assessment | Fire | B23 | Verify | Cover sheet states Building 33 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. | B33_Assessment!A20:J20
33 | B22_Assessment | Fire | B17 | Verify | Existing Tel Closet; verify protection-in-place and firestopping after cable transfer or reuse. | B33_Assessment!A21:J21
33 | B22_Assessment | HVAC | B23 | N/A | Cover sheet states mechanical scope is excluded. Verify whether Office B23 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | B33_Assessment!A25:J25
33 | B22_Assessment | HVAC | B17 | Verify | Existing B17 enlarged plan identifies an existing indoor AC unit. Verify operation during cutover and determine whether active legacy equipment remains after transfer to B23. | B33_Assessment!A26:J26
33 | B22_Assessment | Electrical | B23 | Verify | 33T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | B33_Assessment!A30:J30
33 | B22_Assessment | Electrical | B17 | Verify | Existing B17 elevations show UPS on floor, Cisco switches, SERTEX utility service, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements before disconnect/removal. | B33_Assessment!A31:J31
33 | B22_Assessment | Telecom | B23 | Verify | 33T-701 identifies TE01-B23-1: 55 WAO total, 34 active ports per survey, 88 total ports per schedule, and 97 total ports with 10% allowance. Basement cable tray schedule totals 102 ft. Provide 10 new Cat6A cross-connect cables from existing TE to new TE location. | B33_Assessment!A35:J35
33 | B33_Assessment | Telecom | B17 | Verify | Existing B17 rack elevations include Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, passive Fiber LIU/wall mount, UPS on floor and cross-building port references to Bldgs 3, 80 and 82. | B33_Assessment!A36:J36
33 | B33_Assessment | Security | B23 | Verify | Building 33 does not appear to create a new full TR door/PACS package. Verify existing cameras/security devices in B23 and ensure no camera angle or VMS integration is disrupted. | B33_Assessment!A40:J40
33 | B33_Assessment | Security | B17 | Verify | Existing B17 enlarged plan identifies network door controller, keypad and equipment box; verify protection-in-place and whether any security equipment is relocated or recabled. | B33_Assessment!A41:J41
61 | B33_Assessment | Fire | B13H-A | Verify | Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. | B61_Assessment!A24:J24
61 | B33_Assessment | Fire | 124 | Verify | Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. | B61_Assessment!A25:J25
61 | B33_Assessment | Fire | 226 | Verify | Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. | B61_Assessment!A26:J26
61 | B33_Assessment | Fire | 137 / 137A | Verify | Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | B61_Assessment!A27:J27
61 | B33_Assessment | HVAC | B13H-A | Verify | Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. | B61_Assessment!A31:J31
61 | B33_Assessment | HVAC | 124 | Verify | Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. | B61_Assessment!A32:J32
61 | B33_Assessment | HVAC | 226 | Verify | Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. | B61_Assessment!A33:J33
61 | B33_Assessment | HVAC | 137 / 137A | Verify | Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | B61_Assessment!A34:J34
61 | B33_Assessment | Electrical | B13H-A | Verify | Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. | B61_Assessment!A38:J38
61 | B33_Assessment | Electrical | 124 | Verify | Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. | B61_Assessment!A39:J39
61 | B33_Assessment | Electrical | 226 | Verify | Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. | B61_Assessment!A40:J40
61 | B33_Assessment | Electrical | 137 / 137A | Verify | Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | B61_Assessment!A41:J41
61 | B33_Assessment | Telecom | B13H-A | Verify | 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. | B61_Assessment!A45:J45
61 | B33_Assessment | Telecom | 124 | Verify | 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. | B61_Assessment!A46:J46
61 | B33_Assessment | Telecom | 226 | Verify | 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. | B61_Assessment!A47:J47
61 | B33_Assessment | Telecom | 137 / 137A | Verify | 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service. | B61_Assessment!A48:J48
61 | B33_Assessment | Security | B13H-A | Verify | Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. | B61_Assessment!A52:J52
61 | B61_Assessment | Security | 124 | Verify | Verify TR door hardware and access control, CCTV camera, network door controller and integration. | B61_Assessment!A53:J53
61 | B61_Assessment | Security | 226 | Verify | Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. | B61_Assessment!A54:J54
61 | B61_Assessment | Security | 137 / 137A | Verify | Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | B61_Assessment!A55:J55
62 | B61_Assessment | Fire | B24A | Verify | 0 | B62_TR_Assessment!A24:J24
62 | B61_Assessment | Fire | 125 | Verify | 0 | B62_TR_Assessment!A25:J25
62 | B61_Assessment | Fire | 225 | Verify | 0 | B62_TR_Assessment!A26:J26
62 | B61_Assessment | HVAC | B24A | Verify | 0 | B62_TR_Assessment!A31:J31
62 | B61_Assessment | HVAC | 125 | Verify | 0 | B62_TR_Assessment!A32:J32
62 | B61_Assessment | HVAC | 225 | Verify | 0 | B62_TR_Assessment!A33:J33
62 | B62_TR_Assessment | Electrical | B24A | Verify | 0 | B62_TR_Assessment!A38:J38
62 | B62_TR_Assessment | Electrical | 125 | Verify | 0 | B62_TR_Assessment!A39:J39
62 | B62_TR_Assessment | Electrical | 225 | Verify | 0 | B62_TR_Assessment!A40:J40
70 | B62_TR_Assessment | Fire | B27 | Verify | 0 | B70_TR_Assessment!A24:J24
70 | B62_TR_Assessment | Fire | 125A | Verify | 0 | B70_TR_Assessment!A25:J25
70 | B62_TR_Assessment | Fire | 262A | Verify | 0 | B70_TR_Assessment!A26:J26
70 | B62_TR_Assessment | HVAC | B27 | Verify | 0 | B70_TR_Assessment!A31:J31
70 | B62_TR_Assessment | HVAC | 125A | Verify | 0 | B70_TR_Assessment!A32:J32
70 | B62_TR_Assessment | HVAC | 262A | Verify | 0 | B70_TR_Assessment!A33:J33
70 | B70_TR_Assessment | Electrical | B27 | Verify | 0 | B70_TR_Assessment!A38:J38
70 | B70_TR_Assessment | Electrical | 125A | Verify | 0 | B70_TR_Assessment!A39:J39
70 | B70_TR_Assessment | Electrical | 262A | Verify | 0 | B70_TR_Assessment!A40:J40
78 | B70_TR_Assessment | Electrical | B30 | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, and rated penetrations. | B78_Assessment!A30:J30
78 | B70_TR_Assessment | Electrical | B35 | Verify | Verify FP/FA modifications, FEC location, temporary firestopping and final UL systems. | B78_Assessment!A31:J31
78 | B70_TR_Assessment | Electrical | 1232 | Verify | Verify first-level TR sprinkler/FA work, FEC location and cable tray penetrations. | B78_Assessment!A32:J32
78 | B70_TR_Assessment | Electrical | 227A | Verify | Verify second-level TR sprinkler/FA work, FEC location, vertical riser penetrations and firestopping. | B78_Assessment!A33:J33
78 | B70_TR_Assessment | Fire | 342 | Verify | Verify third-level TR fire protection/fire alarm coordination and firestop work. | B78_Assessment!A34:J34
78 | B70_TR_Assessment | Fire | 401 | Verify | Verify fourth-level TR fire protection/fire alarm coordination and firestop work. | B78_Assessment!A35:J35
78 | B70_TR_Assessment | Fire | Existing rooms | Verify | Verify existing rooms remain protected during cutover and no unsealed penetrations remain. | B78_Assessment!A36:J36
78 | B70_TR_Assessment | Fire | B30 | Verify | Mechanical sheets included for basement. Verify dedicated cooling equipment, capacity, condensate, emergency source, controls/BACnet and high-temperature alarm. | B78_Assessment!A40:J40
78 | B70_TR_Assessment | Fire | B35 | Verify | Verify dedicated cooling and relationship to B30/B35 telecom buildout. | B78_Assessment!A41:J41
78 | B70_TR_Assessment | Fire | 1232 | Verify | Verify first-level TR cooling, controls, emergency power and alarm tie-in. | B78_Assessment!A42:J42
78 | B70_TR_Assessment | Fire | 227A | Verify | Verify second-level TR cooling, condensate route and 24/7 operation. | B78_Assessment!A43:J43
78 | B70_TR_Assessment | HVAC | 342 | Verify | Verify third-level TR cooling and control/alarm integration. | B78_Assessment!A44:J44
78 | B70_TR_Assessment | HVAC | 401 | Verify | Verify fourth-level TR cooling and control/alarm integration. | B78_Assessment!A45:J45
78 | B70_TR_Assessment | HVAC | Existing rooms | Verify | Existing telecom rooms likely have legacy cooling dependencies. Verify active equipment temperature and any protect-in-place cooling requirements. | B78_Assessment!A46:J46
78 | B70_TR_Assessment | HVAC | B30 | Verify | Rack elevations identify new rack UPS/PDU and future rack. Verify panelboard/source, SPD, rack receptacles, PDU feeds, labels, load measurement and LOTO. | B78_Assessment!A50:J50
78 | B70_TR_Assessment | HVAC | B35 | Verify | Verify rack UPS/PDU source, spare/future rack provisions and grounding/bonding. | B78_Assessment!A51:J51
78 | B70_TR_Assessment | HVAC | 1232 | Verify | Verify first-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. | B78_Assessment!A52:J52
78 | B70_TR_Assessment | HVAC | 227A | Verify | Verify second-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. | B78_Assessment!A53:J53
78 | B70_TR_Assessment | Electrical | 342 | Verify | Verify third-level rack receptacles for two racks, UPS/PDU, panel sources and labels. | B78_Assessment!A54:J54
78 | B70_TR_Assessment | Electrical | 401 | Verify | Verify fourth-level rack receptacles, UPS/PDU, panel sources and labels. | B78_Assessment!A55:J55
78 | B70_TR_Assessment | Electrical | Existing rooms | Verify | Existing rack elevations show wall-mounted racks/2-post racks, existing UPS/PDU and demarc/fiber equipment. Confirm active power and transfer needs. | B78_Assessment!A56:J56
78 | B70_TR_Assessment | Electrical | B30 | Verify | 78_78AT-701: 210 WAO total, 23 active ports, 311 scheduled ports, 342 with allowance; rack IDs TR01-B30-1/-2. Basement cable tray total 1,702 ft. | B78_Assessment!A60:J60
78 | B70_TR_Assessment | Electrical | B35 | Verify | 78_78AT-702: 53 WAO total, 23 active ports, 64 scheduled ports, 70 with allowance. Confirm rack ID/room relation and active services. | B78_Assessment!A61:J61
78 | B70_TR_Assessment | Electrical | 1232 | Verify | 78_78AT-702/703: 301 WAO total, 388 active ports, 404 scheduled ports, 444 with allowance. Large active port count; high cutover risk. | B78_Assessment!A62:J62
78 | B70_TR_Assessment | Electrical | 227A | Verify | 78_78AT-703/704: 256 WAO total, 153 active ports, 348 scheduled ports, 383 with allowance. Verify second-level test records and riser labels. | B78_Assessment!A63:J63
78 | B70_TR_Assessment | Telecom | 342 | Verify | 78_78AT-704: 158 WAO total, 163 active ports, 289 scheduled ports, 318 with allowance. Rack IDs TR01-342-1/-2. | B78_Assessment!A64:J64
78 | B70_TR_Assessment | Telecom | 401 | Verify | 78_78AT-705: 89 WAO total, 65 active ports, 123 scheduled ports, 135 with allowance. | B78_Assessment!A65:J65
78 | B70_TR_Assessment | Telecom | Existing rooms | Verify | Photo references identify existing telecom rooms 15E, 1234, 353, 308A and 408A; verify all active services and transfer plan. | B78_Assessment!A66:J66
78 | B70_TR_Assessment | Telecom | B30 | Verify | TR scope includes wall-mounted CCTV cameras and PACS for TR doors. Verify CR/RX/DC/ES/MD, controller and VMS integration. | B78_Assessment!A70:J70
78 | B70_TR_Assessment | Telecom | B35 | Verify | Verify PACS/CCTV integration and door hardware coordination. | B78_Assessment!A71:J71
78 | B70_TR_Assessment | Telecom | 1232 | Verify | Verify first-level TR PACS/CCTV and VMS integration. | B78_Assessment!A72:J72
78 | B70_TR_Assessment | Telecom | 227A | Verify | Verify second-level TR PACS/CCTV and VMS integration. | B78_Assessment!A73:J73
78 | B78_Assessment | Security | 342 | Verify | Verify third-level TR PACS/CCTV and VMS integration. | B78_Assessment!A74:J74
78 | B78_Assessment | Security | 401 | Verify | Verify fourth-level TR PACS/CCTV and VMS integration. | B78_Assessment!A75:J75
78 | B78_Assessment | Security | Existing rooms | Verify | Verify existing PACS/security devices are protected-in-place or recabled without VMS/PACS disruption. | B78_Assessment!A76:J76
80 | B78_Assessment | Fire | 102 | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, and temporary firestopping during cable pulls. | B80_Assessment!A20:J20
80 | B78_Assessment | Fire | 127A / 126 | Verify | Existing telecom closet/room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | B80_Assessment!A21:J21
80 | B78_Assessment | HVAC | 102 | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 102 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet interface, thermostat/control point, condensate pump/path, disconnects, and high-temperature alarm. | B80_Assessment!A25:J25
80 | B78_Assessment | HVAC | 127A / 126 | Verify | Existing telecom room/closet may remain active during cutover. Verify existing environmental condition and whether any active equipment remains after migration to Room 102. | B80_Assessment!A26:J26
80 | B78_Assessment | Electrical | 102 | Verify | Electrical plans/schedules identify B80-TR102A fed from BUS-B80-MDP and B80-TR102B fed from BUS-B80-E1, with rack receptacles, normal/emergency circuits, CU-1-01, SPD requirements and 30-day load measurement requirements. | B80_Assessment!A30:J30
80 | B78_Assessment | Electrical | 127A / 126 | Verify | Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | B80_Assessment!A31:J31
80 | B78_Assessment | Telecom | 102 | Verify | 80T-701 identifies RM102 with 117 WAO total, 98 active ports per survey, 195 total ports per schedule, and 215 total ports with 10% allowance. Rack IDs include TR01-102-1 and TR01-102-2; rack elevation shows 1 new rack plus future rack with switches, Cat6A patch panels, Cat5e patch panel, Fiber LIU, UPS and PDU. | B80_Assessment!A35:J35
80 | B80_Assessment | Telecom | 127A / 126 | Verify | Existing rack elevation shows Cisco switches, legacy optical Fiber LIU on wall, multiple legacy Ortronics 24/48-port patch panels, legacy Cat5e 24-port patch panel, and APC floor UPS. Contractor must transfer existing devices to new rack and protect active services. | B80_Assessment!A36:J36
80 | B80_Assessment | Security | 102 | Verify | Electrical/telecom plans show access-control scope and camera 102-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, electric strike, camera/VMS integration, and door hardware coordination. | B80_Assessment!A40:J40
80 | B80_Assessment | Security | 127A / 126 | Verify | Verify existing security/PACS equipment conditions and whether any existing camera/security device is protected, recabled, or removed during cutover. | B80_Assessment!A41:J41
82 | B80_Assessment | Fire | 102 | Verify | Cover sheet states Building 82 receives a Telecom Enclosure and fire protection scope is excluded. Still verify rated penetrations, 4-inch sleeve, wall/floor openings, temporary firestopping, and life-safety device impacts. | B82_Assessment!A20:J20
82 | B80_Assessment | Fire | B01-A | Verify | Existing telecom room; verify protection-in-place and firestopping after cable transfer or reuse. | B82_Assessment!A21:J21
82 | B80_Assessment | HVAC | 102 | Verify | Mechanical and electrical drawings show IU-1-01 in/near Telecom Room 102 and CU-1-01 outdoor unit. Mechanical notes call for BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency/standby source, condensate pump/path, disconnects, controls, and high-temp alarm. | B82_Assessment!A25:J25
82 | B80_Assessment | HVAC | B01-A | Verify | Existing telecom room may remain active during cutover. Verify existing environmental conditions and whether active equipment remains after transfer to Room 102. | B82_Assessment!A26:J26
82 | B80_Assessment | Electrical | 102 | Verify | Electrical plans/schedules identify TE receptacle, CU-1-01, B82-MDP and B82-P-EMER sources, with SPD devices integral to new telecom panelboards. Verify receptacle type, grounding/bonding, emergency source, labels, and circuit loading. | B82_Assessment!A30:J30
82 | B80_Assessment | Electrical | B01-A | Verify | Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | B82_Assessment!A31:J31
82 | B80_Assessment | Telecom | 102 | Verify | 82T-701 identifies RM102 with 26 WAO total, 31 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. Rack ID TR01-102-01. Cable tray schedule totals 278 ft on first level. New enclosure includes APC UPS, two PDUs, network switch, Cat6A patch panel and Fiber LIU. | B82_Assessment!A35:J35
82 | B82_Assessment | Telecom | B01-A | Verify | Existing B01-A elevations identify Cisco switches, cable management, two Ortronics 24-port patch panels with 11 and 6 used, existing patch panels and APC floor UPS. Field verify active services and transfer plan to new TE. | B82_Assessment!A36:J36
82 | B82_Assessment | Security | 102 | Verify | Building 82 appears to create a TE enclosure rather than a full TR door/PACS package. Verify existing cameras/security devices in Room 102 and ensure no camera angle or VMS integration is disrupted. | B82_Assessment!A40:J40
82 | B82_Assessment | Security | B01-A | Verify | Keynotes indicate existing cameras are to be retained and re-used. Verify security/access conditions and whether any legacy security equipment is present at existing telecom room. | B82_Assessment!A41:J41
BCH | B82_Assessment | Fire | 107 | Verify | Cover sheet states BCH receives a Telecom Enclosure and mechanical/fire protection scope has been excluded. Still verify existing life-safety protection, rated penetrations, 4-inch sleeve fire caulk, temporary firestopping and abandoned penetration patching. | BCH_Assessment!A20:J20
BCH | B82_Assessment | Fire | 00 / 107 | Verify | TE-only scope does not appear to require new FEC/fire sprinkler work, but all wall/floor/ceiling penetrations must be sealed and rated assemblies maintained. | BCH_Assessment!A21:J21
BCH | B82_Assessment | HVAC | 107 | N/A | Cover sheet explicitly excludes mechanical scope. Verify existing room ambient conditions are acceptable for TE equipment and that no active network equipment will overheat. | BCH_Assessment!A25:J25
BCH | B82_Assessment | HVAC | 00 / 107 | N/A | If the final scope is a 45RU new telecom room rather than a small TE, HVAC exclusion should be confirmed with VA/AE because telecom-room heat load may differ from TE assumptions. | BCH_Assessment!A26:J26
BCH | B82_Assessment | Electrical | 107 | Verify | Electrical plan includes first-level electrical work and notes for new wall-mount telecom enclosure, grounding/bonding and camera. Verify circuit source, receptacle type, UPS/PDU load, emergency source if required, grounding/bonding and labels. | BCH_Assessment!A30:J30
BCH | B82_Assessment | Electrical | 00 / 107 | Verify | BCHT-604 shows 12RU TE equipment with APC UPS and PDUs and also a BCH 45RU new telecom room elevation. Confirm exact UPS/PDU/rack power requirement before acceptance. | BCH_Assessment!A31:J31
BCH | B82_Assessment | Telecom | 107 | Verify | BCHT-101 identifies telecom plan first level and enlarged Room 107. BCHT-604 identifies new telecom room/no existing elevations. There is no BCHT-701 schedule in the drawing index, so WAO/cable-tray totals must be field verified from plans and contractor coordination drawings. | BCH_Assessment!A35:J35
BCH | BCH_Assessment | Telecom | 00 / 107 | Verify | BCHT-604 identifies a 12RU TE elevation: APC UPS, two PDUs, network switch, 48-port Cat6A patch panel and Fiber LIU. Also shows BCH Crescent House Room 107 new telecom room elevation. Confirm governing rack/enclosure and labeling. | BCH_Assessment!A36:J36
BCH | BCH_Assessment | Security | 107 | Verify | Telecom/electrical notes reference new IP-addressable camera with wall mount at 8'-6" A.F.F. and VMS integration. Verify whether PACS applies; TE buildings typically do not create full TR door/PACS scope. | BCH_Assessment!A40:J40
BCH | BCH_Assessment | Security | 00 / 107 | Verify | Verify existing camera/security conditions, protection-in-place, and any recabling or VMS integration required. | BCH_Assessment!A41:J41
MCR | BCH_Assessment | Fire | 107 / MCR | Verify | MCR has full fire protection scope including wet pipe and clean-agent fire suppression system. Verify preaction/clean-agent design, agent release interface, fire alarm matrix, detection, abort/release stations, room integrity and acceptance testing. | MCR_Assessment!A28:J28
MCR | BCH_Assessment | Fire | 031 | Verify | Verify fiber entrance room protection, rated penetrations, firestopping, detector/strobe coverage and no gaps after cable tray installation. | MCR_Assessment!A29:J29
MCR | BCH_Assessment | Fire | MDA-A/B | Verify | Verify sprinkler/clean-agent coverage around MDA equipment, fire alarm devices, rack clearance and final firestop assemblies. | MCR_Assessment!A30:J30
MCR | BCH_Assessment | Fire | HDA-A/B | Verify | Verify clean-agent coverage, detector placement, alarm interfaces, and open cabinet airflow protection. | MCR_Assessment!A31:J31
MCR | BCH_Assessment | Fire | Existing 107/137 | Verify | Existing systems must remain protected during temporary fiber, umbilical cord and core relocation work. Verify no impairment without approved fire watch/impairment plan. | MCR_Assessment!A32:J32
MCR | BCH_Assessment | HVAC | 107 / MCR | Verify | Telecom notes call for indoor computer room air conditioner (CRAC) units tied to building management system. Mechanical sheets included; verify redundant capacity, setpoints, humidity, condensate, controls, alarms and emergency power. | MCR_Assessment!A36:J36
MCR | BCH_Assessment | HVAC | UPS-A / UPS-B | Verify | UPS rooms/equipment require thermal load validation, ventilation, emergency power and alarm integration. Verify battery/UPS environmental requirements. | MCR_Assessment!A37:J37
MCR | BCH_Assessment | HVAC | MDA-A/B | Verify | Verify airflow/cold aisle/hot aisle assumptions, blanking panels, floor/ceiling distribution and temperature monitoring. | MCR_Assessment!A38:J38
MCR | BCH_Assessment | HVAC | HDA-A/B | Verify | Server cabinets and patch fields require stable 24/7 cooling and monitoring. Confirm no local hot spots at dense LIU/patch panel zones. | MCR_Assessment!A39:J39
MCR | BCH_Assessment | HVAC | Existing 107/137 | Verify | During split-core temporary phase, existing MCR/server equipment remains active. Verify existing cooling remains in service until cutover and decommissioning are complete. | MCR_Assessment!A40:J40
MCR | BCH_Assessment | Electrical | 107 / MCR | Verify | Electrical set includes site plan, enlarged MCR plans, one-lines and schedules. Verify switchboard/service, ATS/generator integration, normal/emergency/UPS distribution, grounding, lightning protection, SPD, load measurements and commissioning. | MCR_Assessment!A44:J44
MCR | BCH_Assessment | Electrical | MDA-A/B | Verify | MDA rack elevations include new 4-post floor cabinets, LIUs and network elements. Verify redundant A/B power feeds and PDU arrangements. | MCR_Assessment!A45:J45
MCR | BCH_Assessment | Electrical | HDA-A/B | Verify | HDA cabinets include server cabinet front/rear elevations with patch panels and active equipment. Confirm A/B feed separation, PDU mounting, load capacity and labels. | MCR_Assessment!A46:J46
MCR | BCH_Assessment | Electrical | Existing 107/137 | Verify | Existing rack elevations identify multiple APC/Chatsworth/HP PDUs, APC Smart UPS and Eaton 9PX units. Verify what transfers, what stays, and temporary power during migration. | MCR_Assessment!A47:J47
MCR | BCH_Assessment | Electrical | Site / Utility | Verify | New MCR is standalone critical infrastructure. Verify utility service, generator/ATS paths, emergency distribution, grounding electrode and ductbank/site electrical coordination. | MCR_Assessment!A48:J48
MCR | BCH_Assessment | Telecom | 107 / MCR | Verify | MCRT-101 shows new MCR with MDA-A/B, HDA-A/B, UPS-A/B, cameras and fiber path legend. MCRT-701 shows 10 WAO total, 720 WAO available, 98.1% expansion capacity, 10 total ports with 20% allowance and 359 ft cable tray. | MCR_Assessment!A52:J52
MCR | BCH_Assessment | Telecom | 031 | Verify | MCRT-701 Data Device and Circuit Schedule - Fiber Entrance Room 1: outlets 31-A/B/C/D plus security devices 07-CAM-03/04/07/08/11; Rack ID TR01-031-1. | MCR_Assessment!A53:J53
MCR | BCH_Assessment | Telecom | MDA-A/B | Verify | MCRT-607: MDA A/B racks contain horizontal distribution LIUs, hybrid FOC, 48x Cat6A to HDA, and reserved LAN/spine/aggregation elements. Maintain A/B path separation. | MCR_Assessment!A54:J54
MCR | BCH_Assessment | Telecom | HDA-A/B | Verify | MCRT-608/609: HDA A/B include 48-port Cat6A patch panels, HD fiber LIUs, backbone side A/B LIU and server cabinet arrangements. | MCR_Assessment!A55:J55
MCR | BCH_Assessment | Telecom | Existing 107/137 | Verify | Existing MCR rows 1-3 and B61 server cabinet transfer references are extensive. Maintain service using temporary fiber/umbilical cords and phased core relocation. | MCR_Assessment!A56:J56
MCR | BCH_Assessment | Security | 107 / MCR | Verify | MCRT-101 identifies cameras 07-CAM-01 through 07-CAM-12 around the MCR. Telecom notes call for IP-addressable network cameras integrated into existing VMS and PACS/access-control systems including iSTAR Edge/Avigilon ACM controller. | MCR_Assessment!A60:J60
MCR | BCH_Assessment | Security | 031 | Verify | MCRT-701 includes security camera/data devices assigned to TR01-031-1. Confirm camera IDs, mounting, cabling, and VMS commissioning. | MCR_Assessment!A61:J61
MCR | MCR_Assessment | Security | MDA-A/B | Verify | Verify camera coverage, door/access points, VMS monitoring and access control zones for critical equipment. | MCR_Assessment!A62:J62
MCR | MCR_Assessment | Security | HDA-A/B | Verify | Verify coverage of HDA cabinets, doors, motion detection and any lockable cabinet/security requirements. | MCR_Assessment!A63:J63
MCR | MCR_Assessment | Security | Existing 107/137 | Verify | Existing security systems must remain functional during transition; protect existing camera angles and access controls until final turnover. | MCR_Assessment!A64:J64
SITE | MCR_Assessment | Electrical | Overall Site | Verify | Electrical site plans ES101/ES401 are included. Existing utility locations are approximate; coordinate electrical vaults, underground electrical, storm drain manholes and sanitary manholes. | SITE_Assesment!A46:J46
SITE | MCR_Assessment | Electrical | THH / Manholes | Verify | Locking covers and handhole/manhole locations must be field verified. Confirm bonding/grounding requirements where metallic components are present. | SITE_Assesment!A47:J47
SITE | MCR_Assessment | Electrical | MCR / Provider Entrance | Verify | T-601 shows WAN/provider fiber entrances and new fiber Path A/B to the MCR. Coordinate with Century Link/service provider and MCR activation. | SITE_Assesment!A48:J48
SITE | MCR_Assessment | Electrical | Building Tie-ins | Verify | Coordinate conduit penetrations with building electrical/telecom/firestop scope and avoid conflicts with existing services. | SITE_Assesment!A49:J49
SITE | MCR_Assessment | Telecom | Campus Backbone | Verify | Legend identifies new fiber in A route, B route, and A+B routes in separate conduits. Confirm no cross-connect gaps at THHs/manholes. | SITE_Assesment!A53:J53
SITE | MCR_Assessment | Telecom | MCR Provider / WAN | Verify | Site one-line shows WAN fiber from service provider and temporary/provider extension pathways. Coordinate with MCR activation and OIT. | SITE_Assesment!A54:J54
SITE | MCR_Assessment | Telecom | Building Drops | Verify | Each building tie-in must be tested, labeled, and accepted before connection to active operations. | SITE_Assesment!A55:J55
SITE | MCR_Assessment | Telecom | THH Network | Verify | T-601 one-line lists THH #1-#19 and path counts such as 6 Path A + 4 Path B, 6 Path A + 6 Path B, 7 Path A + 7 Path B, 5 Path A + 4 Path B, and 9 Path A + 7 Path B. | SITE_Assesment!A56:J56
SITE | SITE_Assesment | Security | Campus Site Work | Verify | Coordinate staging, access, material storage, noisy work, utility interruption, trench barricades and public access with owner. | SITE_Assesment!A60:J60
SITE | SITE_Assesment | Security | Road / Parking Impacts | Verify | General notes specifically identify accessible parking and public right-of-way impacts; temporary barricades must prevent injury and protect parking signage. | SITE_Assesment!A61:J61
SITE | SITE_Assesment | Security | Critical Utility Crossings | Verify | Hand digging at existing utility crossings is in base bid. Confirm permits, Dig Safe, VA utility locate and escort requirements before excavation. | SITE_Assesment!A62:J62

## B01_Assessment (hidden)
BUILDING 01 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 01 | Building Phase | Construction | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-26 13:26 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 01 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 107 / existing B02 / 138 / 282
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning.
HVAC Status | Not Started | Electrical Status | Not Started | Telecom Status | Not Started | Fire Protection Status | Not Started | Fire Alarm Status | Not Started
Security Status | Not Started | Next Action | Field verify Room 107, existing B02, 138, and 282; confirm active services, existing rack/equipment transfer, B01-TR107A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 394 ft cable tray routes, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
01 | 107 | First | New Telecom Room build area | Telecom Room | 1 | 1 | Verify | 01A-401 / 01E-101 / 01E-601 / 01E-701 / 01T-101 / 01T-604 / 01T-605 / 01T-701 | Primary Building 01 TR. Plans identify Room 107 as new TR with Rack ID TR01-107-1, one new 4-post rack plus future rack, 5kW UPS, future/zone PDU, network switches, 48-port Cat6A patch panels, 24-port Cat5e patch panel, Fiber LIU, panels B01-TR107A/B, IU-1-01/CU-1-01 cooling, camera 107-CAM-1, and 161 total ports with 10% allowance.
01 | B02 | Basement | Existing telecom room / racks | Existing telecom transition point | 3 | 0 | Verify | 01T-100 / 01T-604 / 01R-900 | Existing Basement Telecom Room B02 with two 2-post floor racks and one wall TE. Existing equipment includes open rack, UPS on floor, Tripp Lite Smart Pro UPS, Tera Max/Nokia/Baseband/IRU equipment, Corning LANscape, Cisco, and Ortronics 24-port patch panels. Protect active services and transfer devices as required.
01 | 138 | First | Existing telecom room / patch panels | Existing telecom transition point | 3 | 0 | Verify | 01T-101 / 01T-604 / 01R-900 | Existing First-Level Telecom Room 138 with existing patch panels, APC UPS floor, Cisco, Corning LANscape and Ortronics 24/48-port patch panels. Protect active services and verify migration to Room 107.
01 | 282 | Second | Existing telecom room / racks | Existing telecom transition point | 2 | 0 | Verify | 01T-101 / 01T-605 / 01R-900 | Existing Second-Level Telecom Room 282 with two 2-post floor racks, Cisco switches, cable managers, legacy Ortronics 24/48-port patch panels, Corning LANscape and APC 12-port equipment. Protect active services during Room 107 cutover.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New TR. Verify rated wall/smoke barrier conditions, door/access-control hardware, ceiling/deck, floor sealer, rack/future rack clearances, wall backing, cable tray, fiber path A/B, and working clearances around rack, panels and IU.
B02 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing basement telecom room. Verify active equipment, rack access, existing UPS power, wall TE, pathway and transfer/abandonment scope.
138 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing first-level telecom transition point. Verify rack/panel condition, active services, UPS, patching and cable transfer scope.
282 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing second-level telecom transition point. Verify rack access, active services, pathway/riser and final condition after cutover.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems.
B02 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse.
138 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes.
282 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
107 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup.
B02 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration.
138 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear.
282 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
107 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B01-TR107A / B01-TR107B | Verify | Verify | Verify | Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation.
B02 | Existing | Existing UPS on floor / Tripp Lite Smart Pro UPS | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements.
138 | Existing | Existing APC UPS floor | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition.
282 | Existing | Existing / Verify | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1.
B02 | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan.
138 | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence.
282 | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical/telecom plans show new access control, power supply/battery backup for PACS, HDP12/FIPS-compliant PIV-ready card reader with PIN pad, and camera 107-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration and door hardware coordination.
B02 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/CCTV equipment and any retained cameras. Maintain camera angles where existing security cameras are recabled.
138 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/access conditions and protection-in-place during rack transfer.
282 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify second-level existing security/CCTV impacts during cabling and equipment transfer.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B01-R1 | All | Existing conditions for Room 107 and transition rooms B02/138/282 not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | B01 has multiple existing telecom rooms and a new TR buildout.
B01-R2 | B02/138/282 | Existing equipment may remain active during transfer to Room 107 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | Existing rack elevations show multiple active switches, LIUs, patch panels and UPS equipment.
B01-R3 | 107 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat, humidity and high-temp alarms | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B01-R4 | 107 | B01-TR107A/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panels, breakers, receptacles, SPD, labels, 30-day load measurement and LOTO needs | Electrical / GCC | Closed | Electrical schedules call for new panels and 30-day load measurement prior to panel work.
B01-R5 | All | 394 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 58 ft, first 212 ft, second 124 ft.
B01-R6 | All | Telecom/fiber cutover could affect active hospital communications across basement/first/second levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | RM107 supports 161 total ports including allowance and transfer from multiple existing rooms.
B01-R7 | 107 | PACS/CCTV/door hardware coordination may not be ready at room acceptance | High | Medium | 6 | Verify access-control rough-in, power supply/battery backup, reader, electric strike, door position, camera and VMS/PACS test records | Security / Electrical | Closed | Plans include new PACS and 107-CAM-1.
B01-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | 50-sheet IFC package includes full discipline scope and third-party inspections requirement.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B01-Q1 | Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B01-Q2 | What active services are currently fed from existing Rooms B02, 138 and 282? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B01-Q3 | What equipment from existing racks transfers to new Room 107 versus remains/decommissions? | OIT / Telecom | Closed |  |  | Cutover and rack elevation risk
B01-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B01-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? | GC / COR | Closed |  |  | Life-safety acceptance risk
B01-Q6 | Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B01-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B01-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B01-P001 | 107 | Existing / New Condition | Room 107 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, fiber path A/B, cable tray and penetrations |  | Paul |  | B01-R1/B01-R3 | Closed
B01-P002 | B02 | Existing Equipment | Basement existing telecom room B02 racks, wall TE, Cisco/Nokia/Baseband/IRU/Corning/Ortronics equipment, UPS and cable entries |  | Paul |  | B01-R1/B01-R2 | Closed
B01-P003 | 138 | Existing Equipment | First-level existing telecom room 138 racks, patch panels, Cisco, Corning, APC UPS and active service labels |  | Paul |  | B01-R2/B01-R6 | Closed
B01-P004 | 282 | Existing Equipment | Second-level existing telecom room 282 racks, Cisco switches, Ortronics patch panels, cable managers and active service labels |  | Paul |  | B01-R2/B01-R6 | Closed
B01-P005 | 107 | HVAC | IU-1-01/CU-1-01, condensate pump/line, thermostat, BACnet adapter, disconnects, FMS alarm points and power source |  | Paul |  | B01-R3 | Closed
B01-P006 | 107 | Electrical | B01-TR107A/B panels, rack receptacles, breakers, SPD, PACS power supply, access controller, lighting, CU-1-01 and labels |  | Paul |  | B01-R4/B01-R7 | Closed
B01-P007 | All | Cable Tray / Firestop | Basement/first/second cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping |  | Paul |  | B01-R5 | Closed
B01-P008 | 107 / Existing Rooms | Telecom / Security | New rack/future rack, Fiber LIU, Cat6A, patch panels, labels/test records, 107-CAM-1, PACS and existing rack transfer work |  | Paul |  | B01-R6/B01-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
107 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Green | New first-level TR with 161 total ports including allowance, dedicated cooling, UPS/PDU, B01-TR107A/B panels, cable tray, PACS/CCTV and fire/life-safety scope.
B02 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Green | Existing basement telecom transition point; protect active services until transfer/cutover complete.
138 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Green | Existing first-level telecom transition point; protect active services and verify final condition.
282 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Green | Existing second-level telecom transition point; protect active services and verify final condition.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B98: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B107: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B119: Compare installed materials against approved submittals/spec sections.
Note on B128: Planned vs actual production supports delay/time-extension rebuttal.
Note on B136: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B02_Assessment (hidden)
BUILDING 02 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 02 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-26 13:46 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 02 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 141 / 236 / 342 / existing B-06 / existing 141 / existing 236
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance.
HVAC Status | Not Started | Electrical Status | Not Started | Telecom Status | Not Started | Fire Protection Status | Not Started | Fire Alarm Status | Not Started
Security Status | Not Started | Next Action | Field verify new Rooms 141, 236, 342 and existing B-06/141/236; confirm active services, rack/equipment transfer, B02-TR141A/B, B02-TR236A/B, B02-TR342A/B panel sources, CU-1-01/CU-2-01/CU-3-01 cooling assignments, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, 2,560 ft cable tray routes, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
02 | 141 | First | Existing first-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-401 / 02E-101 / 02E-401 / 02E-601 / 02E-701 / 02T-101 / 02T-401 / 02T-604 / 02T-701 | Primary first-level TR. Schedules identify RM141 with 211 WAO total, 215 active ports, 322 scheduled ports and 354 total ports with 10% allowance. Rack IDs TR01-141-01/02. Enlarged plan shows Room 141 new and demo scope, 174-CAM-01, existing patch panels/fire alarm cabinet relocated to RM141 and future rack space.
02 | 236 | Second | Existing second-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-401 / 02E-102 / 02E-402 / 02E-701 / 02T-102 / 02T-401 / 02T-604 / 02T-702 | Second-level TR. Schedules identify RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approximately 345 ports with 10% allowance. Rack IDs TR01-236-01/02. Enlarged plans show 236-CAM-01 and new/demolition work at Room 236 / existing Room 282.
02 | 342 | Third | Third-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-402 / 02E-103 / 02E-402 / 02E-701 / 02T-103 / 02T-401 / 02T-604 / 02T-703 | Third-level TR. Schedules identify RM342 with 274 WAO total, 96 active ports, 353 scheduled ports and 388 total ports with 10% allowance. Rack IDs TR01-342-01/02. Enlarged plans show 342-CAM-01, 342A-CK-A and new rack scope.
02 | B-06 | Basement | Existing telecom room / legacy rack equipment | Existing telecom transition point | 1 | 0 | Verify | 02T-100 / 02T-604 / 02R-900 | Existing Basement Telecom Room B-06 with legacy Ortronics 48-port patch panels. Photo reference identifies B-06 existing telecom room. Protect active services and verify transfer/abandonment scope.
02 | Existing 141 / 236 | First / Second | Existing telecom room equipment / transition points | Existing telecom transition points | 4 | 0 | Verify | 02T-604 / 02R-900 | Existing First-Level Telecom Room 141 and Second-Level Existing Telecom Room 236 shown in photo references/rack elevations. Existing devices and racks are to be protected or transferred per notes.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify rated walls/smoke barriers, door/access-control hardware, ceiling/deck, floor finish, rack/future rack clearance, wall backing, cable tray, fiber path A/B, and working clearances around racks/panels/IU.
236 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR; verify rated construction, door/PACS, rack clearances, riser penetrations, cable tray conflicts and final room layout around existing/demo conditions.
342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Third-level TR; verify rated construction, door/PACS, rack clearances, cable tray, firestop, ceiling coordination and future rack space.
B-06 / existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing telecom transition rooms must remain operational until cutover. Verify active equipment inventory, labels, access and final transfer/decommission scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems.
236 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping.
342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping.
B-06 / existing rooms | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
141 | CU-1-01 / TR cooling assignment verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms.
236 | CU-2-01 / TR cooling assignment verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm.
342 | CU-3-01 / TR cooling assignment verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration.
B-06 / existing rooms | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
141 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B02-TR141A / B02-TR141B | Verify | Verify | Verify | Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels.
236 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B02-TR236A / B02-TR236B | Verify | Verify | Verify | Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping.
342 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B02-TR342A / B02-TR342B | Verify | Verify | Verify | Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits.
B-06 / existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray.
236 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope.
342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count.
B-06 / existing rooms | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Plans show 174-CAM-01 associated with the first-level TR area and PACS/security requirements. Verify camera/VMS integration, access controller/power supply, CR/RX/DC/ES/MD and door hardware.
236 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Plans show 236-CAM-01. Verify camera/VMS integration, access control, door hardware, motion/detection devices and power.
342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Plans show 342-CAM-01 and 342A-CK-A. Verify camera/VMS integration and access control/security rough-in.
B-06 / existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Maintain existing camera angles when re-cabling and protect existing PACS/equipment racks during transfer.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B02-R1 | All | Existing conditions for Rooms 141/236/342 and existing B-06/141/236 not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | B02 has multiple new TRs and existing transition rooms.
B02-R2 | Existing rooms | Existing equipment may remain active during transfer to new TRs | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | Existing rack elevations/photos show active legacy rack/patch equipment.
B02-R3 | 141/236/342 | Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm each IU/CU serving each TR, power source, condensate route, controls, BACnet, thermostat and high-temp alarms | Mechanical / Electrical | Closed | Electrical schedule references CU-1/2/3-01; assignments must be field verified.
B02-R4 | All TRs | B02-TR141/236/342 A/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panels, breakers, receptacles, SPDs, labels, 30-day load measurement and LOTO needs | Electrical / GCC | Closed | Multiple new telecom panels and rack circuits.
B02-R5 | All | 2,560 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 303 ft, first 1,069 ft, second 544 ft, third 583 ft, fourth 59 ft.
B02-R6 | All | Telecom/fiber cutover could affect active hospital communications across several floors | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | High WAO counts: 211/179/274 WAO across Rooms 141/236/342.
B02-R7 | 141/236/342 | PACS/CCTV/door hardware coordination may not be ready at room acceptance | High | Medium | 6 | Verify access-control rough-in, power supply/battery backup, reader, strike, door position, cameras and VMS/PACS test records | Security / Electrical | Closed | Plans include 174-CAM-01, 236-CAM-01, 342-CAM-01.
B02-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | 66-sheet IFC package with full discipline scope and third-party inspection requirements.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B02-Q1 | Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B02-Q2 | What active services are currently fed from existing Rooms B-06, 141 and 236? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B02-Q3 | What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? | OIT / Telecom | Closed |  |  | Cutover and rack elevation risk
B02-Q4 | Which IU/CU pair serves each TR and are they on emergency/backup power? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B02-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? | GC / COR | Closed |  |  | Life-safety acceptance risk
B02-Q6 | Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B02-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B02-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B02-P001 | 141 | Existing / New Condition | Room 141 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 174-CAM-01, penetrations and demo/relocation conditions |  | Paul |  | B02-R1/B02-R3 | Closed
B02-P002 | 236 | Existing / New Condition | Room 236 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 236-CAM-01, penetrations and existing transfer conditions |  | Paul |  | B02-R1/B02-R6 | Closed
B02-P003 | 342 | Existing / New Condition | Room 342 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 342-CAM-01, penetrations and 342A-CK-A |  | Paul |  | B02-R1/B02-R7 | Closed
B02-P004 | B-06 | Existing Equipment | Basement existing telecom room B-06 legacy rack/patch panels, active service labels and cable entries |  | Paul |  | B02-R2 | Closed
B02-P005 | Existing 141 / 236 | Existing Equipment | Existing first/second-level telecom rooms 141 and 236, existing patch panels, relocated/removed equipment and fire alarm cabinet conditions |  | Paul |  | B02-R2/B02-R6 | Closed
B02-P006 | All TRs | Electrical / HVAC | B02-TR141/236/342 A/B panels, rack receptacles, breakers, SPD, UPS/PDU, CU/IU equipment, condensate, disconnects and labels |  | Paul |  | B02-R3/B02-R4 | Closed
B02-P007 | All | Cable Tray / Firestop | Basement/first/second/third/fourth cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping |  | Paul |  | B02-R5 | Closed
B02-P008 | All TRs | Telecom / Security | Racks, Fiber LIU, Cat6A, patch panels, labels/test records, cameras, PACS and existing rack transfer work |  | Paul |  | B02-R6/B02-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
141 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with 354 total ports including allowance, 2 rack IDs, B02-TR141A/B panels, high cable tray volume and existing room transfer scope.
236 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR with approx. 345 total ports including allowance, B02-TR236A/B panels, camera/PACS and existing transition scope.
342 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Third-level TR with 388 total ports including allowance, B02-TR342A/B panels, camera/security and high WAO count.
B-06 / existing rooms | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing telecom transition points; protect active services until transfer/cutover complete.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B02.20260316(1).pdf
Drawing Index | 66-sheet Building 02 IFC package includes general, architectural, interiors, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, cutsheets and photo references.
General Scope Basis | 02G-000 states the project includes new TRs, Cat6A/fiber, racks, UPS, power supplies/electrical distribution, dedicated HVAC, CCTV, fire protection/fire alarm, PACS, commissioning and third-party inspections. No active connection until VA testing/approval/acceptance.
Telecom Basis | 02T-101/102/103 identify Rooms 141, 236 and 342 with cameras 174-CAM-01, 236-CAM-01 and 342-CAM-01. 02T-604 identifies existing and new rack elevations. 02T-701/702/703 identify WAO/cable schedules and cable tray total of 2,560 ft.
Schedule Basis | 02T-701: RM141 211 WAO, 215 active, 322 scheduled, 354 with 10% allowance. 02T-702: RM236 179 WAO, 178 active, 314 scheduled, approx. 345 with 10% allowance. 02T-703: RM342 274 WAO, 96 active, 353 scheduled, 388 with 10% allowance.
Electrical Basis | 02E-601/701/702/703 identify B02-TR141A/B, B02-TR236A/B and B02-TR342A/B, rack UPS/PDU circuits, lighting/receptacles, cooling equipment, SPDs and 30-day load measurement requirements.
Fire / Security Basis | 02FX sheets include fire protection scope. General notes require clean-agent/CO2 extinguisher cabinets within 75 ft of each TR and sprinkler/fire alarm modifications. 02T/02E identify cameras and PACS/security requirements.
Photo Basis | 02R-900 provides photo references for Basement Existing Telecom Room B-06, First-Level Existing Telecom Room 141, and Second-Level Existing Telecom Room 236.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B110: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B119: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B131: Compare installed materials against approved submittals/spec sections.
Note on B140: Planned vs actual production supports delay/time-extension rebuttal.
Note on B148: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B03_Assessment (hidden)
BUILDING 03 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 03 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-26 15:10 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 03 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 101E / existing 107 / existing 101C / basement + first-level WAO
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance.
HVAC Status | Not Started | Electrical Status | Not Started | Telecom Status | Not Started | Fire Protection Status | Not Started | Fire Alarm Status | Not Started
Security Status | Not Started | Next Action | Field verify Room 101E, existing Room 107, and existing DMARC Room 101C; confirm active services, existing rack/equipment transfer, B03-TR101CA/B panel sources, CU-01 cooling assignment, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, 961 ft cable tray routes, Room 107 inventory, and telecom cutover/fiber transfer sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
03 | 101E | First | New telecom room buildout / relocated TR function | Telecom Room | 2 | 1 | Verify | 03A-401 / 03E-101 / 03E-401 / 03E-601 / 03E-701 / 03T-101 / 03T-401 / 03T-604 / 03T-701 | Primary Building 03 TR. Schedules identify RM101E with 143 WAO total, 213 active ports, 187 scheduled ports, 206 total ports with 10% allowance, Rack IDs TR01-101E-1 and TR01-101E-2, 5kW UPS, Zone PDU, fiber LIU, Cat6A patch panels, and future rack/switch capacity.
03 | 107 | Basement | Existing telecom room / legacy rack equipment | Existing telecom transition point | 1 | 0 | Verify | 03T-100 / 03T-403 / 03T-604 / 03R-900 | Existing Basement Telecom Room 107. Rack elevation identifies Building 3 existing B3-LB-B13-TC-FIBER rack with UPS on floor, Cisco switch, legacy 48-port patch panels, and fiber LIU wall-mounted. 03T-403 provides Room 107 inventory list for reference.
03 | 101C | First | Existing DMARC / telecom room | Existing DMARC transition point | 1 | 0 | Verify | 03T-101 / 03T-401 / 03T-604 / 03R-900 | First-floor existing DMARC Room 101C / telecom room. Enlarged plan shows existing/removal patch panels, existing branch panel, telecom cabinet, 101C-CAM-01, 101C-CK-A, 101C-A/B/C/D and AP locations. Protect active DMARC/fiber until new service is operational.
03 | 108 / 107A / 101C related WAO areas | First | Work area outlets and WAP/camera locations | WAO recabling / device support | 0 | 0 | Verify | 03T-101 / 03T-701 | WAO schedule includes first-level outlets such as 108-A/B/C, 108-CK-A, 108-AP-A, 107A-AP-A, 101C-CAM-01, 101C-A/B/C/D and AP locations served from TR01-101E-1/2.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
101E | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New/renovated TR. Verify rated walls/smoke barriers, door/access-control hardware, ceiling/deck, floor finish, rack/future rack clearances, wall backing, cable tray, fiber path A/B, and working clearances around rack, panels and cooling equipment.
107 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing basement telecom room must remain operational until cutover. Verify active equipment, rack access, existing UPS on floor, wall/floor rack conditions, and transfer/abandonment scope.
101C | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing DMARC/telecom transition point; verify active provider/fiber/DMARC services, branch panel, patch panels, cabinet and protection-in-place.
WAO Areas | Existing / Verify | Existing / Verify | Existing / Verify | Verify | N/A / Verify | Verify | Verify | Verify | Verify existing conduit reuse, surface raceway where needed, 40% fill, WAP protection-in-place, access above ceilings, and infection-control controls.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
101E | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems.
107 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse.
101C | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer.
WAO Areas | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A | Verify | Verify | Verify | Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
101E | CU-01 / TR cooling assignment verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm.
107 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete.
101C | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains.
WAO Areas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
101E | Verify | 5 kW / 208V rack UPS | Verify | Verify | B03-TR101CA / B03-TR101CB | Verify | Verify | Verify | Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements.
107 | Existing | UPS on floor | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements.
101C | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Existing branch panel / B03-TR101CA/B transition | Verify | Verify | Verify | Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer.
WAO Areas | N/A | N/A | N/A | N/A | Existing / new outlet circuits as needed | N/A | Verify labels | Verify | Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
101E | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2.
107 | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover.
101C | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted.
WAO Areas | N/A | Verify route | N/A | N/A | Verify | Verify | Verify | Verify | Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
101E | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Plans require PACS for TR doors and electrical details include access-controlled door rough-in. Verify access controller, power supply/battery backup, CR/RX/DC/ES/MD devices, reader, strike and door hardware coordination.
101C | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | 101C-CAM-01 Verify | Verify | Verify | Verify | Enlarged plan and schedule identify 101C-CAM-01 and 101C-CK-A. Verify camera/VMS integration, existing camera angles and protection-in-place.
107 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/CCTV/PACS impacts during basement telecom room transfer.
WAO Areas | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Maintain existing camera angles when re-cabling; verify WAP/security/clock/Centrak devices are relabeled and tested.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B03-R1 | All | Existing conditions for Room 101E and transition rooms 107/101C not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | B03 has new TR work tied to existing basement telecom and first-floor DMARC.
B03-R2 | 107 / 101C | Existing DMARC/fiber/telecom equipment may remain active during transfer to Room 101E | Critical | Medium | 8 | Document active services, protect in place, identify OIT/provider cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | Existing 107 rack and 101C DMARC/patch panels must not be disrupted before new services are operational.
B03-R3 | 101E | Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm CU-01/IU serving Room 101E, power source, condensate, controls, BACnet, thermostat and high-temp alarms | Mechanical / Electrical | Closed | CU-01 is referenced in electrical schedules; mechanical assignment must be verified.
B03-R4 | 101E | B03-TR101CA/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panels, breakers, receptacles, SPDs, PXR20 trip units, labels, 30-day load measurement and LOTO needs | Electrical / GCC | Closed | New telecom panels and rack circuits must be proven before acceptance.
B03-R5 | All | 961 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 615 ft and first level 346 ft.
B03-R6 | All | Telecom/fiber cutover could affect active hospital communications and provider/DMARC services | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT/provider coordination and VA acceptance before active connection | Telecom / OIT | Closed | Room 101E supports 206 total ports with allowance and replacement of basement/first-level WAOs.
B03-R7 | 101E / 101C | PACS/CCTV/door hardware coordination may not be ready at room acceptance | High | Medium | 6 | Verify access-control rough-in, power supply/battery backup, reader, strike, door position, 101C-CAM-01 and VMS/PACS test records | Security / Electrical | Closed | Plans identify 101C-CAM-01 and PACS/access control requirements.
B03-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | 50-sheet IFC package with full discipline scope and third-party inspection requirements.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B03-Q1 | Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B03-Q2 | What active services are currently fed from existing Room 107 and DMARC Room 101C? | OIT / Contractor / Provider | Closed |  |  | Potential communications/provider outage
B03-Q3 | What existing equipment transfers to new Room 101E versus remains/decommissions? | OIT / Telecom | Closed |  |  | Cutover and rack elevation risk
B03-Q4 | Which IU/CU pair serves Room 101E and is it on emergency/backup power? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B03-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? | GC / COR | Closed |  |  | Life-safety acceptance risk
B03-Q6 | Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B03-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B03-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B03-P001 | 101E | Existing / New Condition | Room 101E walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, penetrations, PACS and final TR layout |  | Paul |  | B03-R1/B03-R3 | Closed
B03-P002 | 107 | Existing Equipment | Basement existing telecom room 107 rack, UPS on floor, Cisco switch, legacy patch panels, fiber LIU, active service labels and cable entries |  | Paul |  | B03-R1/B03-R2 | Closed
B03-P003 | 101C | Existing DMARC | First-floor existing DMARC Room 101C, patch panels, telecom cabinet, branch panel, provider/fiber equipment, 101C-CAM-01 and active service labels |  | Paul |  | B03-R2/B03-R6 | Closed
B03-P004 | 101E / 101C | Electrical / Security | B03-TR101CA/B panels, rack receptacles, breakers, SPD, UPS/PDU, access controller, CU-01, 101C-CAM-01 and labels |  | Paul |  | B03-R4/B03-R7 | Closed
B03-P005 | 101E | HVAC | IU/CU-01, condensate route, thermostat, BACnet adapter, disconnects, alarm points and emergency power source |  | Paul |  | B03-R3 | Closed
B03-P006 | All | Cable Tray / Firestop | Basement and first-level cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping |  | Paul |  | B03-R5 | Closed
B03-P007 | WAO Areas | Telecom Devices | Representative outlets/WAPs/Centrak/clock/camera locations including 108-A/B/C, 108-CK-A, 107A-AP-A, 101C-CAM-01 and related labels |  | Paul |  | B03-R6 | Closed
B03-P008 | 101E / Existing Rooms | Telecom Acceptance | New racks TR01-101E-1/2, Fiber LIU, Cat6A, patch panels, labels/test records and existing rack transfer work |  | Paul |  | B03-R6/B03-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
101E | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Primary first-level TR with 206 total ports including allowance, two rack IDs, B03-TR101CA/B panels, CU-01, 961 ft cable tray and existing 107/101C transfer scope.
107 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom transition point; protect active services until transfer/cutover complete.
101C | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing first-floor DMARC/telecom transition point; protect provider/fiber/active services and verify final condition.
WAO Areas | 0.5 | 0.5 | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement and first-level WAO/WAP/camera recabling served from Room 101E.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B03.20260316(1).pdf
Drawing Index | 50-sheet Building 03 IFC package includes general, architectural, interiors, fire protection, mechanical, electrical, telecommunications, Room 107 inventory, rack elevations, telecom schedules, cutsheets and photo references.
General Scope Basis | 03G-000 states the project includes new TRs, Cat6A/fiber, racks, UPS, power supplies/electrical distribution, dedicated HVAC, CCTV, fire protection/fire alarm, PACS, commissioning and third-party inspections. No active connection until VA testing/approval/acceptance.
Telecom Basis | 03T-101/401/402 identify first-level Room 101E new scope, Room 101C existing DMARC/demo scope, Room 107 existing scope, 101C-CAM-01 and WAO locations. 03T-403 provides Room 107 inventory reference. 03T-604 identifies existing and new rack elevations. 03T-701 identifies WAO/cable schedule and 961 ft cable tray.
Schedule Basis | 03T-701: RM101E 143 WAO total, 213 active ports per survey, 187 scheduled ports, 206 total ports with 10% allowance, cable tray 615 ft basement + 346 ft first level = 961 ft total, Rack IDs TR01-101E-1 and TR01-101E-2.
Electrical Basis | 03E-601/701/702 identify B03-TR101CA/B, rack UPS/PDU circuits, TR receptacles, access controller, CU-01, SPDs, PXR20 trip units and 30-day load measurement requirements.
Fire / Security Basis | 03FX sheets include fire protection scope. General notes require clean-agent/CO2 extinguisher cabinets within 75 ft of each TR and sprinkler/fire alarm modifications. 03T/03E identify camera and PACS/security requirements.
Photo Basis | 03R-900 provides photo references for Basement Level Existing Telecom Room 107 and First Floor Level Existing DMARC Room 101C.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B109: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B118: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B130: Compare installed materials against approved submittals/spec sections.
Note on B139: Planned vs actual production supports delay/time-extension rebuttal.
Note on B147: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B04_Assessment (hidden)
BUILDING 04 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 04 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 13:34 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 04 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B05, 141, 244A / Multidisciplinary TR Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify TR rooms B05, 141, and 244A; confirm cooling, panel/circuiting, fire alarm/sprinkler impacts, FEC locations, and cutover/phasing plan.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
04 | B05 | Basement | Existing telecom / service area | TR | 2 | 0 | Verify | 04A-400 / 04T-604 / 04E-701 | Rack elevations show B05 with Rack 1 of 2 and Rack 2 of 2; new B04-TRB05A/B panels and NPA-TR feed shown.
04 | 141 | First | Existing room to be converted / upgraded | TR | 1 | 1 | Verify | 04A-401 / 04T-604 / 04E-701 | Architectural enlarged views identify Room 141; new 45-minute rated door/frame, 1-hour/smoke-rated envelope, open-to-deck TR, and future rack.
04 | 244A | Second | Existing or renovated telecom area | TR | 1 | 1 | Verify | 04T / 04E-701 | Panel schedule identifies B04-TR244A; room requires field verification of rack count, cooling, pathways, fire protection, and PACS/CCTV requirements.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify existing utilities, abatement, wall/firestop conditions, and two-rack layout.
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing wall to become 1-hour fire/smoke rated; open to deck; new 45-minute rated door and access-control hardware coordination.
244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-floor TR referenced by electrical panel schedule; field verify room conditions and plan locations.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning.
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies.
244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up.
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control.
244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify cooling unit, routing, condensate, controls, and emergency/backup power path.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B05 | Verify | 5 kW | Verify | Verify | B04-NPA-TR / B04-TRB05A / B04-TRB05B | Verify | Verify | Verify | Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits.
141 | Verify | 5 kW | Verify | Verify | B04-TR141A | Verify | Verify | Verify | Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting.
244A | Verify | 5 kW | Verify | Verify | B04-TR244A | Verify | Verify | Verify | Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU.
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU.
244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | TR/panel identified; verify rack elevation and pathway details against 04T sheets.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify access-controlled TR door, camera, and VMS/PACS integration.
141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural notes require door/access control coordination; verify card reader/electric strike rough-in.
244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify room security details and device integration with VA systems.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B04-R1 | All | Existing conditions across basement/first/second TR areas not verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / GC | Closed | B04 has multiple TR work areas.
B04-R2 | B05 | Basement TR routing may conflict with existing utilities / abatement areas | High | Medium | 6 | Coordinate hazardous material survey, utility locations, penetrations, and pathway routing | GCC / Contractor | Closed | Hazardous drawings included for basement and first levels.
B04-R3 | 141 | 1-hour fire/smoke-rated envelope and 45-minute door not field verified | High | Medium | 6 | Inspect rated walls, door/frame, ceiling/open-to-deck conditions, and penetrations | GCC / GC | Closed | Architectural notes identify new 45-minute door/frame and rated wall work.
B04-R4 | All | Cooling emergency power / 24/7 continuity not verified | Critical | Medium | 8 | Confirm source power for indoor/outdoor units, controls, condensate pumps, and alarms | GCC / VA / Electrical | Closed | Owner continuity item.
B04-R5 | All | UPS/PDU/rack electrical source and load coordination unresolved | High | Medium | 6 | Verify panel schedules, source, SPD, breaker sizes, labeling, and load measurements | Electrical / GCC | Closed | Panel schedule shows B04-NPA-TR, TRB05A/B, TR141A, TR244A.
B04-R6 | All | Telecom/fiber cutover could affect active hospital communications | Critical | Medium | 8 | Require phasing plan, test results, and VA/OIT acceptance before cutover | Telecom / OIT / GC | Closed | All telecom equipment/cabling must be tested and accepted before connecting active operations.
B04-R7 | All | Fire alarm/sprinkler impairments during construction could affect occupied operations | Critical | Medium | 8 | Track impairments, fire watch, temporary firestopping, and third-party reports | GC / FP / FA | Closed | Shutdowns limited to one at a time campus-wide.
B04-R8 | All | Commissioning and third-party inspection reports incomplete before turnover | High | Medium | 6 | Track Cx and 3rd-party inspection deliverables by trade | GC / Cx Manager | Closed | Required by cover sheet and commissioning scope.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B04-Q1 | Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? | VA / OIT / Designer | Closed |  |  | Incomplete room inventory / missed scope
B04-Q2 | Are B05, 141, and 244A cooling systems on emergency/backup power? | VA / Electrical / Mechanical | Closed |  |  | Cooling continuity not confirmed
B04-Q3 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed |  |  | Life safety acceptance risk
B04-Q4 | What is the approved migration and cutover sequence for active Building 04 services? | OIT / Contractor | Closed |  |  | Potential communications outage
B04-Q5 | Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? | GC / COR | Closed |  |  | Work stoppage or exposure risk
B04-Q6 | Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? | Electrical / Designer | Closed |  |  | Electrical delay or overload risk
B04-Q7 | Are all rated wall/floor penetrations and speed sleeves identified and firestopped? | GC / Designer | Closed |  |  | Fire/smoke spread risk
B04-Q8 | Which third-party tests, commissioning forms, and acceptance documents are required before VA turnover? | GC / Cx Manager | Closed |  |  | Incomplete turnover package
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B04-P001 | B05 | Existing Condition | Basement TR B05 existing conditions, racks, utilities, penetrations, panels |  | Paul |  | B04-R1/B04-R2 | Closed
B04-P002 | 141 | Existing Condition | Room 141 existing conditions, door/walls/ceiling/window/floor conditions |  | Paul |  | B04-R3 | Closed
B04-P003 | 244A | Existing Condition | Room 244A TR existing condition and panel/rack area |  | Paul |  | B04-R1 | Closed
B04-P004 | All | Firestop | All floor/wall/sleeve/tray penetrations before and after firestop |  | Paul |  | B04-R7 | Closed
B04-P005 | All | HVAC | Cooling units, condensate routing, controls, high-temp alarms |  | Paul |  | B04-R4 | Closed
B04-P006 | All | Electrical | Panels, breakers, UPS/PDU receptacles, SPD, grounding/bonding |  | Paul |  | B04-R5 | Closed
B04-P007 | All | Telecom | Racks, ladder tray, fiber, Cat6A, labels, LIU, cable managers |  | Paul |  | B04-R6 | Closed
B04-P008 | All | Security | PACS, card reader, electric strike, camera, motion sensor rough-in |  | Paul |  | B04-R3 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B05 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Two-rack basement TR; full field verification required.
141 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | First-floor TR with rated wall/door and future rack.
244A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Second-floor TR/panel scope; verify rack/equipment locations.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B04.20260316.pdf
Drawing Index | 74-sheet Building 04 IFC package includes general, hazardous, architectural, interiors, fire protection, mechanical, electrical, telecommunications, and reference sheets.
Architectural Basis | Room 141 notes identify new 45-minute fire-rated door/frame, FEC within 75 ft, open-to-deck telecom room, temporary dust barrier, existing wall to become 1-hour fire/smoke-rated, flooring removal, and potential abatement.
Telecom Basis | 04T-604/605 rack elevations identify B05 as two racks and 141 as one rack plus future rack; 04T-501 provides 4-post rack, grounding busbar, 5kW UPS, Zone PDU, patch panel, cable tray, and labeling standards.
Electrical Basis | 04E schedules identify B04-NPA-TR in Telecom Room B05 and branch panel/circuit references for B04-TRB05A, B04-TRB05B, B04-TR141A, and B04-TR244A.
General / Operations Basis | Cover/general notes require third-party inspections, coordination drawings before work, all impacted systems commissioned/recommissioned, VA acceptance before active connections, shutdowns limited one at a time, and contractor responsibility for system modifications.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B100: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B109: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B121: Compare installed materials against approved submittals/spec sections.
Note on B130: Planned vs actual production supports delay/time-extension rebuttal.
Note on B138: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B05_Assessment (hidden)
BUILDING 05 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 05 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 55% | Construction Ready | No
Review Date | 2026-06-25 13:44 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 05 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | Room 150 / Telecom Enclosure (TE)
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified.
HVAC Status | N/A | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | N/A | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify Room 150 TE location, existing 153-A equipment to remain/transition, electrical source, UPS/PDU receptacles, PACS/CCTV requirements, firestopping, and cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
05 | 150 | First | Telecom / equipment location | Telecom Enclosure (TE) | 1 | 0 | Verify | 05T-604 / 05T-401 / 05E-401 | New elevation identifies Room 150 with one 12RU Telecom Enclosure; includes APC UPS, PDUs, cable managers, 48-port patch panels, Cat6A patch panel, and Fiber LIU.
05 | 153-A | First | Existing wall-mounted TE / existing rack area | Existing equipment / transition point | 1 | 0 | Verify | 05T-604 | Existing elevation shows wall or wall-mount TE at Room 153-A with Cisco switches and multiple legacy 24-port patch panels; existing floor UPS shown.
2. ROOM READINESS | [8 empty] | Existing active telecommunications equipment remains in Room 153-A. Environmental conditioning supporting this equipment was not identified. Contractor shall verify that operating conditions comply with equipment manufacturer requirements for all active equipment remaining in service.
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
150 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | TE installation; verify mounting wall/backing, access clearance, power location, pathway/firestop, and room readiness.
153-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing equipment area; verify what remains operational and how legacy equipment transitions to new TE.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
150 | N/A | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts.
153-A | N/A | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling.
153-A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Existing wall/wall-mount TE area; verify existing environmental conditions during field survey.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
150 | Verify | APC UPS / TE scale | Verify | Verify | Verify | Verify | Verify | Verify | 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source.
153-A | Existing | Existing floor UPS | Existing | Verify | Verify | Verify | Verify | Verify | Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
150 | Verify | N/A / TE | Verify | Verify | Verify | Verify | Verify | Verify | New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU.
153-A | Existing | N/A / Wall TE | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
150 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Project general scope includes CCTV and PACS for telecom spaces; verify whether TE location receives camera/access control or is served by existing room controls.
153-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing security protection and whether access-control work is needed for existing TE area.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B05-R1 | 150 | Telecom Enclosure installation details not field verified | High | Medium | 6 | Survey wall/backing, clearances, power, conduit/wireway, and access path before installation | GCC / Contractor | Closed | TE rather than full TR.
B05-R2 | 153-A | Existing legacy equipment/cabling may remain active during cutover | Critical | Medium | 8 | Document active services, create cutover plan, protect-in-place until new TE is operational | Telecom / OIT / Contractor | Closed | Existing Cisco switches and patch panels shown.
B05-R3 | All | Mechanical/fire protection scope excluded may hide interface risks | Medium | Medium | 4 | Confirm no added cooling/sprinkler work is required and document basis for N/A | GCC / VA / Designer | Closed | Cover sheet specifically excludes mechanical and fire protection scope.
B05-R4 | 150 | Electrical panel/circuit source for TE equipment not confirmed | High | Medium | 6 | Verify 05E-401/501/601/701 schedules, UPS/PDU receptacles, labels, and emergency power source | Electrical / GCC | Closed | UPS/PDU devices shown in rack elevation.
B05-R5 | All | Firestopping/penetration sealing still required despite fire protection scope exclusion | High | Medium | 6 | Inspect all new and reused conduits, sleeves, wall/floor penetrations, and temporary firestop | GC / Firestop Contractor | Closed | Cabling work can create rated assembly risk.
B05-R6 | All | Commissioning / acceptance documentation may be treated as minor due to TE scope | Medium | Medium | 4 | Track testing, labeling, OIT acceptance, third-party inspections, and as-builts | GCC / GC / OIT | Closed | All telecom cabling must be tested and accepted.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B05-Q1 | Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? | VA / OIT / Designer | Closed |  |  | Room inventory could be wrong
B05-Q2 | What active services are currently fed from the existing 153-A TE/legacy patch panels? | OIT / Contractor | Closed |  |  | Potential communications outage
B05-Q3 | What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? | OIT / Contractor | Closed |  |  | Cutover risk
B05-Q4 | Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? | Electrical / Designer | Closed |  |  | Power source cannot be verified
B05-Q5 | Is emergency/backup power required or provided for the TE UPS/PDU source? | VA / Electrical | Closed |  |  | Continuity requirement unclear
B05-Q6 | Are firestopping locations and surface raceway/conduit routes shown and coordinated? | GC / Designer | Closed |  |  | Rated assembly/firestop risk
B05-Q7 | Does Room 150 or existing Room 153-A require PACS/CCTV modifications, or is existing security adequate? | Security / VA | Closed |  |  | Security acceptance risk
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B05-P001 | 150 | Existing Condition | Room 150 wall/TE location, mounting surface, clearances, power, pathway |  | Paul |  | B05-R1/B05-R4 | Closed
B05-P002 | 153-A | Existing Condition | Existing wall/wall-mount TE, Cisco switches, legacy patch panels, floor UPS |  | Paul |  | B05-R2 | Closed
B05-P003 | All | Firestop | All new/reused penetrations and surface raceway/conduit routes |  | Paul |  | B05-R5 | Closed
B05-P004 | 150 | Electrical | UPS/PDU outlet, circuit label, panel source, grounding/bonding |  | Paul |  | B05-R4 | Closed
B05-P005 | All | Telecom | TE, patch panels, Fiber LIU, labels, testing records, as-built conditions |  | Paul |  | B05-R6 | Closed
B05-P006 | All | Security | Door/security/CCTV/PACS conditions at TE location |  | Paul |  | B05-R6 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
150 | 50% | 50% | N/A | 50% | 50% | Verify | 50% | Partial / Yellow | New 12RU TE; field verification required.
153-A | 50% | 50% | N/A | 50% | 50% | Verify | 50% | Partial / Yellow | Existing TE/legacy equipment transition point.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B05.20260316.pdf
Drawing Index | 31-sheet Building 05 IFC package includes general, architectural, electrical, telecommunications, rack elevations, schedules, details, and references.
Special Scope Note | Cover sheet states: this building receives a Telecom Enclosure (TE); mechanical and fire protection scope has been excluded.
Telecom Basis | 05T-604 identifies new Room 150 Telecom Enclosure 12RU and existing Room 153-A wall/wall-mount TE with Cisco switches and legacy patch panels.
Electrical Basis | 05T-604 identifies UPS/PDU equipment in the TE elevation; verify 05E schedules and field panel/circuit source before work.
Operational Basis | General notes require existing ports replaced, existing conduits reused where possible, 10% allowance for data ports, coordination with COR/A/E, testing/labeling, and acceptance before tying to active operations.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B86: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B95: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B107: Compare installed materials against approved submittals/spec sections.
Note on B116: Planned vs actual production supports delay/time-extension rebuttal.
Note on B124: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B06_Assessment (hidden)
BUILDING 06 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 06 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 13:52 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 06 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B-01, 178, 233 / Multidisciplinary TR Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify existing B-01 equipment, Rooms 178 and 233, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
06 | B-01 | Basement | Existing wall/wall-mount TE and floor UPS | Existing equipment / transition point | 1 | 0 | Verify | 06T-604 | Existing basement wall/wall-mount TE with Cisco switches, legacy Ortronics 48-port patch panels, and floor UPS.
06 | 178 | First | Existing telecom room / group therapy area adjacent | Telecom Room | 2 | 0 | Verify | 06A-401 / 06E-401 / 06T-604 / 06E-701 | Room 178 shown as 114 SF Telecom Room; existing 2-post racks and new B06-TR178A/B panel work with IU-1-01 cooling.
06 | 233 | Second | Data closet / patient toilet area conversion | Telecom Room | 1 | 1 | Verify | 06A-402 / 06E-401 / 06T-604 / 06E-701 | Room 233 shown as 119 SF Telecom Room/Data Closet; future rack elevation, B06-TR233A/B panels, and IU-2-01 cooling.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement TE/UPS; protect active services and verify transitions.
178 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify rated construction, door/security, equipment clearance, cooling unit, and electrical panels.
233 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR/Data Closet; architectural notes identify rated wall/door work and fire extinguisher requirements.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B-01 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing equipment area; verify no cabling penetrations are left unsealed.
178 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs.
233 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B-01 | Existing | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify basement equipment environmental condition and any heat/load issues during cutover.
178 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route.
233 | IU-2-01 / CU-2-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B-01 | Existing | Existing floor UPS | Existing | Verify | Verify | Verify | Verify | Verify | Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements.
178 | Verify | 5 kW / rack equipment | Verify | Verify | B06-NP-TR / B06-EP-TR / B06-TR178A / B06-TR178B | Verify | Verify | Verify | Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation.
233 | Verify | 5 kW / rack equipment | Verify | Verify | B06-TR233A / B06-TR233B | Verify | Verify | Verify | Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B-01 | Existing | N/A / TE | Existing | Verify | Verify | Verify | Verify | Verify | Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS.
178 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification.
233 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
B-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing basement access/security while protecting active equipment.
178 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged plan references existing card reader to remain/protect in place and new tri-tech motion sensor; verify PACS/CCTV integration.
233 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify door hardware/access control, motion sensor, camera, and VA security integration.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B06-R1 | All | Existing conditions across B-01, 178 and 233 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | Building 06 includes basement, first and second level work.
B06-R2 | B-01 | Existing basement equipment may remain active during cutover | Critical | Medium | 8 | Document active services and protect in place until new system is tested and accepted | Telecom / OIT | Closed | Existing Cisco/legacy patch panels and UPS shown.
B06-R3 | 178 | Electrical panel replacement/new telecom power could interrupt active systems | Critical | Medium | 8 | Coordinate load measurement, panel renovation, shutdowns and temporary power plan | Electrical / GCC | Closed | B06-EP-TR and B06-TR178A/B panel work.
B06-R4 | 233 | Room 233 conversion/rated wall and door work may impact adjacent patient toilet/private bath areas | High | Medium | 6 | Verify phasing, barriers, infection control and temporary life-safety provisions | GC / VA | Closed | Architectural enlarged views show TR 233 adjacent to patient toilet/private bath.
B06-R5 | 178/233 | Dedicated cooling emergency power, controls, condensate and BACnet interface not verified | Critical | Medium | 8 | Confirm emergency power source, disconnects, condensate routes, BACnet adapter and high-temp alarms | Mechanical / Electrical | Closed | IU-1-01/CU-1-01 and IU-2-01/CU-2-01.
B06-R6 | All | Fire alarm/sprinkler impairments and penetrations may affect occupied operations | Critical | Medium | 8 | Track impairments, fire watch, temporary firestop and third-party reports | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide.
B06-R7 | All | Telecom/fiber cutover could affect active hospital communications | Critical | Medium | 8 | Require cutover plan, test results and VA/OIT acceptance before energizing active operations | Telecom / OIT | Closed | All cabling must be tested, approved and accepted.
B06-R8 | All | Commissioning/third-party inspection reports may not be ready at turnover | High | Medium | 6 | Track commissioning and third-party inspection deliverables by trade | GC / Cx Manager | Closed | Required by cover sheet and commissioning sections.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B06-Q1 | Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B06-Q2 | What active services are fed from existing B-01 and Room 178 legacy equipment? | OIT / Contractor | Closed |  |  | Potential communications outage
B06-Q3 | What is the approved cutover sequence for B-01, 178 and 233? | OIT / Contractor | Closed |  |  | Cutover risk
B06-Q4 | Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B06-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed |  |  | Life safety acceptance risk
B06-Q6 | Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B06-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B06-Q8 | Which commissioning/third-party tests must be complete before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B06-P001 | B-01 | Existing Condition | Existing basement wall/wall-mount TE, Cisco switches, legacy patch panels, floor UPS |  | Paul |  | B06-R1/B06-R2 | Closed
B06-P002 | 178 | Existing Condition | Room 178 TR, existing 2-post racks, panels, card reader/security, HVAC location |  | Paul |  | B06-R1/B06-R3 | Closed
B06-P003 | 233 | Existing Condition | Room 233/Data Closet, adjacent toilet/bath areas, walls/door/ceiling/penetrations |  | Paul |  | B06-R4 | Closed
B06-P004 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B06-R6 | Closed
B06-P005 | 178/233 | HVAC | IU/CU equipment, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm |  | Paul |  | B06-R5 | Closed
B06-P006 | All | Electrical | B06-NP-TR, B06-EP-TR, B06-TR178A/B, B06-TR233A/B, breakers, SPD, labels |  | Paul |  | B06-R3/B06-R6 | Closed
B06-P007 | All | Telecom | Racks, ladder tray, fiber, Cat6A, LIU, patch panels, labels, test records |  | Paul |  | B06-R7 | Closed
B06-P008 | All | Security | Card readers, electric strikes, door position, motion sensors, CCTV/PACS integration |  | Paul |  | B06-R4 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B-01 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Existing equipment transition point; protect active services.
178 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | First-floor TR with new cooling and electrical scope.
233 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Second-floor TR/Data Closet with rated construction and future rack scope.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B06.20260316.pdf
Drawing Index | 63-sheet Building 06 IFC package includes architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules, risers, rack elevations, and references.
Telecom Basis | 06T-604 identifies existing basement B-01 wall/wall-mount TE and UPS, existing Room 178 racks, and a future new rack elevation for Room 233.
Electrical Basis | 06E-401/701 identify Room 178 and Room 233 panels/circuits including B06-NP-TR, B06-EP-TR, B06-TR178A/B and B06-TR233A/B, with panel load measurement and SPD requirements.
Mechanical Basis | 06M enlarged plans show new IU-1-01/CU-1-01 for Room 178 and IU-2-01/CU-2-01 for Room 233, with condensate pumps, thermostats, BACnet adapters and emergency power provisions.
Architectural / Life Safety Basis | 06A-402 identifies Room 233/data closet enlarged views with 1-hour fire/smoke-rated wall work, FEC within 75 ft, and new 45-minute fire-rated door/frame.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data port allowance, third-party inspections, commissioning/recommissioning, coordination drawings, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B100: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B109: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B121: Compare installed materials against approved submittals/spec sections.
Note on B130: Planned vs actual production supports delay/time-extension rebuttal.
Note on B138: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B07_Assessment (hidden)
BUILDING 07 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 07 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 14:07 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 07 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B-18, 228A / Multidisciplinary TR Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify TR B-18 and 228A; confirm rack/equipment layout, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
07 | B-18 | Basement | Existing office / telecom-service area | Telecom Room | 1 | 1 | Verify | 07A-400 / 07E-401 / 07T-604 / 07M-701 | Rack elevation shows B-18 as 1 of 1 + future, 4-post floor rack, UPS, future Zone PDU, network switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
07 | 228A | Second | Social worker shared / adjacent OPM storage and DOM MSA area | Telecom Room | 1 | 1 | Verify | 07A-401 / 07E-401 / 07T-604 / 07M-701 | Architectural enlarged view identifies Telecom Room 228A at 236 SF; includes fire-rated door/wall work, FEC requirement, exterior furring wall/window enclosure and temporary dust barrier.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B-18 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify office-to-TR conversion conditions, existing utilities, wall/ceiling/firestop conditions and future rack clearance.
228A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-floor TR; verify 1-hour fire/smoke-rated wall, 45-minute door/frame, open-to-deck/furring wall details, access control and equipment clearances.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B-18 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination.
228A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B-18 | IU-0-01 / CU-0-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm.
228A | IU-2-01 / CU-2-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B-18 | Verify | 5 kW / rack equipment | Verify | Verify | B07-TRB18A / B07-TRB18B | Verify | Verify | Verify | Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement.
228A | Verify | 5 kW / rack equipment | Verify | Verify | B07-TR228A / B07-TR228B | Verify | Verify | Verify | Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B-18 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU.
228A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
B-18 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify access control, door hardware and CCTV/PACS integration for basement TR.
228A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural notes require access control hardware modifications at new rated door; verify card reader, electric strike, door position switch, motion sensor and camera.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B07-R1 | All | Existing conditions for B-18 and 228A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B07 includes basement and second-floor TR scope.
B07-R2 | B-18 | Basement TR conversion may conflict with existing utilities, office finishes or active pathways | High | Medium | 6 | Verify routing, clearances, penetrations, existing conduit and access before work | GC / Telecom | Closed | Basement B-18 shown on rack elevation and electrical enlarged plans.
B07-R3 | 228A | Second-floor rated wall/door work and exterior furring wall/window enclosure could affect schedule | High | Medium | 6 | Coordinate architectural work, door/frame, wall rating, furring wall, finishes and infection control barriers | GC / VA | Closed | 07A-401 notes include 45-minute rated door and new furring wall at exterior wall.
B07-R4 | B-18/228A | Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified | Critical | Medium | 8 | Confirm IU/CU assignments, emergency source, BACnet/interface, condensate pump routing and alarm points | Mechanical / Electrical | Closed | IU-0-01/CU-0-01 and IU-2-01/CU-2-01 schedules.
B07-R5 | All | Electrical panel/circuit source and rack load coordination unresolved | High | Medium | 6 | Verify B07-TRB18A/B and B07-TR228A/B panel schedules, circuit labels, SPDs and load measurements | Electrical / GCC | Closed | Electrical enlarged plans identify panel/circuit references.
B07-R6 | All | Telecom/fiber cutover may affect active hospital communications | Critical | Medium | 8 | Require cutover plan, test results, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | All cabling must be tested, approved and accepted before connecting to active operations.
B07-R7 | All | Fire alarm/sprinkler impairments and firestopping could affect occupied operations | Critical | Medium | 8 | Track impairments, temporary firestopping, fire watch, sprinkler/head changes and FA acceptance testing | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide.
B07-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspection, testing, labels and as-built deliverables by trade | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B07-Q1 | Confirm final TR scope: B-18 basement and 228A second floor only? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B07-Q2 | Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? | Mechanical / Designer | Closed |  |  | Cooling scope unclear
B07-Q3 | Are cooling units and controls on emergency/backup power? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity not confirmed
B07-Q4 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed |  |  | Life safety acceptance risk
B07-Q5 | What active services are currently fed from B-18 and/or existing pathways serving 228A? | OIT / Contractor | Closed |  |  | Potential communications outage
B07-Q6 | Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B07-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B07-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B07-P001 | B-18 | Existing Condition | Basement TR B-18 existing room, walls, ceiling, floor, utilities, penetrations and pathway |  | Paul |  | B07-R1/B07-R2 | Closed
B07-P002 | 228A | Existing Condition | Second-floor TR 228A, door/wall/furring/window conditions, adjacent spaces and pathway |  | Paul |  | B07-R1/B07-R3 | Closed
B07-P003 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B07-R7 | Closed
B07-P004 | B-18/228A | HVAC | IU/CU units, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B07-R4 | Closed
B07-P005 | All | Electrical | B07-TRB18A/B and B07-TR228A/B panels, breakers, SPD, rack receptacles and labels |  | Paul |  | B07-R5 | Closed
B07-P006 | All | Telecom | Racks, ladder tray, fiber, Cat6A, patch panels, LIU, labels and test records |  | Paul |  | B07-R6 | Closed
B07-P007 | All | Security | Card reader, electric strike, door position, CCTV/PACS and motion sensors |  | Paul |  | B07-R3 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B-18 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Basement TR; field verification required.
228A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Second-floor TR; rated wall/door and cooling coordination required.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B07.20260316.pdf
Drawing Index | 60-sheet Building 07 IFC package includes general, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules, risers, rack elevations and reference photos.
Telecom Basis | 07T-604 identifies B-18 as 1 rack plus future with UPS, future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU; 228A is shown on second-level telecom/electrical enlarged plans.
Architectural Basis | 07A-401 identifies Telecom Room 228A at 236 SF and includes new 45-minute rated door/frame, FEC within 75 ft, temporary dust barrier, new furring wall at exterior wall, and finish/transition requirements.
Mechanical Basis | 07M-701 split-system schedules list IU-0-01/CU-0-01 at 18,000 BTUH and IU-2-01/CU-2-01 at 36,000 BTUH; field verify room assignment, power and controls.
Electrical Basis | 07E-401 identifies B07-TRB18A/B and B07-TR228A/B circuit references for basement and second-floor TRs; verify panel schedules, rack receptacles, SPDs, source and emergency power.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B91: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B100: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B112: Compare installed materials against approved submittals/spec sections.
Note on B121: Planned vs actual production supports delay/time-extension rebuttal.
Note on B129: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B08_Assessment (hidden)
BUILDING 08 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 08 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 14:18 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 08 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B-15, B12B, 2065A / TR-TE Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify B-15, B12B, and 2065A; confirm active services, 2065A rack layout, panel/power source, IU/CU cooling, hazardous material/abatement impacts, FEC locations, PACS/CCTV, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
08 | B-15 | Basement | Existing wall/wall-mounted TE and floor UPS | Existing equipment / transition point | 2 | 0 | Verify | 08T-604 | Existing rack elevation identifies Building 08 basement Room B-15 with wall/wall-mounted TE, legacy patch panels, legacy Fiber LIU, and floor UPS.
08 | B12B | Basement | Office / basement cabling area | Telecom enclosure / TE cabling service area | 1 | 0 | Verify | 08A-401 / 08E-701 / 08T-701 | Door schedule identifies B12B as Office with 45-minute door; telecom schedule and electrical schedule reference TE01-B12B-1 and TE receptacle Room B12B. Field verify actual TE/equipment scope.
08 | 2065A | Second | Existing copy/office/storage area converted | Telecom Room | 2 | 0 | Verify | 08A-401 / 08E-701 / 08T-604 / 08M-701 | Telecom Room 2065A, 127 SF; new rack elevation shows two 4-post floor racks, UPS, Zone PDU, network switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B-15 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom equipment; protect active services and verify legacy equipment status.
B12B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement Office/TE area; verify wall/door rating, pathways, outlet/panel scope, firestopping and actual TE location.
2065A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New Telecom Room; verify 1-hour fire/smoke-rated room, 45-minute door/frame, open-to-deck construction, static-dissipative floor sealer, clearances and equipment layout.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B-15 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected.
B12B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers.
2065A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B-15 | Existing | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing environmental conditions and whether active legacy equipment remains during cutover.
B12B | N/A / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Field verify whether TE equipment load requires cooling or if served by existing building HVAC.
2065A | IU-2-01 / CU-2-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B-15 | Existing | Existing floor UPS | Existing | Verify | Verify | Verify | Verify | Verify | Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements.
B12B | Verify | TE scale | Verify | Verify | TE receptacle Room B12B / B08-TR2065AB reference | Verify | Verify | Verify | Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel.
2065A | Verify | 5 kW / rack equipment | Verify | Verify | B08-TR2065AA / B08-TR2065AB | Verify | Verify | Verify | Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B-15 | Existing | N/A / TE | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS.
B12B | Verify | N/A / TE | Verify | Verify | Verify | Verify | Verify | Verify | Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance.
2065A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
B-15 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing basement access/security while protecting active equipment.
B12B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 45-minute door shown; verify access-control hardware applicability and whether TE is secured.
2065A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Door schedule/hardware note requires coordination with electrical/access control; verify card reader, electric strike, door position, motion sensor, camera and VA integration.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B08-R1 | All | Existing conditions for B-15, B12B and 2065A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B08 includes existing equipment, TE/cabling area and new TR scope.
B08-R2 | B-15 | Existing basement legacy equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place and define cutover/demo sequence | Telecom / OIT | Closed | Existing TE, patch panels, Fiber LIU and UPS shown.
B08-R3 | B12B | Basement B12B appears as Office in architectural schedule but TE in telecom/electrical schedules | High | Medium | 6 | Field verify actual TE location, room name, door/wall rating and panel/cable routing | GCC / VA / Designer | Closed | Potential room/scope mismatch.
B08-R4 | 2065A | Second-floor Telecom Room conversion includes rated wall/door/open-to-deck work and possible hazardous material impacts | High | Medium | 6 | Coordinate architectural work, dust barriers, floor abatement, FEC and rated assemblies before construction | GC / VA | Closed | Hazardous material abatement plan included for Level 2.
B08-R5 | 2065A | Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified | Critical | Medium | 8 | Confirm IU/CU assignment, emergency source, BACnet/interface, condensate routing and alarm points | Mechanical / Electrical | Closed | IU-2-01/CU-2-01 scheduled at 36,000 BTUH.
B08-R6 | All | Electrical panel/circuit source and rack load coordination unresolved | High | Medium | 6 | Verify B08-TR2065AA/AB panel schedules, rack receptacles, SPD, labels and load measurement requirements | Electrical / GCC | Closed | Panel schedule includes telecom panelboard notes and 30-day load measurement requirements.
B08-R7 | All | Fire alarm/sprinkler impairments and firestopping could affect occupied operations | Critical | Medium | 8 | Track impairments, temporary firestopping, fire watch, sprinkler/device changes and FA acceptance testing | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide.
B08-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, test records, labels, OIT acceptance and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B08-Q1 | Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? | VA / OIT / Designer | Closed |  |  | Room inventory may miss scope
B08-Q2 | What active services are currently fed from existing B-15 equipment? | OIT / Contractor | Closed |  |  | Potential communications outage
B08-Q3 | Is B12B truly a TE/equipment location or only a cabling pathway/service area? | VA / Designer / Contractor | Closed |  |  | Scope ambiguity
B08-Q4 | Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B08-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? | GC / COR | Closed |  |  | Life safety acceptance risk
B08-Q6 | Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B08-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B08-Q8 | Which hazardous material/abatement steps apply to Level 2 floor penetrations and flooring removal? | GC / IH / COR | Closed |  |  | Work delay or exposure risk
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B08-P001 | B-15 | Existing Condition | Existing basement TE, legacy patch panels, Fiber LIU, floor UPS and pathways |  | Paul |  | B08-R1/B08-R2 | Closed
B08-P002 | B12B | Existing Condition | Basement B12B office/TE location, door, pathways, receptacles, panel source and penetrations |  | Paul |  | B08-R3 | Closed
B08-P003 | 2065A | Existing Condition | Second-floor TR 2065A room, door/walls/ceiling/floor, exterior furring/window, penetrations |  | Paul |  | B08-R4 | Closed
B08-P004 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B08-R7 | Closed
B08-P005 | 2065A | HVAC | IU-2-01/CU-2-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power |  | Paul |  | B08-R5 | Closed
B08-P006 | All | Electrical | B08-TR2065AA/AB panels, breakers, SPD, rack receptacles, TE receptacle B12B and labels |  | Paul |  | B08-R6 | Closed
B08-P007 | All | Telecom | B-15 legacy equipment, B12B TE schedule, 2065A racks, fiber, Cat6A, patch panels, LIU, labels and test records |  | Paul |  | B08-R2/B08-R8 | Closed
B08-P008 | All | Security | Card reader, electric strike, door position, CCTV/PACS and motion sensors |  | Paul |  | B08-R4 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B-15 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Existing equipment transition point; protect active services.
B12B | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Basement office/TE ambiguity requires field verification.
2065A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | New second-floor TR with two racks, cooling, rated work and possible abatement.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B08.20260316.pdf
Drawing Index | 56-sheet Building 08 IFC package includes general, hazardous material abatement, architectural, interiors, fire protection, mechanical, electrical, telecommunications, schedules, rack elevations and reference photos.
Architectural Basis | 08A-401 identifies B12B and Telecom Room 2065A enlarged views; 2065A is 127 SF, open to deck, with new 45-minute fire-rated door/frame, fire extinguisher cabinet requirement, 1-hour fire/smoke-rated existing wall upgrade, flooring removal and potential abatement at penetrations.
Telecom Basis | 08T-604 identifies existing basement Room B-15 equipment and new second-level Room 2065A two-rack layout; 08T-701 identifies B12B basement data device schedule and TE01-B12B-1 rack ID with 80 WAO total and 128 total ports with 10% allowance.
Mechanical Basis | 08M-701 lists IU-2-01/CU-2-01 36,000 BTUH split system with emergency power connection, condensate pump and BACnet controller requirements; verify service to TR 2065A.
Electrical Basis | 08E-701 identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and TE receptacle Room B12B; panel notes include SPD and load measurement requirements.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B100: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B109: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B121: Compare installed materials against approved submittals/spec sections.
Note on B130: Planned vs actual production supports delay/time-extension rebuttal.
Note on B138: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B09_Assessment (hidden)
BUILDING 09 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
HVAC Status | 09 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 14:28 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 09 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B01, 104B, 206A / Multidisciplinary TR Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify B01, 104B, and 206A; confirm existing equipment and active services, panel sources, IU/CU cooling, fire alarm/sprinkler impacts, FEC locations, PACS/CCTV scope, hazardous/abatement impacts, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
09 | B01 | Basement | Storage / existing telecom equipment area | Telecom Room | 2 | 0 | Verify | 09A-400 / 09E-402 / 09T-604 / 09E-701 | Telecom Room B01, 200 SF; existing/new telecom equipment shown with panels B09-TRB01A/B and cooling circuits CU-0-1, CU-1-1, CU-2-1 in electrical schedule/enlarged plans.
09 | 104B | First | Interview room / existing area converted | Telecom Room | 2 | 0 | Verify | 09A-401 / 09E-401 / 09T-604 / 09E-701 | Telecom Room 104B, 85 SF; panels B09-TR104BA/B shown; first-level enlarged plans identify access control/security devices, IU-1-01, and TR receptacle/rack circuiting.
09 | 206A | Second | Nursing service / adjacent office area | Telecom Room | 2 | 0 | Verify | 09A-401 / 09E-401 / 09T-604 / 09E-701 | Telecom Room 206A, 120 SF; panels B09-TR206AA/B shown; second-level enlarged plans identify IU-2-01, TR circuits, security devices, and room layout adjacent to Nursing Service 206.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify existing storage-to-TR conversion, wall/ceiling/floor condition, active equipment, pathways, and clearances.
104B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated wall requirements, 45-minute door/frame, access control, security devices, and equipment clearance.
206A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR; verify rated wall/door, open-to-deck conditions, penetrations, cooling unit, and rack/service clearance.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR.
104B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft.
206A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B01 | IU-0-01 / CU-0-1 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms.
104B | IU-1-01 / CU-1-1 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power.
206A | IU-2-01 / CU-2-1 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B01 | Verify | 5 kW / rack equipment | Verify | Verify | B09-TRB01A / B09-TRB01B / B09-EP-TR | Verify | Verify | Verify | Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes.
104B | Verify | 5 kW / rack equipment | Verify | Verify | B09-TR104BA / B09-TR104BB | Verify | Verify | Verify | Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits.
206A | Verify | 5 kW / rack equipment | Verify | Verify | B09-TR206AA / B09-TR206AB | Verify | Verify | Verify | Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover.
104B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records.
206A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Enlarged plans show existing/new security boxes, network door controller, camera/security scope; verify PACS/CCTV integration and protection of active security systems.
104B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 104B camera designation; verify card reader, electric strike, door contact, motion and camera.
206A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 206A camera designation; verify PACS/VMS integration and commissioning.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B09-R1 | All | Existing conditions for B01, 104B and 206A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B09 includes basement, first and second level TR work.
B09-R2 | B01 | Basement TR includes existing equipment and could remain active during cutover | Critical | Medium | 8 | Document active services, protect-in-place and define cutover/demo sequence | Telecom / OIT | Closed | B01 shows existing security/network/telecom equipment and panel work.
B09-R3 | All | Hazardous material abatement plans exist for basement, first and second levels | High | Medium | 6 | Coordinate ACM/lead/abatement review before penetrations, flooring removal or ceiling/wall work | GC / IH / COR | Closed | B09 drawing index includes 09H-100, 09H-101 and 09H-102.
B09-R4 | 104B/206A | Rated wall/door work and fire/smoke assemblies could affect schedule and acceptance | High | Medium | 6 | Verify wall ratings, door/frame rating, penetrations, smoke/fire barriers and access control hardware | GC / VA | Closed | Fire protection/architectural enlarged plans show rated wall legends and TR layouts.
B09-R5 | All | Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified | Critical | Medium | 8 | Confirm IU/CU assignments, emergency source, BACnet/interface, condensate routing and alarms | Mechanical / Electrical | Closed | IU-0/1/2 and CU-0/1/2 appear in electrical/enlarged data.
B09-R6 | All | Electrical panel/circuit source and rack load coordination unresolved | High | Medium | 6 | Verify B09-TRB01A/B, B09-TR104BA/B, B09-TR206AA/B schedules, SPDs, labels and load measurements | Electrical / GCC | Closed | B09 has multiple TR panels across all three levels.
B09-R7 | All | Fire alarm/sprinkler impairments and firestopping could affect occupied operations | Critical | Medium | 8 | Track impairments, temporary firestopping, fire watch, sprinkler/head changes and FA acceptance testing | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide.
B09-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, test records, labels, OIT acceptance and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B09-Q1 | Confirm final TR scope: B01 basement, 104B first level, and 206A second level? | VA / OIT / Designer | Closed |  |  | Room inventory may miss scope
B09-Q2 | What active services are currently fed from B01 existing equipment/security/network devices? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B09-Q3 | What hazardous/abatement steps apply to B01, 104B and 206A work areas? | GC / IH / COR | Closed |  |  | Work delay or exposure risk
B09-Q4 | Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B09-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed |  |  | Life safety acceptance risk
B09-Q6 | Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B09-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B09-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B09-P001 | B01 | Existing Condition | Basement TR B01 existing telecom/security/network equipment, storage conditions, panels, ceiling, walls and pathways |  | Paul |  | B09-R1/B09-R2 | Closed
B09-P002 | 104B | Existing Condition | First-level TR 104B, walls/door/ceiling/floor, security devices, IU-1-01 location and pathways |  | Paul |  | B09-R1/B09-R4 | Closed
B09-P003 | 206A | Existing Condition | Second-level TR 206A, walls/door/ceiling/floor, adjacent Nursing Service 206, IU-2-01 location and pathways |  | Paul |  | B09-R1/B09-R4 | Closed
B09-P004 | All | Hazardous Materials | Flooring, ceilings, pipe insulation, penetrations and abatement-related locations before disturbance |  | Paul |  | B09-R3 | Closed
B09-P005 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B09-R7 | Closed
B09-P006 | All | HVAC | IU/CU equipment, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B09-R5 | Closed
B09-P007 | All | Electrical | B09 TR panels, breakers, SPD, rack receptacles, access controllers, lighting and labels |  | Paul |  | B09-R6 | Closed
B09-P008 | All | Telecom/Security | Racks, fiber, Cat6A, LIU, patch panels, labeling/testing, cameras, access control and VMS/PACS integration |  | Paul |  | B09-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B01 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Basement TR with existing equipment and multiple panel/cooling dependencies.
104B | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | First-level TR with security/access control, cooling and rated wall/door coordination.
206A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Second-level TR adjacent to Nursing Service with cooling, electrical and fire/life-safety coordination.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B09.20260316.pdf
Drawing Index | 65-sheet Building 09 IFC package includes general, hazardous material abatement for basement/first/second levels, architectural, interiors, fire protection, mechanical, electrical, telecommunications, schedules, risers, rack elevations and reference photos.
Telecom Basis | Fiber riser and telecom enlarged content identify Building 09 served by TRs B01, 104B and 206A; each requires redundant fiber paths, Cat6A replacement, rack/patch panel/LIU work, labeling, testing and VA acceptance.
Electrical Basis | Electrical enlarged plans and schedules identify B09-TRB01A/B, B09-TR104BA/B and B09-TR206AA/B, including TR receptacles, rack receptacles, access controllers, lighting, CU circuits and SPD notes.
Mechanical Basis | Electrical/mechanical coordination references IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 serving the basement, first and second-level telecom spaces; verify exact capacity and controls against mechanical schedules.
Fire / Architectural Basis | Fire protection enlarged plan identifies Telecom Rooms B01, 104B and 206A with rated wall legend; general notes require fire alarm modifications, sprinkler modifications, FEC within 75 ft, rated penetration firestopping and temporary firestopping where needed.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B100: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B109: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B121: Compare installed materials against approved submittals/spec sections.
Note on B130: Planned vs actual production supports delay/time-extension rebuttal.
Note on B138: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B10_Assessment (hidden)
BUILDING 10 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 10 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 14:50 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 10 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 200A / Attic Telecom Room Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify attic Telecom Room 200A, basement normal/emergency electrical source rooms B24/B25, existing wall-mounted rack/equipment, panel sources B10-TR200AA/AB, IU/CU-1-01 cooling, FEC/fire alarm/sprinkler impacts, hazardous/abatement scope, and telecom cutover plan.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
10 | 200A | Attic | Existing attic telecom/equipment area | Telecom Room | 2 | 1 | Verify | 10A-401 / 10E-401 / 10T-604 / 10M-701 | Primary Building 10 TR. Drawings identify attic-level Room 200A with existing wall-mounted rack/equipment, new telecom rack equipment, panels B10-TR200AA/AB, IU-1-01, CU-1-01, rack receptacles and future rack space.
10 | B24 | Basement | Existing electrical room - normal power | Electrical source / coordination room | 0 | 0 | Verify | 10E-401 / 10E-701 | Basement existing electrical room normal power referenced on electrical enlarged plan; coordinate B10-MDP/B10-L10-E feeders and load measurement.
10 | B25 | Basement | Existing electrical room - emergency power | Emergency electrical source / coordination room | 0 | 0 | Verify | 10E-401 / 10E-601 / 10E-701 | Basement existing electrical room emergency power referenced on electrical enlarged plan; coordinate ATS-B10-LSD, emergency source and TR equipment continuity.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
200A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Attic TR; verify room enclosure, open-to-deck/rated wall requirements, existing rack/equipment, attic access, structural/pathway clearance, future rack clearance and housekeeping.
B24 | N/A | N/A | N/A | Verify | N/A | Verify | Verify | Verify | Electrical source room; verify panel access, breaker/feeder routes, lockout/tagout needs and working clearances.
B25 | N/A | N/A | N/A | Verify | N/A | Verify | Verify | Verify | Emergency electrical source room; verify ATS/emergency panel access, shutdown constraints and power continuity.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
200A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping.
B24 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place.
B25 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
200A | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm.
B24 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work.
B25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
200A | Verify | 5 kW / rack equipment | Verify | Verify | B10-TR200AA / B10-TR200AB | Verify | Verify | Verify | Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels.
B24 | N/A | N/A | N/A | N/A | B10-MDP / B10-L10-E | Verify | Verify | Verify | Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing.
B25 | N/A | N/A | N/A | N/A | ATS-B10-LSD / emergency distribution | Verify | Verify | Verify | Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
200A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover.
B24 | N/A | N/A | N/A | Verify | N/A | N/A | N/A | Verify | Coordinate telecom power pathways through/source from basement electrical room if applicable.
B25 | N/A | N/A | N/A | Verify | N/A | N/A | N/A | Verify | Coordinate emergency source/backup power pathways for telecom equipment and cooling.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
200A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | General scope requires PACS/CCTV for TR doors; verify door hardware, access controller, camera/VMS integration and any existing attic access/security constraints.
B24 | N/A | N/A | N/A | N/A | Verify | N/A | Verify | Verify | Verify security impact only if electrical source room access or devices are modified.
B25 | N/A | N/A | N/A | N/A | Verify | N/A | Verify | Verify | Verify emergency electrical room security impact if work requires access control changes.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B10-R1 | 200A | Attic Telecom Room existing conditions and access not field verified | High | Medium | 6 | Survey Room 200A, attic access route, existing rack/equipment, floor/deck conditions, clearances and utilities | GCC / Contractor | Closed | Attic work may have access and staging constraints.
B10-R2 | 200A | Hazardous material abatement plan exists for attic level | High | Medium | 6 | Coordinate attic abatement/IH review before penetrations, ceiling/floor work, cabling or HVAC/electrical installation | GC / IH / COR | Closed | Drawing index includes 10H-102 hazardous material abatement plan - attic.
B10-R3 | 200A | Existing wall-mounted rack/equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place and develop night-shift cutover/temporary rack plan | Telecom / OIT | Closed | Telecom drawings reference existing wall-mounted rack/equipment to be replaced/transferred.
B10-R4 | 200A | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 capacity, power source, condensate routing, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B10-R5 | B24/B25 | Panel source, generator/ATS path and shutdown sequencing unclear | Critical | Medium | 8 | Verify B10-MDP, B10-L10-E, ATS-B10-LSD, panel feeders, load measurement and LOTO before electrical work | Electrical / GCC | Closed | Basement normal/emergency electrical rooms are source coordination points.
B10-R6 | 200A | Fire alarm/sprinkler/firestopping work in attic TR could affect occupied operations | Critical | Medium | 8 | Track impairments, fire watch, sprinkler/head changes, FA device work, rated penetrations and temporary firestopping | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide.
B10-R7 | 200A | Telecom/fiber cutover could affect active hospital communications | Critical | Medium | 8 | Require cutover plan, testing, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | All telecom cabling must be tested, approved and accepted before connecting to active operations.
B10-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, test reports, power verification, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B10-Q1 | Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B10-Q2 | What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? | OIT / Contractor | Closed |  |  | Potential communications outage
B10-Q3 | What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? | GC / IH / COR | Closed |  |  | Work delay/exposure risk
B10-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B10-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? | GC / COR | Closed |  |  | Life-safety acceptance risk
B10-Q6 | Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B10-Q7 | Are all attic wall/floor/ceiling penetrations, sleeves and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B10-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B10-P001 | 200A | Existing Condition | Attic TR 200A existing rack/equipment, floor/deck, walls, access route, pathways and clearances |  | Paul |  | B10-R1/B10-R3 | Closed
B10-P002 | 200A | Hazardous Materials | Attic abatement-related materials, flooring/penetrations, ceiling/deck and disturbance areas |  | Paul |  | B10-R2 | Closed
B10-P003 | B24 | Electrical | Existing normal electrical room panels, B10-MDP/B10-L10-E, feeder route and working clearances |  | Paul |  | B10-R5 | Closed
B10-P004 | B25 | Electrical | Existing emergency electrical room, ATS-B10-LSD/emergency distribution and access constraints |  | Paul |  | B10-R5 | Closed
B10-P005 | 200A | Firestop | All attic wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B10-R6 | Closed
B10-P006 | 200A | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B10-R4 | Closed
B10-P007 | 200A | Telecom | Racks, UPS/PDU, fiber, Cat6A, patch panels, LIU, bonding, labels and test records |  | Paul |  | B10-R7 | Closed
B10-P008 | 200A | Security | Card reader, electric strike, door position, CCTV/PACS, motion sensor and VMS/PACS integration |  | Paul |  | B10-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
200A | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Attic TR with rack/equipment, cooling, electrical, fire/life-safety and abatement coordination.
B24 | 0.5 | 0.5 | N/A | 0.5 | N/A | Verify | 0.5 | Partial / Yellow | Normal electrical source coordination only.
B25 | 0.5 | 0.5 | N/A | 0.5 | N/A | Verify | 0.5 | Partial / Yellow | Emergency electrical source coordination only.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B10.20260316.pdf
Drawing Index | 51-sheet Building 10 IFC package includes general, attic hazardous material abatement, architectural, interiors, fire protection, mechanical, electrical, telecommunications, schedules, rack elevations and reference photos.
Architectural / Hazardous Basis | Drawing index identifies 10H-102 hazardous material abatement plan - attic and 10A-401 architectural enlarged views - second level/attic TR scope; field verify abatement and architectural/rated assembly work before construction.
Telecom Basis | 10T-101/10T-604 identify attic-level telecom work and rack elevations for Room 200A, including existing wall-mounted rack/equipment, new racks, future rack space, UPS, PDUs, switches, Cat6A patch panels, Fiber LIU, grounding/bonding and labeling/testing requirements.
Mechanical Basis | 10M sheets identify dedicated split-system cooling for Telecom Room 200A with IU-1-01 and CU-1-01, BACnet adapter and controls; verify emergency power, condensate and alarms in field.
Electrical Basis | 10E-401/701 identify B10-TR200AA and B10-TR200AB panels in Telecom Room 200A, rack/TR receptacles, CU-1-01, B10-MDP/B10-L10-E and ATS-B10-LSD source coordination with load measurement and SPD requirements.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B100: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B109: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B121: Compare installed materials against approved submittals/spec sections.
Note on B130: Planned vs actual production supports delay/time-extension rebuttal.
Note on B138: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B12_Assessment (hidden)
BUILDING 12 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 12 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 60% | Construction Ready | No
Review Date | 2026-06-25 15:01 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 12 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | Fiber-only / Pull-through fiber assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover.
HVAC Status | N/A | Electrical Status | N/A / Verify | Telecom Status | Verify | Fire Protection Status | N/A / Verify | Fire Alarm Status | N/A / Verify
Security Status | N/A / Verify | Next Action | Field verify existing fiber pathway through Building 12, existing rack/demarc/serving closet condition, floor/wall penetrations, routing from basement/first/second level telecom plans, phasing/cutover approach, and test/label/as-built deliverables.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
12 | 00 / existing fiber path | B/1/2 | Existing building fiber pathway / pull-through route | Fiber-only pull-through scope | 0 | 0 | Verify | 12G-000 / 12T-100 / 12T-101 / 12T-604 | Cover sheet states Building 12 receives fiber only. Rack elevation sheet identifies Building 12 as existing rack elevation/fiber only with no rack mounting and no new TR buildout.
12 | Existing rack/demarc - field verify | Field verify | Existing service point / serving closet | Protect-in-place / fiber transition point | 0 | 0 | Verify | 12T-604 / 12T-601 / 12T-602 / 12T-603A/B | 12T-604 identifies building level B/1/2 and mounting type NONE/FIBER ONLY. Field verification required to document where fiber enters, passes through, and terminates.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
Fiber path B/1/2 | N/A / Verify | N/A / Verify | N/A | Verify | N/A | Verify | Verify | Verify | No new TR room indicated; focus is route readiness, penetrations, cable tray/conduit capacity, and access to existing pathway.
Existing rack/demarc - field verify | N/A / Verify | N/A / Verify | N/A | Verify | N/A / Verify | Verify | Verify | Verify | Confirm existing equipment, demarc, or closet location; protect active services and confirm no new rack required.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
Fiber path B/1/2 | N/A | N/A | N/A / Verify | N/A / Verify | N/A | Verify | Verify | Verify | No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route.
Existing rack/demarc - field verify | N/A | N/A | N/A / Verify | N/A / Verify | N/A | Verify | Verify | Verify | No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
Fiber path B/1/2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment.
Existing rack/demarc - field verify | Existing / N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Field verify existing environmental conditions only if existing service point/equipment is accessed.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
Fiber path B/1/2 | N/A | N/A | N/A | N/A | N/A | N/A | Labeling Verify | Verify | No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown.
Existing rack/demarc - field verify | Existing / N/A | N/A | N/A | N/A | N/A | N/A | Labeling Verify | Verify | Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
Fiber path B/1/2 | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing.
Existing rack/demarc - field verify | Existing / none new | N/A / Verify | Verify | Verify | Verify | Verify | Verify | Verify | 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
Fiber path B/1/2 | N/A | N/A | N/A | N/A | N/A / Verify | N/A | N/A | N/A / Verify | No new TR door or PACS/CCTV package shown for Building 12; verify security access only for work areas and existing equipment rooms.
Existing rack/demarc - field verify | N/A / Verify | N/A / Verify | N/A | N/A | N/A / Verify | N/A | N/A | N/A / Verify | Confirm access requirements to existing closet/demarc while protecting active operations.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B12-R1 | All | Fiber-only scope could be mistaken for full TR scope or skipped as minor work | High | Medium | 6 | Clearly tag Building 12 as fiber-only and verify required fiber path, testing, labels and acceptance deliverables | GCC / OIT / GC | Closed | Cover sheet note says this building is to receive fiber only.
B12-R2 | Fiber path B/1/2 | Existing pull-through pathway not field verified | High | Medium | 6 | Trace basement/first/second level pathway, conduit/cable tray capacity, pull points and access before scheduled pull | Telecom Contractor | Closed | 12T-100/101 plan sheets and 12T-604 identify fiber-only B/1/2 scope.
B12-R3 | All | Existing service continuity during fiber pull/cutover may not be defined | Critical | Medium | 8 | Coordinate with VA OIT, submit phasing/cutover plan, and maintain legacy service until new fiber is tested and accepted | OIT / Telecom | Closed | All telecom cabling must be tested, approved and accepted before active connection.
B12-R4 | All | Pathway penetrations/firestopping may be overlooked because there is no architectural/FP package | High | Medium | 6 | Inspect all new/reused penetrations and require permanent or temporary firestopping at end of shift | GC / Firestop | Closed | General notes still require firestopping for floor/rated wall penetrations.
B12-R5 | Existing rack/demarc - field verify | Existing termination/demarc location and ownership unclear | Medium | Medium | 4 | Field document existing rack/demarc/serving closet and confirm where new fiber terminates or passes through | GCC / OIT | Closed | 12T-604 shows room/rack as 00; actual field condition must be documented.
B12-R6 | All | Test reports, labels and as-builts may be incomplete for fiber-only work | High | Medium | 6 | Track fiber OTDR/certification, labeling, route documentation and VA/OIT acceptance before closeout | Telecom / GCC | Closed | Fiber-only work still requires record drawings and acceptance.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B12-Q1 | Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? | VA / OIT / Designer | Closed |  |  | Scope misunderstanding
B12-Q2 | What exact pathway does the Building 12 fiber take through basement, first and second levels? | Telecom Contractor / OIT | Closed |  |  | Fiber pull and access risk
B12-Q3 | Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? | OIT / Contractor | Closed |  |  | Termination and ownership unclear
B12-Q4 | Are existing conduits/cable trays available and below fill limits for the new fiber? | Telecom Contractor | Closed |  |  | Pathway capacity risk
B12-Q5 | Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? | GC / Firestop | Closed |  |  | Life safety/firestop risk
B12-Q6 | What is the approved cutover/testing/acceptance sequence for Building 12 fiber? | OIT / COR / Contractor | Closed |  |  | Possible outage or acceptance delay
B12-Q7 | Which fiber test reports, labels, route documentation and as-builts are required for closeout? | Telecom / GCC | Closed |  |  | Closeout documentation gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B12-P001 | Fiber path B/1/2 | Existing Condition | Existing conduit/cable tray/pathway from entry through basement/first/second levels |  | Paul |  | B12-R2 | Closed
B12-P002 | Existing rack/demarc - field verify | Existing Condition | Existing rack, demarc, serving closet or fiber termination/pass-through point |  | Paul |  | B12-R5 | Closed
B12-P003 | All | Firestop | All floor/wall/sleeve penetrations before pull, during work, and after permanent firestop |  | Paul |  | B12-R4 | Closed
B12-P004 | All | Telecom | Fiber reels, pull route, pull boxes, labels, slack loops, termination points and test records |  | Paul |  | B12-R3/B12-R6 | Closed
B12-P005 | All | Closeout | Fiber certification/OTDR screenshots, labeling, as-built route and VA/OIT acceptance evidence |  | Paul |  | B12-R6 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
Fiber path B/1/2 | 0.6 | 0.5 | N/A | N/A | 0.6 | Verify | 0.55 | Partial / Yellow | Fiber-only pathway and cutover must be field verified.
Existing rack/demarc - field verify | 0.5 | 0.5 | N/A | N/A | 0.6 | Verify | 0.53 | Partial / Yellow | Existing service point/termination requires field confirmation.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B12.20260316.pdf
Drawing Index | 20-sheet Building 12 IFC package includes general notes and telecommunications only: plans for basement/first and second levels, details, riser diagrams, existing/new fiber riser diagrams, rack elevations and telecom cutsheets.
Scope Basis | Cover sheet general note 4 states: This building is to receive fiber only. There are no architectural enlarged views, mechanical, electrical, fire protection or hazardous packages listed for B12 beyond general notes and telecom sheets.
Rack / Room Basis | 12T-604 indicates Building 12, rack 00, room 00, building level B/1/2, existing rack elevation/fiber only, and mounting type NONE/FIBER ONLY. It also states this building is pull-through fiber only.
Telecom Basis | 12T-100 and 12T-101 cover telecom plans for basement/first and second levels; 12T-601/602/603A/603B cover riser and fiber riser diagrams. Verify route and termination in field.
Operational Basis | General notes still require conduit reuse where possible, 10% allowance where applicable, coordination with VA COR/A/E for deviations, testing/labeling, owner acceptance, commissioning/closeout as applicable, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B86: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B95: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B107: Compare installed materials against approved submittals/spec sections.
Note on B116: Planned vs actual production supports delay/time-extension rebuttal.
Note on B124: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B13_Assessment (hidden)
BUILDING 13 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 13 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 15:08 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 13 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 124, existing 222 / Telecom Room Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify Room 124 and existing Tel Room 222; confirm active services, rack/equipment transfer, B13-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
13 | 124 | First | Telecom Room / new TR build area | Telecom Room | 2 | 1 | Verify | 13A-401 / 13E-401 / 13T-100 / 13T-701 | Primary Building 13 TR. Plans identify Telecom Room 124 at 119 SF, served by Rack ID TR01-124-1, panels B13-TR124AA/AB, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, and a future rack allowance.
13 | 222 | Second | Existing Tel Room / existing rack and patching area | Existing telecom transition point | 1 | 0 | Verify | 13T-100 / 13R-900 | Existing second-level Tel Room 222 shown with existing telco patch, plywood backboard, indoor AC unit, wall-mounted rack, patch panel, and security cabinet. Protect active services and verify what is transferred to Room 124.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack clearances, wall backing, and pathway entry points.
222 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing second-floor tel room; verify existing equipment status, pathway, AC unit, backboard, and transition/abandonment scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls.
222 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
124 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm.
222 | Existing indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
124 | Verify | 5 kW / 240V rack UPS | Verify | Verify | B13-TR124AA / B13-TR124AB | Verify | Verify | Verify | Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements.
222 | Existing | Existing | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B.
222 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged plan shows security/access-control device callouts at Room 124 and 124-CAM-01 camera designation; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination.
222 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B13-R1 | All | Existing conditions for Room 124 and existing Tel Room 222 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B13 includes new TR plus existing second-level tel transition point.
B13-R2 | 124 | First-level hazardous material abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | Drawing index includes 13H-101 hazardous material abatement plan - first level.
B13-R3 | 222 | Existing Tel Room 222 equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing rack/backboard/security/patch equipment shown.
B13-R4 | 124 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B13-R5 | 124 | 240V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B13-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs | Electrical / GCC | Closed | Panel and circuit references are concentrated at Room 124.
B13-R6 | 124 | Rated wall/door/firestop scope may affect life-safety acceptance | High | Medium | 6 | Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | GC / FP / FA | Closed | New TRs must be 1-hour fire/smoke rated.
B13-R7 | All | Telecom/fiber cutover could affect active hospital communications across first and second levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | 13T-701 shows Room 124 serving large port count and Level 2 outlets.
B13-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B13-Q1 | Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B13-Q2 | What active services are currently fed from existing Tel Room 222 equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B13-Q3 | What hazardous/abatement steps apply to first-level Room 124 work? | GC / IH / COR | Closed |  |  | Work delay or exposure risk
B13-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B13-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? | GC / COR | Closed |  |  | Life-safety acceptance risk
B13-Q6 | Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B13-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B13-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B13-P001 | 124 | Existing Condition | Room 124 walls, ceiling/deck, floor, door, adjacent Telehealth 124A/109, rack location, pathways and penetrations |  | Paul |  | B13-R1/B13-R6 | Closed
B13-P002 | 222 | Existing Condition | Existing Tel Room 222 wall rack, telco patch, plywood backboard, AC unit, patch panel and security cabinet |  | Paul |  | B13-R1/B13-R3 | Closed
B13-P003 | 124 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas |  | Paul |  | B13-R2 | Closed
B13-P004 | 124 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B13-R6 | Closed
B13-P005 | 124 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B13-R4 | Closed
B13-P006 | 124 | Electrical | B13-TR124AA/AB panels, rack receptacles, breakers, SPD, access controller, lighting and labels |  | Paul |  | B13-R5 | Closed
B13-P007 | 124/222 | Telecom | New racks, fiber path A/B, Cat6A, patch panels, LIU, labels/test records and existing Room 222 transfer work |  | Paul |  | B13-R7 | Closed
B13-P008 | 124/222 | Security | 124-CAM-01, card reader, electric strike, door position, motion sensor, existing security cabinet and VMS/PACS integration |  | Paul |  | B13-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
124 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with two racks, future rack, 240V UPS, cooling, access control and fire/life-safety coordination.
222 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing second-level tel room and transition point; protect active services until cutover complete.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B13.20260316.pdf
Drawing Index | 46-sheet Building 13 IFC package includes general, first-level hazardous material abatement, architectural, interiors, fire protection, mechanical, electrical, telecommunications, schedules/rack elevations, and photo references.
Architectural / Hazardous Basis | 13H-101 identifies first-level hazardous material abatement plan. 13A-401 identifies first-level architectural enlarged views for Telecom Room 124 and associated room/rated construction coordination.
Telecom Basis | 13T-100 identifies Telecom Room 124 at 119 SF and existing second-level Tel Room 222; 13T-701 identifies Rack ID TR01-124-1, 58 WAO total, 65 active ports per survey, 91 ports per schedule, and 100 total ports with 10% allowance.
Mechanical Basis | 13M-101/701 identify dedicated split-system cooling for Telecom Room 124 using IU-1-01 and CU-1-01 with BACnet adapter/control coordination; verify emergency power, condensate and alarms in field.
Electrical Basis | 13E-401/701 identify B13-TR124AA and B13-TR124AB panel/circuit references, 240V rack UPS requirements, normal/emergency rack power, CU-1-01, access/security devices, lighting, SPD and load measurement requirements.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B93: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B102: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B114: Compare installed materials against approved submittals/spec sections.
Note on B123: Planned vs actual production supports delay/time-extension rebuttal.
Note on B131: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B14_Assessment (hidden)
BUILDING 14 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 14 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 15:18 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 14 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 119, existing B.01/B2 / Telecom Room Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 14 includes new first-level Telecom Room 119 and existing basement telecom rooms B.01/B2; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify Room 119 and existing basement Tel/F Panel B.01/B2; confirm active services, rack/equipment transfer, B14-TR119A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
14 | 119 | First | Telecom Room / new TR build area | Telecom Room | 1 | 1 | Verify | 14A-401 / 14E-100 / 14T-100 / 14T-604 / 14T-701 | Primary Building 14 TR. Plans identify Telecom Room 119 at 124 SF, served by Rack ID TR01-119-1, panels B14-TR119A/B, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, 56 feet of first-level cable tray, and a future rack allowance.
14 | B.01 | Basement | Existing Tel/F Panel room / telecom equipment area | Existing telecom transition point | 1 | 0 | Verify | 14T-100 / 14T-604 / 14R-900 | Existing basement Tel/F Panel B.01 shown at 165 SF with existing wall-mounted TE, patch panels, telco patch, plywood backboards, and legacy fiber/equipment. Protect active services and verify what transfers to Room 119.
14 | B2 | Basement | Existing telecom room reference | Existing telecom transition point | 1 | 0 | Verify | 14R-900 | Photo reference sheet identifies basement existing telecom room B2. Field verify whether B2 is same/related to B.01 or separate legacy telecom space.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
119 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack/future rack clearances, wall backing, and pathway entry points.
B.01 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room; verify active equipment status, pathway, backboards, wall-mounted TE, and transition/abandonment scope.
B2 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room photo reference; verify whether active services/equipment remain and confirm relationship to B.01.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
119 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls.
B.01 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover.
B2 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room; verify no unsealed penetrations remain after cable transfer or reuse.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
119 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 119 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm.
B.01 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Tel/F Panel room; verify existing environmental conditions during cutover and whether legacy equipment remains active.
B2 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom room reference; field verify cooling/ventilation and active equipment condition.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
119 | Verify | 5 kW / 240V rack UPS | Verify | Verify | B14-TR119A / B14-TR119B | Verify | Verify | Verify | Electrical plan/schedules identify B14-TR119A/B, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and panel load measurement requirements.
B.01 | Existing | Existing | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing basement wall-mounted TE/equipment area; verify power source, active equipment, UPS/PDU status, and transition requirements before disconnect or removal.
B2 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing telecom room photo reference; confirm power sources and any cutover requirements.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
119 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 14T-701 identifies Room 119 schedule: 44 WAO total, 29 active ports per survey, 76 total ports per schedule, and 84 total ports with 10% allowance. New Rack ID TR01-119-1 serves first and second level outlets with Fiber Path A/B.
B.01 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room B.01 equipment includes wall-mounted TE, Cisco switch/legacy patch panel, telco patch, plywood backboards, and legacy Fiber LIU; verify active services and transfer plan to Room 119.
B2 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room B2 is identified by photo reference; verify active devices, routing, and relation to B.01.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
119 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 119-CAM-01 and security/access-control scope for Room 119; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination.
B.01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify whether existing security equipment remains, is relocated, or requires temporary protection during cutover.
B2 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify security/access conditions and whether any legacy security equipment is present.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B14-R1 | All | Existing conditions for Room 119 and existing basement telecom rooms B.01/B2 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B14 includes new TR plus existing basement telecom transition points.
B14-R2 | 119 | First-level hazardous material abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | Drawing index includes 14H-101 hazardous material abatement plan - first level; page 6 notes lead-based paint abatement in room/restroom context.
B14-R3 | B.01/B2 | Existing basement telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing wall-mounted TE, patch panels, telco patch and legacy Fiber LIU shown.
B14-R4 | 119 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B14-R5 | 119 | 240V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B14-TR119A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs | Electrical / GCC | Closed | Panel and circuit references are concentrated at Room 119.
B14-R6 | 119 | Rated wall/door/firestop scope may affect life-safety acceptance | High | Medium | 6 | Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | GC / FP / FA | Closed | New TRs must be 1-hour fire/smoke rated.
B14-R7 | All | Telecom/fiber cutover could affect active hospital communications across basement, first and second levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | 14T-701 shows Room 119 serving Level 1 and Level 2 outlets with 84 total ports including allowance.
B14-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B14-Q1 | Confirm final telecom scope: new Room 119 and existing basement B.01/B2 transition only? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B14-Q2 | What active services are currently fed from existing B.01/B2 equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B14-Q3 | What hazardous/abatement steps apply to first-level Room 119 work? | GC / IH / COR | Closed |  |  | Work delay or exposure risk
B14-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 119? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B14-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 119? | GC / COR | Closed |  |  | Life-safety acceptance risk
B14-Q6 | Are B14-TR119A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B14-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B14-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B14-P001 | 119 | Existing Condition | Room 119 walls, ceiling/deck, floor, door, adjacent conference/restroom/office spaces, rack location, pathways and penetrations |  | Paul |  | B14-R1/B14-R6 | Closed
B14-P002 | B.01 | Existing Condition | Existing basement Tel/F Panel B.01, wall-mounted TE, patch panels, telco patch, plywood backboards, legacy Fiber LIU and pathways |  | Paul |  | B14-R1/B14-R3 | Closed
B14-P003 | B2 | Existing Condition | Existing basement telecom room B2 photo reference, equipment, pathways, power and protection-in-place needs |  | Paul |  | B14-R1/B14-R3 | Closed
B14-P004 | 119 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas |  | Paul |  | B14-R2 | Closed
B14-P005 | 119 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B14-R6 | Closed
B14-P006 | 119 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B14-R4 | Closed
B14-P007 | 119 | Electrical | B14-TR119A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels |  | Paul |  | B14-R5 | Closed
B14-P008 | 119/B.01 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 119-CAM-01 and existing B.01/B2 transfer work |  | Paul |  | B14-R7/B14-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
119 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 240V UPS, cooling, access control, cable tray and fire/life-safety coordination.
B.01 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement tel/fiber panel room and transition point; protect active services until cutover complete.
B2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom room reference; field verify scope and active status.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B14.20260316.pdf
Drawing Index | 46-sheet Building 14 IFC package includes general, first-level hazardous material abatement, architectural, interiors, fire protection, mechanical, electrical, telecommunications, rack elevations, telecom schedules, and photo references.
Architectural / Hazardous Basis | 14H-101 identifies first-level hazardous material abatement plan. 14A-401 identifies first-level architectural enlarged views for Telecom Room 119 and associated rated construction coordination.
Telecom Basis | 14T-100 identifies Telecom Room 119 at 124 SF and existing basement Tel/F Panel B.01 at 165 SF; 14T-604 identifies B.01 existing wall/wall-mount TE and Room 119 new rack plus future rack; 14T-701 identifies 44 WAO total, 29 active ports, 76 ports per schedule and 84 ports with 10% allowance.
Mechanical Basis | 14M-101/701 identify dedicated split-system cooling for Telecom Room 119 using IU-1-01 and CU-1-01 with BACnet adapter/control coordination; verify emergency power, condensate and alarms in field.
Electrical Basis | 14E-100/601/701 identify B14-TR119A and B14-TR119B panel/circuit references, 240V rack UPS requirements, normal/emergency rack power, CU-1-01, lighting, SPD and load measurement requirements.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B101: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B110: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B122: Compare installed materials against approved submittals/spec sections.
Note on B131: Planned vs actual production supports delay/time-extension rebuttal.
Note on B139: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B15_Assessment (hidden)
BUILDING 15 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 15 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 15:27 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 15 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 124A / existing 222 and B01 / Telecom Room Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 15 includes new first-level Telecom Room 124A and existing telecom transition points at second-level Tel Room 222 and basement B01; field verification, active service cutover, 240V UPS/PDU power, dedicated heat-pump cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify Room 124A, existing Tel Room 222 and basement B01; confirm active services, rack/equipment transfer, B15-TR124AA/AB panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, first-level hazardous/abatement impacts, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
15 | 124A | First | Office/room converted to Telecom Room | Telecom Room | 1 | 1 | Verify | 15A-401 / 15E-401 / 15T-100 / 15T-604 / 15T-701 | Primary Building 15 TR. Plans identify Telecom Room 124A at 121 SF, served by Rack ID TR15-109A-01, panels B15-TR124AA/AB, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, and a future rack allowance.
15 | 222 | Second | Existing Tel Room / wall-mounted rack and support equipment | Existing telecom transition point | 1 | 0 | Verify | 15T-100 / 15T-604 / 15R-900 | Existing second-level Tel Room 222 shown at 65 SF with existing/remain indoor AC unit, security cabinet, ground bar, plywood backboard, wall-mounted rack, existing Cisco switches, legacy patch panels, and floor UPS; protect active services and verify transfer to Room 124A.
15 | B01 | Basement | Existing telecom/crossover area | Existing telecom transition point | 1 | 0 | Verify | 15T-604 / 15R-900 | Rack elevations identify existing B-01 crossover wall/wall-mount TE with legacy 24-port patch panel. Photo reference identifies basement existing telecom room B01.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
124A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack/future rack clearances, wall backing, and pathway entry points.
222 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing second-level tel room; verify active equipment status, pathway, indoor AC unit, ground bar, backboard, wall rack, UPS, and transition/abandonment scope.
B01 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom/crossover room; verify active equipment status, pathway, legacy 24-port patch panel, power, and relationship to Room 222/124A transfer.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
124A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls.
222 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover.
B01 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom/crossover room; verify no unsealed penetrations remain after cable transfer or reuse.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
124A | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 124A and CU-1-01 outdoor heat-pump/A/C unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm.
222 | Existing/remain indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Tel Room 222 is shown with existing/remain indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover.
B01 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom/crossover space; verify environmental conditions and whether active equipment remains during cutover.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
124A | Verify | 5 kW / 240V rack UPS | Verify | Verify | B15-TR124AA / B15-TR124AB | Verify | Verify | Verify | Electrical enlarged plans and schedules identify B15-TR124AA/AB, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and 30-day load measurement requirements.
222 | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify power source, active equipment, APC floor UPS status, and transition requirements before disconnect or removal.
B01 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing B-01 crossover; verify power sources and cutover needs for legacy patch panel/crossover.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
124A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 15T-701 identifies Room 109A schedule but field plan/electrical room callouts identify Telecom Room 124A; schedule has 62 WAO total, 76 active ports per survey, 101 total ports per schedule, and 111 total ports with 10% allowance. New Rack ID TR15-109A-01 serves basement, first and second level outlets.
222 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 222 equipment includes wall/wall-mounted TE, Cisco switches, legacy 48-port patch panels, ground bar, plywood backboard, security cabinet, and floor UPS; verify active services and transfer plan to Room 124A.
B01 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B-01 crossover includes legacy 24-port patch panel; verify active devices, routing, and relation to Room 222 and Room 124A.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
124A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 124A-CAM-1 and security/access-control scope for Room 124A; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination.
222 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover.
B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify security/access conditions and whether any legacy security equipment is present.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B15-R1 | All | Existing conditions for Room 124A and existing telecom rooms 222/B01 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B15 includes new TR plus existing second-level and basement telecom transition points.
B15-R2 | 124A | First-level hazardous material abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | Drawing index includes 15H-101 hazardous material abatement plan - first level; page 6 notes lead-based paint abatement through entire room/door frames.
B15-R3 | 222/B01 | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing wall-mounted rack, Cisco switches, patch panels, security cabinet, ground bar and UPS shown.
B15-R4 | 124A | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B15-R5 | 124A | 240V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B15-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs | Electrical / GCC | Closed | Panel and circuit references are concentrated at Room 124A.
B15-R6 | 124A | Rated wall/door/firestop scope may affect life-safety acceptance | High | Medium | 6 | Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | GC / FP / FA | Closed | New TRs must be 1-hour fire/smoke rated.
B15-R7 | All | Telecom/fiber cutover could affect active hospital communications across basement, first and second levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | 15T-701 shows Room 124A/109A serving 111 total ports including allowance.
B15-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B15-Q1 | Confirm final telecom scope: new Room 124A and existing Rooms 222/B01 transition only? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B15-Q2 | Why does 15T-701 reference RM 109A while plans and electrical schedules identify Telecom Room 124A? | VA / Designer / OIT | Closed |  |  | Room naming mismatch could affect PMIS tracking
B15-Q3 | What active services are currently fed from existing Room 222 and B01 equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B15-Q4 | What hazardous/abatement steps apply to first-level Room 124A work? | GC / IH / COR | Closed |  |  | Work delay or exposure risk
B15-Q5 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124A? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B15-Q6 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124A? | GC / COR | Closed |  |  | Life-safety acceptance risk
B15-Q7 | Are B15-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B15-Q8 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B15-P001 | 124A | Existing Condition | Room 124A walls, ceiling/deck, floor, door, adjacent Office 124/Office 109/HAC 123, rack location, pathways and penetrations |  | Paul |  | B15-R1/B15-R6 | Closed
B15-P002 | 222 | Existing Condition | Existing Tel Room 222 wall rack, Cisco switches, legacy patch panels, indoor AC unit, security cabinet, ground bar, plywood backboard and floor UPS |  | Paul |  | B15-R1/B15-R3 | Closed
B15-P003 | B01 | Existing Condition | Existing basement telecom/crossover B01, legacy 24-port patch panel, pathway, power and protection-in-place needs |  | Paul |  | B15-R1/B15-R3 | Closed
B15-P004 | 124A | Hazardous Materials | First-level abatement-related materials, lead-based paint/door frames, flooring, walls, ceiling/penetrations, and disturbance areas |  | Paul |  | B15-R2 | Closed
B15-P005 | 124A | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B15-R6 | Closed
B15-P006 | 124A | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B15-R4 | Closed
B15-P007 | 124A | Electrical | B15-TR124AA/AB panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels |  | Paul |  | B15-R5 | Closed
B15-P008 | 124A/222/B01 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 124A-CAM-1 and existing 222/B01 transfer work |  | Paul |  | B15-R7/B15-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
124A | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 240V UPS, heat-pump cooling, access control, cable tray and fire/life-safety coordination.
222 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing second-level tel room and transition point; protect active services until cutover complete.
B01 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom/crossover room; field verify scope and active status.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B15.20260316(1).pdf
Drawing Index | 47-sheet Building 15 IFC package includes general, first-level hazardous material abatement, architectural, interiors, fire protection, mechanical, electrical, telecommunications, rack elevations, telecom schedules, and photo references.
Architectural / Hazardous Basis | 15H-101 identifies first-level hazardous material abatement plan. 15A-401 identifies first-level architectural enlarged views for Telecom Room 124A and associated rated construction coordination.
Telecom Basis | 15T-100 identifies Telecom Room 124A at 121 SF and existing second-level Tel Room 222 at 65 SF; 15T-604 identifies Room 222 existing rack/equipment, B-01 crossover, and Room 109-A/124A new rack plus future rack; 15T-701 identifies 62 WAO total, 76 active ports, 101 ports per schedule and 111 ports with 10% allowance.
Mechanical Basis | 15M-101/701 identify dedicated split-system heat-pump/A/C cooling for Telecom Room 124A using IU-1-01 and CU-1-01 with BACnet adapter/control coordination; verify emergency power, condensate and alarms in field.
Electrical Basis | 15E-401/701 identify B15-TR124AA and B15-TR124AB panel/circuit references, 240V rack UPS requirements, normal/emergency rack power, CU-1-01, lighting, SPD and load measurement requirements.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B101: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B110: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B122: Compare installed materials against approved submittals/spec sections.
Note on B131: Planned vs actual production supports delay/time-extension rebuttal.
Note on B139: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B16_Assessment (hidden)
BUILDING 16 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 16 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 15:34 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 16 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 015 / existing 014 / Basement TR Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 16 includes new basement Telecom Room 015 and existing basement Telecom Room 014; field verification, active service transfer, 240V UPS/PDU power, dedicated cooling, panel replacement/source coordination, firestopping, PACS/CCTV integration, and cable tray coordination remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify Room 015 and existing Room 014; confirm active services, rack/equipment transfer, B16-TR015A/B panel sources, IU/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, panel replacement/load measurement, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
16 | 015 | Basement | Vacant / new telecom room build area | Telecom Room | 1 | 1 | Verify | 16A-400 / 16E-100 / 16T-100 / 16T-604 / 16T-701 | Primary Building 16 TR. Plans identify Telecom Room 015 at 79 SF, served by Rack ID TR01-015-A-1, panels B16-TR015A/B, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, 96 feet total cable tray, and future rack allowance.
16 | 014 | Basement | Existing telecom room / stair-adjacent legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 16T-100 / 16T-604 / 16R-900 | Existing basement Telecom Room 014 shown with wall-mounted rack, plywood backboard, patch panel, security cabinet, telco patch, existing floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU/wall; protect active services and verify transfer to Room 015.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
015 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack/future rack clearances, wall backing, and pathway entry points.
014 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room; verify active equipment status, pathway, rack/UPS/backboard, security cabinet, and transition/abandonment scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
015 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls.
014 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
015 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 015 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm.
014 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Telecom Room 014; verify existing environmental conditions during cutover and whether legacy equipment remains active.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
015 | Verify | 5 kW / 240V rack UPS | Verify | Verify | B16-TR015A / B16-TR015B | Verify | Verify | Verify | Electrical plans/schedules identify B16-TR015A/B, 240V rack UPS requirements, rack receptacles, TR receptacles, lighting, access controller, CU-1-01, SPD requirements, existing panel demolition/replacement, and 30-day load measurement requirements.
014 | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
015 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 16T-701 identifies Room 015-A schedule: 25 WAO total, 25 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. New Rack ID TR01-015-A-1 serves basement, first, second and attic level outlets.
014 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 014 equipment includes wall/TE rack, floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU; verify active services and transfer plan to Room 015.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
015 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 015-CAM-1 and security/access-control scope for Room 015; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination.
014 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in Room 014; verify whether security equipment remains, is relocated, or requires temporary protection during cutover.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B16-R1 | All | Existing conditions for Room 015 and existing Telecom Room 014 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B16 includes new basement TR plus existing basement telecom transition point.
B16-R2 | 014 | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing wall-mounted rack, Cisco switch, legacy patch panel, security cabinet and UPS shown.
B16-R3 | 015 | Basement TR buildout may conflict with existing utilities, water heater/stair/storage conditions and pathway routing | High | Medium | 6 | Survey adjacent Water Heater 010, Vacant 011/012/013, Stair 014, pathway/ductbank routing, and constructability constraints | GC / GCC | Closed | Room 015 is basement level and adjacent to existing utilities/rooms.
B16-R4 | 015 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B16-R5 | 015 | 240V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B16-TR015A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs | Electrical / GCC | Closed | Panel schedule includes existing panel replacement/demolition and 30-day load measurement requirements.
B16-R6 | 015 | Rated wall/door/firestop scope may affect life-safety acceptance | High | Medium | 6 | Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | GC / FP / FA | Closed | New TRs must be 1-hour fire/smoke rated.
B16-R7 | All | Telecom/fiber cutover could affect active hospital communications across basement, first, second and attic levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | 16T-701 shows Room 015 serving 40 total ports including allowance.
B16-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B16-Q1 | Confirm final telecom scope: new Room 015 and existing Room 014 transition only? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B16-Q2 | What active services are currently fed from existing Room 014 equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B16-Q3 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 015? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B16-Q4 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 015? | GC / COR | Closed |  |  | Life-safety acceptance risk
B16-Q5 | Are B16-TR015A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B16-Q6 | Which existing panel/circuit breaker/feeder demolition and replacement affects Room 015 telecom power? | Electrical / GCC | Closed |  |  | Panel outage/cutover risk
B16-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B16-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B16-P001 | 015 | Existing Condition | Room 015 walls, ceiling/deck, floor, door, adjacent Vacant 011/012/013, Stair 014, Water Heater 010, rack location, pathways and penetrations |  | Paul |  | B16-R1/B16-R3 | Closed
B16-P002 | 014 | Existing Condition | Existing Telecom Room 014 wall rack/TE, Cisco switch, legacy 12-port patch panel, Fiber LIU, floor UPS, plywood backboard and security cabinet |  | Paul |  | B16-R1/B16-R2 | Closed
B16-P003 | 015 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B16-R6 | Closed
B16-P004 | 015 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B16-R4 | Closed
B16-P005 | 015 | Electrical | B16-TR015A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels |  | Paul |  | B16-R5 | Closed
B16-P006 | 015/014 | Telecom | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records and existing Room 014 transfer work |  | Paul |  | B16-R7 | Closed
B16-P007 | 015/014 | Security | 015-CAM-1, card reader, electric strike, door position, motion sensor, existing security cabinet and VMS/PACS integration |  | Paul |  | B16-R8 | Closed
B16-P008 | All | Cable Tray / Pathway | Basement and first-level cable tray/pathway route, supports, fill, firestopping and seismic bracing |  | Paul |  | B16-R3/B16-R7 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
015 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New basement TR with one rack plus future rack, 240V UPS, cooling, access control, cable tray and fire/life-safety coordination.
014 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom room and transition point; protect active services until cutover complete.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B16.20260316.pdf
Drawing Index | 45-sheet Building 16 IFC package includes general, architectural, interiors, fire protection, mechanical, electrical, telecommunications, rack elevations, telecom schedules, and photo references.
Architectural Basis | 16A-400 identifies basement architectural enlarged views for Telecom Room 015, existing telecom room 014, and telecom room open-to-deck/rated construction requirements.
Telecom Basis | 16T-100 identifies Telecom Room 015 at 79 SF and existing basement Room 014; 16T-604 identifies Room 015 new rack plus future rack and Room 014 existing wall/TE rack with UPS, Cisco switch, legacy patch panel and Fiber LIU; 16T-701 identifies 25 WAO total, 25 active ports, 36 ports per schedule and 40 ports with 10% allowance.
Mechanical Basis | 16M-100/701 identify dedicated split-system cooling for Telecom Room 015 using IU-1-01 and CU-1-01 with BACnet adapter/control coordination; verify emergency power, condensate and alarms in field.
Electrical Basis | 16E-100/601/701 identify B16-TR015A and B16-TR015B panel/circuit references, 240V rack UPS requirements, normal/emergency rack power, CU-1-01, lighting, SPD, existing panel replacement/demolition and 30-day load measurement requirements.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B93: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B102: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B114: Compare installed materials against approved submittals/spec sections.
Note on B123: Planned vs actual production supports delay/time-extension rebuttal.
Note on B131: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B17_Assessment (hidden)
BUILDING 17 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 17 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 15:52 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 17_29 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 118 / existing B35A / B29 served from B17
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 17_29 includes new first-level Telecom Room 118 serving Building 17 and Building 29, plus existing basement Telecom Closet B35A; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, cable tray, firestopping, and PACS/CCTV integration remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify Telecom Room 118, existing B35A, and Building 29 service path; confirm active services, B17-TR118A/B panel sources, BUS-B17-EQDP / BUS-B17-NPB1-R sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, hazardous material impacts, and cutover plan.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
17 | 118 | First | New telecom room build area | Telecom Room | 1 | 1 | Verify | 17_29A-401 / 17_29E-401 / 17_29T-100 / 17_29T-604 / 17_29T-701 | Primary Building 17 TR. Plans identify Telecom Room 118 at 157 SF, Rack ID TR17-118-1, panels B17-TR118A/B, 208V rack UPS/PDU equipment, IU-1-01/CU-1-01 cooling, 517 feet total cable tray, and future rack allowance. Rack elevation notes Room 118 serves Building 29.
17 | B35A | Basement | Existing telecom closet / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 17_29T-100 / 17_29T-604 / 17_29R-900 | Existing basement Telecom Closet B35A shown at 12 SF with wall-mounted TE, patch panel, security cabinet, plywood backboard, indoor AC unit, floor UPS, Cisco switches, legacy Ortronics 24/48-port patch panels and SERTEX utility service ports. Protect active services and verify transfer to Room 118.
29 | Building 29 path | First / served from B17 | Building 29 service extension | Served from B17 TR 118 | 0 | 0 | Verify | 17_29T-100 / 17_29T-604 / 17_29T-701 | Building 29 is shown served from B17, with path to B29 via 4-inch PVC and fiber extending from Building 17 to Building 29. Field verify pathway, service boundary, and active outlets included in TR17-118-1 schedule.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
118 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack/future rack clearances, wall backing, and cable tray/pathway entry points.
B35A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom closet; verify active equipment status, pathway, rack/UPS/backboard, indoor AC, security cabinet, and transition/abandonment scope.
B29 Path | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify route from Building 17 to Building 29, 4-inch PVC path, fiber handoff, ownership limits, labeling and final test documentation.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
118 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls.
B35A | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom closet; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover.
B29 Path | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Verify firestopping at pathway penetrations between Building 17 and Building 29 and any rated floor/wall assemblies.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
118 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 118 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm.
B35A | Existing indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing B35A is shown with existing indoor AC unit; verify whether it remains active, is abandoned, or needs temporary protection during cutover.
B29 Path | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No dedicated cooling expected for pathway; verify any equipment cabinets or active service locations in Building 29 if applicable.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
118 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B17-TR118A / B17-TR118B | Verify | Verify | Verify | Electrical plans/schedules identify B17-TR118A fed from BUS-B17-NPB1-R and B17-TR118B fed from BUS-B17-EQDP, with TR RM118 rack receptacles, 208V UPS/PDU equipment, CU-1-01, SPD requirements, and 30-day load measurement requirements.
B35A | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal.
B29 Path | N/A | N/A | N/A | N/A | B17 source / verify | Verify | Verify | Verify | Verify whether any Building 29 equipment or extension path requires power, grounding, bonding, or labeling tied back to B17 TR 118.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
118 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 17_29T-701 identifies Room 118 schedule: 113 WAO total, 67 active ports per survey, 154 total ports per schedule, and 169 total ports with 10% allowance. Rack ID TR17-118-1 serves basement, first, second-level outlets and Building 29 path.
B35A | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room B35A equipment includes SERTEX utility service ports, legacy Ortronics patch panels, Cisco switches, wall-mounted TE, Fiber/legacy equipment, security cabinet, and floor UPS; verify active services and transfer plan to Room 118.
B29 Path | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Building 29 is shown served from B17; verify fiber from Building 17 to Building 29, path to B29 4-inch PVC, outlet labels, test records and as-builts.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
118 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 118-CAM-01 and security/access-control scope for Room 118; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination.
B35A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in B35A; verify whether security equipment remains, is relocated, or requires temporary protection during cutover.
B29 Path | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify Building 29 pathway and any security scope tied into B17 TR 118/VMS/PACS.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B17-R1 | All | Existing conditions for Room 118, B35A and Building 29 service path not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B17_29 includes new TR plus existing basement telecom transition point and B29 service path.
B17-R2 | 118 | First-level hazardous material abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | Drawing index includes 17_29H-101 hazardous material abatement plan - first level.
B17-R3 | B35A | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing SERTEX utility service, Cisco switches, legacy patch panels, security cabinet and UPS shown.
B17-R4 | 118 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B17-R5 | 118 | 208V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B17-TR118A/B schedules, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, SPD, labels, load measurement and LOTO needs | Electrical / GCC | Closed | Panel sources include normal and equipment/emergency-side distribution references.
B17-R6 | 118/B29 Path | Cable tray and pathway scope is large and crosses multiple levels/building service boundary | High | Medium | 6 | Verify 517 ft cable tray, supports, seismic bracing, 40% fill, path to B29 4-inch PVC, penetrations and labeling before install | Telecom / GC | Closed | Cable tray schedule: basement 200 ft, first level 202 ft, second level 115 ft.
B17-R7 | All | Telecom/fiber cutover could affect active hospital communications across B17 and B29 | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | Room 118 serves 169 total ports including allowance and B29 path.
B17-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B17-Q1 | Confirm final telecom scope: new Room 118, existing B35A, and Building 29 served from B17? | VA / OIT / Designer | Closed |  |  | Room inventory or PMIS mapping could miss scope
B17-Q2 | What active services are currently fed from existing B35A equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B17-Q3 | What exact Building 29 outlets/devices are served through TR17-118-1? | VA / OIT / Designer | Closed |  |  | Building 29 scope boundary unclear
B17-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 118? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B17-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 118? | GC / COR | Closed |  |  | Life-safety acceptance risk
B17-Q6 | Are B17-TR118A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B17-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B17-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B17-P001 | 118 | Existing Condition | Room 118 walls, ceiling/deck, floor, door, adjacent Lab/Freezer/Research/Corridor areas, rack location, pathways and penetrations |  | Paul |  | B17-R1/B17-R2 | Closed
B17-P002 | B35A | Existing Condition | Existing Telecom Closet B35A wall TE, SERTEX service ports, legacy patch panels, Cisco switches, security cabinet, plywood backboard, indoor AC and floor UPS |  | Paul |  | B17-R1/B17-R3 | Closed
B17-P003 | B29 Path | Pathway | Path to B29 4-inch PVC, fiber route, penetrations, handoff points and labeling |  | Paul |  | B17-R6/B17-R7 | Closed
B17-P004 | 118 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas |  | Paul |  | B17-R2 | Closed
B17-P005 | 118/B29 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop, including B29 pathway |  | Paul |  | B17-R6 | Closed
B17-P006 | 118 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B17-R4 | Closed
B17-P007 | 118 | Electrical | B17-TR118A/B panels, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels |  | Paul |  | B17-R5 | Closed
B17-P008 | 118/B35A/B29 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 118-CAM-01 and existing B35A transfer work |  | Paul |  | B17-R7/B17-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
118 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TR with one rack plus future rack, 208V UPS, cooling, access control, 517 ft cable tray and B29 service coordination.
B35A | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing basement telecom closet and transition point; protect active services until cutover complete.
B29 Path | 0.5 | 0.5 | N/A | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Building 29 served from B17; verify pathway, fiber, labeling, test records and PMIS mapping.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B17_29.20260316(1).pdf
Drawing Index | 47-sheet Building 17_29 IFC package includes general, first-level hazardous material abatement, architectural, interiors, fire protection, mechanical, electrical, telecommunications, rack elevations, telecom schedules, and photo references.
Architectural / Hazardous Basis | 17_29H-101 identifies first-level hazardous material abatement plan. 17_29A-401 identifies first-level architectural enlarged views for Telecom Room 118 and associated rated/open-to-deck construction coordination.
Telecom Basis | 17_29T-100 identifies Telecom Room 118 at 157 SF, existing basement Telecom Closet B35A at 12 SF, Building 29 served from B17, and path to B29 4-inch PVC. 17_29T-604 identifies Room 118 new rack plus future rack and B35A existing equipment. 17_29T-701 identifies 113 WAO total, 67 active ports, 154 ports per schedule and 169 ports with 10% allowance.
Mechanical Basis | 17_29M-101/701 identify dedicated split-system cooling for Telecom Room 118 using IU-1-01 and CU-1-01 with BACnet adapter/control coordination; verify emergency power, condensate and alarms in field.
Electrical Basis | 17_29E-401/701/702 identify B17-TR118A and B17-TR118B panel/circuit references, 208V rack UPS requirements, normal/equipment power sources including BUS-B17-NPB1-R and BUS-B17-EQDP, CU-1-01, lighting, SPD and load measurement requirements.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B101: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B110: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B122: Compare installed materials against approved submittals/spec sections.
Note on B131: Planned vs actual production supports delay/time-extension rebuttal.
Note on B139: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B18_Assessment (hidden)
BUILDING 18 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 18 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 15:59 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 18 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 110 / existing 111B and 213 / Telecom Room Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 18 includes new first-level Telecom Room 110 and existing telecom transition rooms 111B and 213; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, lead-paint/first-level hazardous material coordination, firestopping, cable tray, and PACS/CCTV integration remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify Telecom Room 110, existing TE 111B, existing Closet 213, and all active services; confirm B18-TR110A/B panel sources, IU/CU-1-01 cooling, FEC, fire alarm/sprinkler impacts, cable tray route, PACS/CCTV scope, lead-paint/hazardous impacts, and cutover plan.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
18 | 110 | First | New telecom room build area | Telecom Room | 1 | 1 | Verify | 18A-401 / 18E-101 / 18T-100 / 18T-401 / 18T-604 / 18T-701 | Primary Building 18 TR. Plans identify Telecom Room 110 at 168 SF, Rack ID TR01-111A-1, panels B18-TR110A/B, 208V rack UPS/PDU equipment, IU-1-01/CU-1-01 cooling, 315 feet total cable tray, and future rack allowance. Room 110 is the new rack room even though the schedule labels RM 111A.
18 | 111B | First | Existing TE / stair-adjacent legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 18T-401 / 18T-604 / 18R-900 | Existing first-level TE 111B shown at 13 SF with wall-mounted rack, plywood backboard, patch panel, security cabinet, existing floor UPS, and 5RU fiber optic housing. Protect active services and verify transfer to Room 110.
18 | 213 | Second | Existing telecom closet / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 18T-401 / 18T-604 / 18R-900 | Existing second-level Closet 213 shown at 8 SF with wall-mounted rack, plywood backboard, patch panel, security cabinet, APC floor UPS, SERTEX utility service ports, Cisco switch and legacy Ortronics patch panels. Protect active services and verify transfer to Room 110.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
110 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, 45-minute door/frame, access control, static-control floor sealer, rack/future rack clearances, wall backing, and cable tray/pathway entry points.
111B | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing first-level TE; verify active equipment status, pathway, rack/UPS/backboard, security cabinet, fiber housing and transition/abandonment scope.
213 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing second-level closet; verify active equipment status, pathway, rack/UPS/backboard, security cabinet and transition/abandonment scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
110 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls.
111B | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing TE room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover.
213 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing second-level closet; verify protection-in-place and firestopping after transfer or abandonment.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
110 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 110 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm.
111B | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing TE 111B; verify existing environmental conditions during cutover and whether legacy equipment remains active.
213 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Closet 213; verify existing environmental conditions during cutover and whether legacy equipment remains active.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
110 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B18-TR110A / B18-TR110B | Verify | Verify | Verify | Electrical plans/schedules identify B18-TR110A/B, 208V rack UPS requirements, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and telecom panelboard schedule requirements.
111B | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal.
213 | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify active equipment, APC UPS status, source circuits, SERTEX utility service and transfer requirements before disconnect/removal.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
110 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 18T-701 identifies RM 111A schedule: 86 WAO total, 61 active ports per survey, 122 ports per schedule, and 134 total ports with 10% allowance. New rack elevation is Room 110, 1 rack plus future, with UPS, Future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU.
111B | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 111B equipment includes wall-mounted rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber optic housing; verify active services and transfer plan to Room 110.
213 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 213 equipment includes SERTEX utility service ports, Cisco switch, multiple legacy Ortronics patch panels, wall/wall-mount TE and APC floor UPS; verify active services and transfer plan to Room 110.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
110 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 111A-CAM-01 and security/access-control scope for the new TR area; verify room naming, CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination.
111B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in 111B; verify whether security equipment remains, is relocated, or requires temporary protection during cutover.
213 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in 213; verify whether security equipment remains, is relocated, or requires temporary protection during cutover.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B18-R1 | All | Existing conditions for Room 110, Room 111B and Room 213 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B18 includes new first-level TR plus existing first and second-level telecom transition points.
B18-R2 | 110 | First-level hazardous material / lead-based paint abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | 18H-101 notes lead-based paint abatement through entire telecom room/door frames.
B18-R3 | 111B/213 | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing racks, SERTEX ports, Cisco switch, patch panels, security cabinets and UPS units shown.
B18-R4 | 110 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B18-R5 | 110 | 208V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B18-TR110A/B schedules, rack receptacles, SPD, labels, source circuits and LOTO needs | Electrical / GCC | Closed | Panel references are concentrated at Room 110 with CU-1-01 and rack receptacles.
B18-R6 | 110 | Cable tray and pathway scope crosses first and second levels | High | Medium | 6 | Verify 315 ft cable tray, supports, seismic bracing, 40% fill, penetrations, coordination with lighting/HVAC and labeling before install | Telecom / GC | Closed | Cable tray schedule: first level 174 ft, second level 141 ft.
B18-R7 | All | Telecom/fiber cutover could affect active hospital communications and legacy cross-building service ports | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | Room 213 existing rack elevation references SERTEX utility service ports to B17, B19 and B3.
B18-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B18-Q1 | Confirm final telecom scope: new Room 110 with existing 111B and 213 transition only? | VA / OIT / Designer | Closed |  |  | Room inventory or PMIS mapping could miss scope
B18-Q2 | Why does 18T-701 reference RM 111A while new rack/electrical plans identify Telecom Room 110? | VA / Designer / OIT | Closed |  |  | Room naming mismatch could affect PMIS tracking
B18-Q3 | What active services are currently fed from existing 111B and 213 equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B18-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 110? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B18-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 110? | GC / COR | Closed |  |  | Life-safety acceptance risk
B18-Q6 | Are B18-TR110A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B18-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B18-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B18-P001 | 110 | Existing Condition | Room 110 walls, ceiling/deck, floor, door, adjacent Corridor 121/Stair 122/Office 112, rack location, pathways and penetrations |  | Paul |  | B18-R1/B18-R2 | Closed
B18-P002 | 111B | Existing Condition | Existing TE 111B wall rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber housing |  | Paul |  | B18-R1/B18-R3 | Closed
B18-P003 | 213 | Existing Condition | Existing Closet 213 wall rack/TE, SERTEX service ports, Cisco switch, legacy Ortronics patch panels, security cabinet, plywood backboard and APC floor UPS |  | Paul |  | B18-R1/B18-R3 | Closed
B18-P004 | 110 | Hazardous Materials | First-level abatement/lead-paint areas, flooring, walls, ceiling/penetrations, and disturbance areas |  | Paul |  | B18-R2 | Closed
B18-P005 | 110 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop |  | Paul |  | B18-R6 | Closed
B18-P006 | 110 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B18-R4 | Closed
B18-P007 | 110 | Electrical | B18-TR110A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels |  | Paul |  | B18-R5 | Closed
B18-P008 | 110/111B/213 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 111A-CAM-01 and existing 111B/213 transfer work |  | Paul |  | B18-R7/B18-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
110 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | New first-level TR with one rack plus future rack, 208V UPS, cooling, access control, 315 ft cable tray and fire/life-safety coordination.
111B | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Existing first-level TE and transition point; protect active services until cutover complete.
213 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Existing second-level telecom closet and transition point; protect active services until cutover complete.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B18.20260316.pdf
Drawing Index | 48-sheet Building 18 IFC package includes general, first-level hazardous material abatement, architectural, interiors, fire protection, mechanical, electrical, telecommunications, enlarged telecom plans, rack elevations, telecom schedules, and photo references.
Architectural / Hazardous Basis | 18H-101 identifies first-level hazardous material abatement plan and lead-based paint abatement in the telecom room area. 18A-401 identifies first-level architectural enlarged views and rated/open-to-deck construction coordination for the new telecom room.
Telecom Basis | 18T-100/401 identify Telecom Room 110 at 168 SF, existing first-level TE 111B at 13 SF and existing second-level Closet 213 at 8 SF. 18T-604 identifies Room 110 new rack plus future rack, existing 111B fiber housing, and existing 213 SERTEX/Cisco/legacy patch equipment. 18T-701 identifies 86 WAO total, 61 active ports, 122 ports per schedule and 134 total ports with 10% allowance.
Mechanical Basis | 18M-100/701 identify dedicated split-system cooling for Telecom Room 110 using IU-1-01 and CU-1-01 with BACnet adapter/control coordination; verify emergency power, condensate and alarms in field.
Electrical Basis | 18E-101/601/701/702 identify B18-TR110A and B18-TR110B panel/circuit references, 208V rack UPS requirements, rack/TR receptacles, CU-1-01, lighting, SPD and telecom panelboard requirements.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B100: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B109: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B121: Compare installed materials against approved submittals/spec sections.
Note on B130: Planned vs actual production supports delay/time-extension rebuttal.
Note on B138: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B20_Assessment (hidden)
BUILDING 20 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 20 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 16:37 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 20 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 1B / existing 8A / Telecom Enclosure Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 20 is a telecom-enclosure building, not a full TR buildout. Scope centers on new first-level Office 1B wall-mount TE enclosure and existing Tel/Data Closet 8A; mechanical and fire protection scope are excluded by the cover sheet, but field verification, active equipment transfer, fiber/copper cutover, cable tray, firestopping, power/UPS/PDU, and existing equipment protection remain open.
HVAC Status | Excluded / Verify Existing | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Excluded / Firestop Only | Fire Alarm Status | Verify Existing
Security Status | Verify Existing | Next Action | Field verify Office 1B new TE location, existing Tel/Data Closet 8A, active services, TE01-1B-1 schedule, existing open TE cabinet, existing ground bar/patch panel/equipment box/indoor AC/backboard, 459 ft cable tray route, 10 Cat6A cross-connect cables, power/UPS/PDU source, and fiber Path A/B cutover.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
20 | 1B | First | Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 20T-101 / 20T-701 / 20E-101 / 20E-601 | Primary Building 20 TE. Plans identify Office 1B at 110 SF with new wall-mount telecom enclosure Rack ID TE01-1B-1, 12RU enclosure, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and 33 total ports with 10% allowance.
20 | 8A | First | Existing Tel/Data Closet / open TE cabinet | Existing telecom transition point | 2 | 0 | Verify | 20T-101 / 20T-701 / 20R-900 | Existing Tel/Data Closet 8A at 17 SF with existing open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy Ortronics 48-port patch panel, floor UPS and Fiber LIU. Protect active services and transfer to Office 1B TE.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
1B | Verify | Verify | N/A / Office | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in Office 1B; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, and that office use can remain operational.
8A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing Tel/Data Closet; verify active equipment status, existing open cabinet, indoor AC, ground bar/backboard, floor UPS, pathway and transition/abandonment scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
1B | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 20 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts.
8A | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing closet; verify protection-in-place and firestopping after cable transfer or reuse.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
1B | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Cover sheet states mechanical scope is excluded. Verify whether Office 1B ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment.
8A | Existing indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Tel/Data Closet 8A includes indoor AC unit to remain/protect in place; verify operation during cutover and whether equipment remains after transition.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
1B | Verify | APC UPS / TE enclosure | Verify | Verify | 20E-101 / 20E-601 source to verify | Verify | Verify | Verify | 20T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels.
8A | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing 8A elevation shows UPS on ground, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
1B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 20T-701 identifies TE01-1B-1: 21 WAO total, 24 active ports per survey, 30 ports per schedule, 33 total ports with 10% allowance. Provide new wall-mount TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location.
8A | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Tel/Data Closet 8A contains open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy 48-port patch panel and Fiber LIU. Field verify all active services.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
1B | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 20 does not appear to create a new TR door/PACS package. Verify any existing cameras/security devices in Office 1B and ensure no camera angle or VMS integration is disrupted.
8A | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Keynotes indicate existing cameras are to be retained and re-used/protected in place; verify existing security equipment and cabinet impacts during cutover.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B20-R1 | All | Existing conditions for new Office 1B TE and existing Tel/Data Closet 8A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B20 has a compact TE scope but still depends on field conditions and existing equipment transfer.
B20-R2 | 1B/8A | Existing equipment in 8A may remain active during transfer to new TE in 1B | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 20T-101 keynotes require transfer of existing devices and phasing plan.
B20-R3 | 1B | Room naming and TE designation could cause PMIS mapping confusion | Medium | Medium | 4 | Track as Building 20 / Office 1B / TE01-1B-1 and link existing Room 8A as transition point | GCC / VA | Closed | Schedule is Office 1B and rack ID TE01-1B-1; existing telecom room is 8A.
B20-R4 | 1B | No mechanical scope, but TE/UPS/network equipment may add heat load to Office 1B | High | Medium | 6 | Verify heat load, office ventilation, equipment clearances and owner acceptance before energizing enclosure | VA / Electrical / Telecom | Closed | Cover excludes mechanical/fire protection; existing HVAC may be relied on.
B20-R5 | 1B | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs.
B20-R6 | All | 459 feet of cable tray/pathway requires coordination despite small port count | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | Telecom / GC | Closed | 20T-701 cable tray schedule lists Level 1 estimated length of 459 ft.
B20-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | 20T-101 requires fire caulk at sleeves and rated penetration protection.
B20-R8 | All | Commissioning/test documentation may be overlooked due to TE-only scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification and owner signoff | GC / Cx Manager | Closed | Cover/general notes still require testing, acceptance and documentation.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B20-Q1 | Confirm final scope: new wall-mount TE enclosure in Office 1B and existing Tel/Data Closet 8A transition only? | VA / OIT / Designer | Closed |  |  | Room inventory or PMIS mapping could miss scope
B20-Q2 | What active services are currently fed from existing 8A open TE cabinet and related equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B20-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Office 1B? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B20-Q4 | Is Office 1B HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed |  |  | Heat/load risk after mechanical scope excluded
B20-Q5 | Are existing cameras/security devices in Building 20 protected and retained with no VMS/PACS changes? | Security / OIT | Closed |  |  | Security continuity unclear
B20-Q6 | Are all 459 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed |  |  | Install delay or firestop gap
B20-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed |  |  | Cutover and labeling risk
B20-Q8 | Which test records and turnover documents are required for TE-only acceptance? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B20-P001 | 1B | Existing Condition | Office 1B wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location |  | Paul |  | B20-R1/B20-R3 | Closed
B20-P002 | 8A | Existing Condition | Existing Tel/Data Closet 8A open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard and cable entries |  | Paul |  | B20-R1/B20-R2 | Closed
B20-P003 | 8A | Existing Equipment | BIX blocks, Cisco switch, legacy Ortronics 48-port patch panel, UPS on ground and Fiber LIU on wall |  | Paul |  | B20-R2/B20-R5 | Closed
B20-P004 | 1B/8A | Pathway | 459 ft Level 1 cable tray route, sleeves, wall penetrations, support points, light/HVAC conflicts and 40% fill concerns |  | Paul |  | B20-R6/B20-R7 | Closed
B20-P005 | 1B | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and disconnect/access |  | Paul |  | B20-R5 | Closed
B20-P006 | 1B/8A | Telecom | TE01-1B-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer |  | Paul |  | B20-R2/B20-R8 | Closed
B20-P007 | All | Firestop | 4-inch speed sleeve, wall penetrations and fire caulk before/after photos |  | Paul |  | B20-R7 | Closed
B20-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition |  | Paul |  | B20-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
1B | 50% | 50% | N/A / Verify | 50% | 50% | Verify | 50% | Partial / Yellow | New first-level Office TE with 12RU wall enclosure, UPS/PDU, 459 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
8A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Existing Tel/Data Closet and transition point; protect active services until cutover complete.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B20.20260316(1).pdf
Drawing Index | 24-sheet Building 20 IFC package includes general, architectural, electrical, telecommunications, telecom schedules/rack elevations, and photo references. There is no mechanical/fire protection drawing package for this building.
Scope Basis | Cover sheet note 4 states Building 20 is to receive a Telecom Enclosure and mechanical/fire protection scope has been excluded.
Telecom Basis | 20T-101 identifies Office 1B new TE location at 110 SF and existing Tel/Data Closet 8A at 17 SF with existing open TE cabinet/equipment. 20T-701 identifies Rack ID TE01-1B-1, 21 WAO total, 24 active ports, 30 ports per schedule, 33 total with 10% allowance, 459 ft Level 1 cable tray, and new 12RU telecom enclosure equipment.
Electrical Basis | 20E-101/601 provide the electrical plan and one-line/schedule references; verify power source, UPS/PDU receptacles, bonding/grounding, SPD/labels if applicable, and circuit capacity in field.
Operational Basis | General notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, testing/labeling/documentation, VA/OIT acceptance before active connections, and shutdowns limited one at a time.
Photo Basis | 20R-900 provides the first-level existing telecom room 8A photo reference for existing cabinet/equipment verification.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B92: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B101: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B113: Compare installed materials against approved submittals/spec sections.
Note on B122: Planned vs actual production supports delay/time-extension rebuttal.
Note on B130: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B21_Assessment (hidden)
BUILDING 21 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 21 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 17:01 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 21_19 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 100A / existing B1.TR and B19 B05TR / Telecom Enclosure Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 21 is combined with Building 19 and is primarily a telecom-enclosure scope. New first-level M&O Foreman Office 100A / RM 104 schedule is served by a new 12RU TE enclosure, while existing Building 21 B1.TR and Building 19 B05TR equipment remain transition points. Fire protection scope is excluded, but mechanical/electrical sheets exist for equipment support. Field verification, active-service transfer, 659 ft cable tray, firestopping, UPS/PDU power, fiber/copper cutover, and B19/B21 scope boundary remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Excluded / Firestop Only | Fire Alarm Status | Verify Existing
Security Status | Verify Existing | Next Action | Field verify new TE location at M&O Foreman Office 100A, existing B21 B1.TR, existing B19 B05TR, B19-serving-B21 relationship, active services, TR01-104-1 / 100-A schedule, 659 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, and all firestopping/penetrations.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
21 | 100A | First | M&O Foreman Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 21_19T-101 / 21_19T-604 / 21_19T-701 / 21_19E-101 | Primary Building 21/B19 TE. Plans identify M&O Foreman Office 100A at 202 SF with new 12RU telecom enclosure, shown as 19 serving 21, Room 100-A, and schedule Rack ID TR01-104-1 / RM 104. Includes APC UPS, two PDUs, network switches B20 and B19, 48-port Cat6A patch panel, Fiber LIU, and 131 total ports with 10% allowance.
21 | B1.TR | Basement | Existing telecom room / wall-mount TE | Existing telecom transition point | 1 | 0 | Verify | 21_19T-100 / 21_19T-604 | Existing Building 21 basement B1.TR shown with legacy Ortronics 24/48-port patch panels, UPS on ground, Cisco switch, multiple legacy 24-port patch panels, Fiber LIU, and APC floor UPS. Protect active services and verify transfer/cutover to new TE.
19 | B05TR | Basement / First | Existing telecom room / wall-mount TE | Existing telecom transition point serving B19/B21 | 2 | 0 | Verify | 21_19T-100 / 21_19T-604 / 21_19R-900 | Existing Building 19 B05TR shown with basement and first-level existing elevations, legacy Ortronics patch panels, Cisco switch, Fiber LIU, APC floor UPS, and photo reference for basement B05. New enclosure is marked '19 serving 21'.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
100A | Verify | Verify | N/A / Office | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in M&O Foreman Office 100A; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, and that office use can remain operational.
B1.TR | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing B21 basement telecom room; verify active equipment status, pathway, UPS/backboard, Fiber LIU, and transition/abandonment scope.
B05TR | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing B19 telecom room/equipment; verify active services, B19/B21 service boundary, path to new TE, and transition scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
100A | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 21_19 receives a Telecom Enclosure and fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts.
B1.TR | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing B21 basement TR; verify protection-in-place and firestopping after cable transfer or reuse.
B05TR | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing B19 B05TR; verify protection-in-place and firestopping after cable transfer or reuse.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
100A | Verify / Existing HVAC | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical sheets exist in index. Verify whether new TE heat load in Office 100A is supported by existing/new HVAC and whether any mechanical scope applies despite TE designation.
B1.TR | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing B21 B1.TR; verify environmental conditions during cutover and whether legacy equipment remains active.
B05TR | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing B19 B05TR; verify environmental conditions and whether equipment remains active during/after Building 21 transfer.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
100A | Verify | APC UPS / TE enclosure | Verify | Verify | 21_19E-101 / 21_19E-701 source to verify | Verify | Verify | Verify | 21_19T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switches, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels.
B1.TR | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing B21 B1.TR elevation shows UPS on ground, Cisco switch, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements.
B05TR | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing B19 B05TR elevations show APC floor UPS, legacy patch panels, Cisco switch and Fiber LIU; verify power source, active equipment and transfer/retention requirements.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
100A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 21_19T-701 identifies RM 104 schedule: 90 WAO total, 67 active ports per survey, 119 ports per schedule, and 131 total ports with 10% allowance. 659 ft cable tray total: 63 ft basement and 596 ft first level.
B1.TR | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B21 B1.TR equipment includes multiple legacy patch panels, Cisco switch, UPS on ground, Fiber LIU and APC floor UPS; verify active services and transfer plan to new TE.
B05TR | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B19 B05TR equipment includes legacy Ortronics patch panels, Cisco switch, Fiber LIU and APC floor UPS; verify active services and whether B19/B21 devices are served from new enclosure.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
100A | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 21_19 appears to create a TE enclosure rather than a full TR door/PACS package. Verify any existing cameras/security devices in Room 100A and ensure no camera angle or VMS integration is disrupted.
B1.TR | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify any existing security device/cabinet impacts during cutover.
B05TR | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/camera protection-in-place and any impact from B19/B21 shared telecom equipment.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B21-R1 | All | Existing conditions for new 100A TE, B21 B1.TR and B19 B05TR not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B21 is combined with B19 and has multiple transition points.
B21-R2 | 100A/B1.TR/B05TR | Existing equipment may remain active during transfer to new TE enclosure | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | Rack elevations show existing B21 and B19 equipment and new 19-serving-21 enclosure.
B21-R3 | 100A | Room naming mismatch: schedule says RM 104 / TR01-104-1 while plan/enlarged view identifies Room 100A | High | Medium | 6 | Track PMIS as Building 21 / Room 100A / Schedule RM 104 / Rack ID TR01-104-1 and confirm with designer | GCC / VA / Designer | Closed | Important for PMIS mapping and field punch list.
B21-R4 | All | B19/B21 combined package may blur scope boundary and ownership of ports | High | Medium | 6 | Separate Building 21 work, Building 19 transition work, and shared service/cross-connect items in PMIS notes | GCC / OIT | Closed | Sheet package is 21_19 and new enclosure is labeled 19 serving 21.
B21-R5 | 100A | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and PDUs.
B21-R6 | All | 659 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | Telecom / GC | Closed | 21_19T-701 cable tray schedule lists 63 ft basement and 596 ft first level.
B21-R7 | All | Fire protection scope excluded, but rated penetrations and temporary firestopping still apply | High | Medium | 6 | Track 4-inch sleeves, rated penetrations, fire caulk, temporary firestopping and patching even without FP scope | GC / Firestop | Closed | Cover excludes fire protection; telecom notes require fire caulk and rated penetrations.
B21-R8 | All | Commissioning/test documentation may be overlooked due to TE-only scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification and owner signoff | GC / Cx Manager | Closed | General notes still require testing, acceptance and documentation.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B21-Q1 | Confirm final scope: new TE enclosure at Room 100A/RM 104 and existing B21 B1.TR plus B19 B05TR transition? | VA / OIT / Designer | Closed |  |  | Room inventory or PMIS mapping could miss scope
B21-Q2 | Why does 21_19T-701 list RM 104 / TR01-104-1 while enlarged plan identifies Room 100A? | VA / Designer / OIT | Closed |  |  | Room naming mismatch could affect PMIS tracking
B21-Q3 | What active services are currently fed from existing B21 B1.TR and B19 B05TR equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B21-Q4 | What exactly is meant by '19 serving 21' on the new TE enclosure elevation? | VA / OIT / Designer | Closed |  |  | Building 19/21 boundary unclear
B21-Q5 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in 100A? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B21-Q6 | Are all 659 ft of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed |  |  | Install delay or firestop gap
B21-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed |  |  | Cutover and labeling risk
B21-Q8 | Which test records and turnover documents are required for TE-only acceptance? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B21-P001 | 100A | Existing Condition | M&O Foreman Office 100A wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location |  | Paul |  | B21-R1/B21-R3 | Closed
B21-P002 | B1.TR | Existing Condition | Existing B21 basement B1.TR wall TE, legacy patch panels, Cisco switch, Fiber LIU, UPS on ground and cable entries |  | Paul |  | B21-R1/B21-R2 | Closed
B21-P003 | B05TR | Existing Condition | Existing B19 B05TR basement and first-level TE/equipment, APC floor UPS, Cisco switch, patch panels, Fiber LIU and pathways |  | Paul |  | B21-R1/B21-R4 | Closed
B21-P004 | 100A/B05TR/B1.TR | Pathway | 659 ft cable tray route, sleeves, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns |  | Paul |  | B21-R6/B21-R7 | Closed
B21-P005 | 100A | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access |  | Paul |  | B21-R5 | Closed
B21-P006 | 100A/B1.TR/B05TR | Telecom | TR01-104-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer |  | Paul |  | B21-R2/B21-R8 | Closed
B21-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos |  | Paul |  | B21-R7 | Closed
B21-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition |  | Paul |  | B21-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
100A | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level TE with 12RU wall enclosure, UPS/PDU, 659 ft cable tray, fiber/copper cutover and B19/B21 room naming coordination.
B1.TR | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Building 21 basement telecom transition point; protect active services until cutover complete.
B05TR | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Building 19 telecom transition point tied into Building 21 scope; confirm shared service boundary.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B21_19.20260316.pdf
Drawing Index | 37-sheet Building 21_19 IFC package includes general, architectural, mechanical, electrical, telecommunications, telecom rack elevations, schedules, fiber risers, and photo references.
Scope Basis | Cover sheet note 4 states this building is to receive a Telecom Enclosure and fire protection scope has been excluded. Mechanical/electrical sheets are still included in the drawing index.
Telecom Basis | 21_19T-101 identifies B21/B19 first-level telecom plan and new enlarged plan at Room 100A, with 55 data ports served for B21 area. 21_19T-604 identifies existing B19 B05TR, existing B21 B1.TR, and new 19-serving-21 12RU TE enclosure at 100-A. 21_19T-701 identifies RM 104 / TR01-104-1 with 90 WAO total, 67 active ports, 119 ports per schedule, 131 total with 10% allowance, and 659 ft cable tray.
Electrical / Mechanical Basis | 21_19E and 21_19M sheets exist for basement/first level and schedules; verify power source, UPS/PDU receptacles, bonding/grounding, and any cooling/environmental support in field.
Operational Basis | General notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, testing/labeling/documentation, VA/OIT acceptance before active connections, and shutdowns limited one at a time.
Photo Basis | 21_19R-900 provides photo reference for basement-level existing telecom room B05.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B100: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B109: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B121: Compare installed materials against approved submittals/spec sections.
Note on B130: Planned vs actual production supports delay/time-extension rebuttal.
Note on B138: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B22_Assessment (hidden)
BUILDING 22 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 22 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 17:11 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 22 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 102 / existing 103 / Telecom Enclosure Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 22 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new first-level Break Room 102 TE enclosure and existing first-level wall/wall-mount TE Room 103. Field verification, active service transfer, 139 ft cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, and B19 utility service relationship remain open.
HVAC Status | Excluded / Verify Existing | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Excluded / Firestop Only | Fire Alarm Status | Verify Existing
Security Status | Verify Existing | Next Action | Field verify Break Room 102 new TE location, existing Room 103 wall/wall-mount TE, active services, TR01-102-1 schedule, 139 ft cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, and existing B19 port relationship.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
22 | 102 | First | Break Room / new TE location | Telecom Enclosure | 1 | 0 | Verify | 22T-101 / 22T-701 / 22E-101 / 22E-701 | Primary Building 22 TE. Plans identify Break Room 102 at 358 SF with new 12RU telecom enclosure Rack ID TR01-102-1, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and 8 total ports with 10% allowance.
22 | 103 | First | Existing wall/wall-mount TE / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 22T-101 / 22T-701 / 22R-900 | Existing Room 103 first-level wall/wall-mount TE shown with APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall, and ports 1-24 to Building 19 ports 73-96. Protect active services and transfer to Room 102 TE.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
102 | Verify | Verify | N/A / Break Room | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in Break Room 102; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, and that break-room use can remain operational.
103 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing first-level wall/wall-mount TE; verify active equipment status, UPS, Cisco switch, SERTEX utility service, Fiber LIU, pathway, and transition/abandonment scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
102 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 22 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts.
103 | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing TE room; verify protection-in-place and firestopping after cable transfer or reuse.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
102 | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Cover sheet states mechanical scope is excluded. Verify whether Break Room 102 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment.
103 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Room 103 equipment area; verify existing environmental conditions during cutover and whether legacy equipment remains active.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
102 | Verify | APC UPS / TE enclosure | Verify | Verify | 22E-101 / 22E-701 source to verify | Verify | Verify | Verify | 22T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels.
103 | Existing | Existing APC UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing 103 elevation shows APC UPS, Cisco switch, SERTEX utility service, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 22T-701 identifies TR01-102-1: 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total port quantities, and 8 total ports with 10% allowance. Provide new wall-mount 12RU TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location.
103 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 103 contains APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall and ports 1-24 to Bldg 19 ports 73-96. Field verify all active services and B19 handoff.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
102 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 22 does not appear to create a new full TR door/PACS package. Verify any existing cameras/security devices in Break Room 102 and ensure no camera angle or VMS integration is disrupted.
103 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify security/access conditions and whether any legacy security equipment is present at existing TE location.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B22-R1 | All | Existing conditions for new Break Room 102 TE and existing Room 103 TE not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B22 has a compact TE scope but still depends on field conditions and existing equipment transfer.
B22-R2 | 102/103 | Existing equipment in 103 may remain active during transfer to new TE in 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 22T-101 keynotes require transfer of existing devices and phasing plan.
B22-R3 | 102 | Break Room 102 use may conflict with wall-mount TE access and clearances | Medium | Medium | 4 | Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance | GCC / VA | Closed | New TE is in Break Room 102 rather than a dedicated TR.
B22-R4 | 102 | No mechanical scope, but TE/UPS/network equipment may add heat load to Break Room 102 | High | Medium | 6 | Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure | VA / Electrical / Telecom | Closed | Cover excludes mechanical/fire protection; existing HVAC may be relied on.
B22-R5 | 102 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs.
B22-R6 | All | 139 feet of cable tray/pathway requires coordination despite small port count | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | Telecom / GC | Closed | 22T-701 cable tray schedule lists first floor estimated length of 139 ft.
B22-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | 22T-101 requires fire caulk at sleeves and rated penetration protection.
B22-R8 | 103 / B19 | Existing SERTEX utility service and B19 port relationship may create cutover dependency | High | Medium | 6 | Verify ports 1-24 to Bldg 19 ports 73-96, service provider dependency, labels, test records and OIT approval | Telecom / OIT | Closed | Existing Room 103 elevation identifies ports to Building 19.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B22-Q1 | Confirm final scope: new wall-mount TE enclosure in Break Room 102 and existing Room 103 transition only? | VA / OIT / Designer | Closed |  |  | Room inventory or PMIS mapping could miss scope
B22-Q2 | What active services are currently fed from existing Room 103 equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B22-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B22-Q4 | Is Break Room 102 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed |  |  | Heat/load risk after mechanical scope excluded
B22-Q5 | Are existing cameras/security devices in Building 22 protected and retained with no VMS/PACS changes? | Security / OIT | Closed |  |  | Security continuity unclear
B22-Q6 | Are all 139 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed |  |  | Install delay or firestop gap
B22-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed |  |  | Cutover and labeling risk
B22-Q8 | What is the operational impact of Room 103 ports 1-24 to Building 19 ports 73-96? | VA / OIT / Designer | Closed |  |  | B19 dependency/cutover risk
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B22-P001 | 102 | Existing Condition | Break Room 102 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location |  | Paul |  | B22-R1/B22-R3 | Closed
B22-P002 | 103 | Existing Condition | Existing Room 103 wall/wall-mount TE, APC UPS, Cisco switch, SERTEX utility service, legacy patch panel, Fiber LIU and cable entries |  | Paul |  | B22-R1/B22-R2 | Closed
B22-P003 | 103 / B19 | Existing Equipment | Ports 1-24 to Building 19 ports 73-96, active service labeling, utility service and handoff condition |  | Paul |  | B22-R8 | Closed
B22-P004 | 102/103 | Pathway | 139 ft first-floor cable tray route, sleeves, wall penetrations, support points, light/HVAC conflicts and 40% fill concerns |  | Paul |  | B22-R6/B22-R7 | Closed
B22-P005 | 102 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access |  | Paul |  | B22-R5 | Closed
B22-P006 | 102/103 | Telecom | TR01-102-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer |  | Paul |  | B22-R2/B22-R8 | Closed
B22-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos |  | Paul |  | B22-R7 | Closed
B22-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition |  | Paul |  | B22-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
102 | 0.5 | 0.5 | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New first-level Break Room TE with 12RU wall enclosure, UPS/PDU, 139 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
103 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing wall/wall-mount TE and transition point; protect active services until cutover complete.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B22.20260316.pdf
Drawing Index | 25-sheet Building 22 IFC package includes general, architectural, electrical, telecommunications, telecom schedules/rack elevations, fiber risers, and photo references. Mechanical and fire protection drawing packages are excluded for this building.
Scope Basis | Cover sheet note 4 states Building 22 is to receive a Telecom Enclosure and mechanical/fire protection scope has been excluded.
Telecom Basis | 22T-101 identifies Break Room 102 at 358 SF and the new TE location served from Level 01, with existing/relocated Trane BMS, patch panel, keypad and equipment box noted in the demo/enlarged view. 22T-701 identifies Rack ID TR01-102-1, 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total ports, 8 total ports with 10% allowance, 139 ft first-floor cable tray, and new 12RU telecom enclosure equipment.
Existing Equipment Basis | 22T-701 existing elevation identifies Room 103 first-level wall/wall-mount TE with APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall, and ports 1-24 to Building 19 ports 73-96.
Electrical Basis | 22E-101/601/701 provide electrical plan, one-line and schedule references; verify power source, UPS/PDU receptacles, bonding/grounding, circuit capacity and labels in field.
Operational Basis | General notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, testing/labeling/documentation, VA/OIT acceptance before active connections, and shutdowns limited one at a time.
Photo Basis | 22R-900 provides the first-level existing telecom room photo reference labeled Room 124; verify if this is a photo-label mismatch or related existing room reference.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B94: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B103: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B115: Compare installed materials against approved submittals/spec sections.
Note on B124: Planned vs actual production supports delay/time-extension rebuttal.
Note on B132: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B33_Assessment (hidden)
BUILDING 33 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 33 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 18:32 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 33 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B23 / existing B17 / Telecom Enclosure Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 33 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new basement EEO Manager Office B23 TE enclosure and existing Tel Closet B17. Field verification, active service transfer, 102 ft basement cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, fiber/copper cutover, and legacy service relationships to Buildings 3, 80 and 82 remain open.
HVAC Status | Excluded / Verify Existing | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Excluded / Firestop Only | Fire Alarm Status | Verify Existing
Security Status | Verify Existing | Next Action | Field verify EEO Manager Office B23 new TE location, existing Tel Closet B17, active services, TE01-B23-1 schedule, 102 ft basement cable tray route, 10 Cat6A cross-connect cables, UPS/PDU source, fiber paths A/B, firestopping/sleeves, existing camera/security devices, and B17 legacy port/service relationships.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
33 | B23 | Basement | EEO Manager Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 33T-100 / 33T-604 / 33T-701 / 33E-100 / 33E-701 | Primary Building 33 TE. Plans identify EEO Manager Office B23 at 175 SF with new 12RU telecom enclosure Rack ID TE01-B23-1, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, 55 WAO total, and 97 total ports with 10% allowance.
33 | B17 | Basement / First photo reference | Existing Tel Closet / open TE cabinet and legacy equipment | Existing telecom transition point | 2 | 0 | Verify | 33T-100 / 33T-604 / 33R-900 | Existing Tel Closet B17 shown at 13 SF with existing open TE cabinet, network door controller, indoor AC unit, plywood backboard, keypad, patch panel, ground bar, equipment box, Cisco switches, legacy patch panels, Fiber LIU, SERTEX utility service, and UPS on floor. Protect active services and verify transfer to Room B23 TE.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B23 | Verify | Verify | N/A / Office | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in EEO Manager Office B23; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, and office-use impacts.
B17 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing Tel Closet; verify active equipment status, open TE cabinet, indoor AC, network door controller, keypad/security devices, UPS, backboard, Fiber LIU, and transition/abandonment scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B23 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 33 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts.
B17 | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing Tel Closet; verify protection-in-place and firestopping after cable transfer or reuse.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B23 | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Cover sheet states mechanical scope is excluded. Verify whether Office B23 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment.
B17 | Existing indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing B17 enlarged plan identifies an existing indoor AC unit. Verify operation during cutover and determine whether active legacy equipment remains after transfer to B23.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B23 | Verify | APC UPS / TE enclosure | Verify | Verify | 33E-100 / 33E-701 source to verify | Verify | Verify | Verify | 33T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels.
B17 | Existing | Existing UPS on floor | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing B17 elevations show UPS on floor, Cisco switches, SERTEX utility service, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements before disconnect/removal.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B23 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 33T-701 identifies TE01-B23-1: 55 WAO total, 34 active ports per survey, 88 total ports per schedule, and 97 total ports with 10% allowance. Basement cable tray schedule totals 102 ft. Provide 10 new Cat6A cross-connect cables from existing TE to new TE location.
B17 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B17 rack elevations include Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, passive Fiber LIU/wall mount, UPS on floor and cross-building port references to Bldgs 3, 80 and 82.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
B23 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 33 does not appear to create a new full TR door/PACS package. Verify existing cameras/security devices in B23 and ensure no camera angle or VMS integration is disrupted.
B17 | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify | Verify | Existing B17 enlarged plan identifies network door controller, keypad and equipment box; verify protection-in-place and whether any security equipment is relocated or recabled.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B33-R1 | All | Existing conditions for new B23 TE and existing B17 Tel Closet not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B33 has a compact TE scope but depends on existing equipment transfer and field conditions.
B33-R2 | B23/B17 | Existing equipment in B17 may remain active during transfer to new TE in B23 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 33T-100 keynotes require transfer of existing devices and phasing plan.
B33-R3 | B23 | Office B23 use may conflict with wall-mount TE access and clearances | Medium | Medium | 4 | Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance | GCC / VA | Closed | New TE is in EEO Manager Office B23 rather than a dedicated TR.
B33-R4 | B23 | No mechanical scope, but TE/UPS/network equipment may add heat load to Office B23 | High | Medium | 6 | Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure | VA / Electrical / Telecom | Closed | Cover excludes mechanical/fire protection; existing HVAC may be relied on.
B33-R5 | B23 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs.
B33-R6 | All | 102 feet of basement cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | Telecom / GC | Closed | 33T-701 cable tray schedule lists basement level estimated length of 102 ft.
B33-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | 33T-100 requires fire caulk at sleeves and rated penetration protection.
B33-R8 | B17 / Other Bldgs | Existing B17 cross-building service relationships may create cutover dependency | High | Medium | 6 | Verify ports to Bldgs 3, 80 and 82, SERTEX utility service, labels, test records, service provider dependency and OIT approval | Telecom / OIT | Closed | Existing B17 elevation identifies ports 1-72 to Bldg 3, 73-96 to Bldg 80, 97-120 to Bldg 82, and 121-144 to Bldg 3.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B33-Q1 | Confirm final scope: new wall-mount TE enclosure in B23 and existing B17 transition only? | VA / OIT / Designer | Closed |  |  | Room inventory or PMIS mapping could miss scope
B33-Q2 | What active services are currently fed from existing B17 equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B33-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in B23? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B33-Q4 | Is Office B23 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed |  |  | Heat/load risk after mechanical scope excluded
B33-Q5 | Are existing cameras/security devices in Building 33 protected and retained with no VMS/PACS disruption? | Security / OIT | Closed |  |  | Security continuity unclear
B33-Q6 | Are all 102 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed |  |  | Install delay or firestop gap
B33-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed |  |  | Cutover and labeling risk
B33-Q8 | What is the operational impact of B17 ports serving Buildings 3, 80 and 82? | VA / OIT / Designer | Closed |  |  | Cross-building dependency/cutover risk
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B33-P001 | B23 | Existing Condition | EEO Manager Office B23 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location |  | Paul |  | B33-R1/B33-R3 | Closed
B33-P002 | B17 | Existing Condition | Existing Tel Closet B17 open TE cabinet, network door controller, indoor AC unit, plywood backboard, keypad, patch panel, ground bar and equipment box |  | Paul |  | B33-R1/B33-R2 | Closed
B33-P003 | B17 | Existing Equipment | Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, Fiber LIU, UPS on floor and cross-building port labels |  | Paul |  | B33-R2/B33-R8 | Closed
B33-P004 | B23/B17 | Pathway | 102 ft basement cable tray route, 4-inch sleeve, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns |  | Paul |  | B33-R6/B33-R7 | Closed
B33-P005 | B23 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access |  | Paul |  | B33-R5 | Closed
B33-P006 | B23/B17 | Telecom | TE01-B23-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing B17 equipment transfer |  | Paul |  | B33-R2/B33-R8 | Closed
B33-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos |  | Paul |  | B33-R7 | Closed
B33-P008 | B17/B23 | Security / Existing Devices | Existing cameras, network door controller, keypad and equipment box to remain/protect or be recabled |  | Paul |  | B33-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B23 | 0.5 | 0.5 | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New basement office TE with 12RU wall enclosure, UPS/PDU, 102 ft cable tray, fiber/copper cutover and no dedicated mechanical/FP scope.
B17 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing Tel Closet and transition point; protect active services until cutover complete.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B33.20260316.pdf
Drawing Index | 26-sheet Building 33 IFC package includes general, architectural, electrical, telecommunications, telecom schedules/rack elevations, fiber risers, and photo references. Mechanical and fire protection drawing packages are excluded for this building.
Scope Basis | Cover sheet note 4 states Building 33 is to receive a Telecom Enclosure and mechanical/fire protection scope has been excluded.
Telecom Basis | 33T-100 identifies EEO Manager Office B23 at 175 SF as the new TE location and existing Tel Closet B17 at 13 SF with existing open TE cabinet/equipment. 33T-604 identifies existing B17 rack/equipment and new B23 12RU TE enclosure. 33T-701 identifies Rack ID TE01-B23-1, 55 WAO total, 34 active ports, 88 ports per schedule, 97 total ports with 10% allowance and 102 ft basement cable tray.
Existing Equipment Basis | 33T-604 existing B17 elevations identify Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, Fiber LIU wall mount, UPS on floor and ports serving Buildings 3, 80 and 82.
Electrical Basis | 33E-100/601/701 provide electrical plan, one-line and schedule references; verify power source, UPS/PDU receptacles, bonding/grounding, circuit capacity and labels in field.
Operational Basis | General notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, testing/labeling/documentation, VA/OIT acceptance before active connections, and shutdowns limited one at a time.
Photo Basis | 33R-900 provides the existing telecom room photo reference labeled First Level Existing Telecom Room B17; coordinate with plan/rack elevation references that show B17 equipment and basement/first-level labeling.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B93: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B102: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B114: Compare installed materials against approved submittals/spec sections.
Note on B123: Planned vs actual production supports delay/time-extension rebuttal.
Note on B131: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B62_TR_Assessment (hidden)
BUILDING 62 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 62 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 12:30 | Reviewer | Paul Thibodeau | Source Package | IFC B62 Drawings | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B24A, 125, 225 / TR Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Cooling / emergency power not verified
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Verify cooling power path, firestopping, extinguisher location, and existing conditions
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
62 | B24A | Basement | Restroom / Storage | TR | 1 | 1 | Verify | B62 IFC
62 | 125 | First | Medication Room | TR | 1 | 1 | Verify | B62 IFC
62 | 225 | Second | Office | TR | 1 | 1 | Verify | B62 IFC
2. ROOM READINESS
Room | Walls | Ceiling | Floor | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B24A | Verify | Verify | Verify | Verify | Verify | Verify | Pass | Verify
125 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
225 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B24A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
125 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
225 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls Tested | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B24A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
125 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
225 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B24A | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify
125 | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify
225 | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify
6. TELECOM
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B24A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
125 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
225 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
7. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B62-R1 | All | Cooling redundancy / emergency power not verified | High | Medium | 6 | Confirm power path for cooling, controls, condensate pump | GCC / VA | Closed
B62-R2 | All | Firestopping condition unknown | High | Medium | 6 | Survey penetrations and temporary/permanent firestop plan | GCC | Closed
B62-R3 | All | Existing room conditions undocumented | Medium | High | 6 | Create photo record before construction begins | GCC | Closed
B62-R4 | All | Condensate leak risk near IT equipment | High | Medium | 6 | Verify condensate routing and alarms | GCC / Contractor | Closed
8. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B62-Q1 | Are cooling units emergency powered? | VA / Designer | Closed |  |  | Cannot confirm continuity of operations
B62-Q2 | Are future rack loads included in HVAC sizing? | Designer | Closed |  |  | Cooling may be undersized after expansion
B62-Q3 | Is extinguisher location identified within 75 feet? | Contractor / COR | Closed |  |  | Life safety / acceptance risk
B62-Q4 | Are all penetrations fully documented and firestopped? | Contractor / Designer | Closed |  |  | Fire/smoke spread risk
9. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B62-P001 | B24A | Existing Condition | Existing room condition |  | Paul |  |  | Closed
B62-P002 | 125 | Existing Condition | Existing room condition |  | Paul |  |  | Closed
B62-P003 | 225 | Existing Condition | Existing room condition |  | Paul |  |  | Closed
B62-P004 | All | Firestop | Penetration/firestopping photo |  | Paul |  | B62-R2 | Closed
10. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B24A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow
125 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow
225 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Rack installed and secured.
Ladder tray installed.
Cable management installed.
Ground busbar installed.
Bonding complete.
Exposed piping bonded.
Patch panels installed.
Fiber LIU installed.
Labeling complete.
Testing complete.
VA acceptance before connection to active operations.
8. PMIS Survey Form for Cameron / EHRM Team
Recommended PMIS columns:
Field | Entry
Building | 62
Room | B24A / 125 / 225
Floor | Basement / First / Second
Existing Use | Restroom-storage / medication room / office
TR Type | TR
Rack Count | 1 new + 1 future
Cooling Provided | Yes / No / Verify
Cooling Capacity | kW / BTU
Cooling on Emergency Power | Yes / No / Verify
Condensate Risk | Low / Medium / High
UPS Installed | Yes / No / Verify
UPS Size | 5 kW
Sprinkler Modified | Yes / No / Verify
Detector/Strobe Installed | Yes / No / Verify
Extinguisher within 75 ft | Yes / No / Verify
Firestopping Complete | Yes / No / Verify
Access Control | Yes / No / Verify
CCTV | Yes / No / Verify
Open Risks | Notes
Owner Question | Notes
Photo Reference | Link/file
Status | Not Started / In Progress / Complete / Concern
9. Best Immediate Questions to Ask
For Building 62, I would ask:
1. Are B24A, 125, and 225 confirmed final TR locations?
2. Are the dedicated cooling units on emergency/backup power?
3. What is the designed cooling capacity for each TR?
4. Are condensate pumps required, and where do they discharge?
5. Are fire alarm devices coordinated with HVAC discharge?
6. Are sprinkler heads protected with cages in all TRs?
7. Is the extinguisher location identified within 75 feet of each TR?
8. Are all TR penetrations through rated assemblies shown and firestopped?
9. Is the future rack cooling/power load included or only current load?
10. What shutdowns are required for fire alarm, sprinkler, electrical, and telecom cutover?
Note on B82: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B91: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B103: Compare installed materials against approved submittals/spec sections.
Note on B112: Planned vs actual production supports delay/time-extension rebuttal.
Note on B120: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B70_TR_Assessment (hidden)
BUILDING 70 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 70 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 12:30 | Reviewer | Paul Thibodeau | Source Package | IFC B70 Drawings | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B27, 125A, 262A / TR Assessment
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Cooling / emergency power and existing TR phasing not verified
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Verify cooling power path, firestopping, extinguisher locations, and migration phasing
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
70 | B27 | Basement | Telecom Room / existing service area | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room B27; rack elevation references B-27 with 1 rack + future.
70 | 125A | First | Telecom Room / existing or renovated space | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room 125A; rack elevation references 125-A with 1 rack + future.
70 | 262A | Second | Telecom Room / existing or renovated space | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room 262A; rack elevation references 262-A with 1 rack + future.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B27 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
125A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
262A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B27 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
125A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
262A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B27 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
125A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
262A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B27 | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify
125A | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify
262A | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify
6. TELECOM
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B27 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
125A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
262A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify
7. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B70-R1 | All | Cooling emergency power / continuity not verified | High | Medium | 6 | Confirm power path for cooling, controls, BACnet adapter, and condensate pump | GCC / VA | Closed
B70-R2 | All | 1-hour rated/smoke-rated TR envelope and penetrations not field verified | High | Medium | 6 | Survey walls, doors, sleeves, trays, firestop, and head-of-wall conditions | GCC | Closed
B70-R3 | B27 | Existing basement service conditions may constrain routing and access | Medium | High | 6 | Document existing utilities, clearances, and phasing around active systems | GCC | Closed
B70-R4 | All | Existing TR/service equipment transfer could affect active operations | High | Medium | 6 | Require phasing plan and maintain analog/low-voltage systems operational | GCC / Contractor | Closed
B70-R5 | All | Condensate leak risk near IT equipment | High | Medium | 6 | Verify condensate routing, insulation, pump power, and alarms | GCC / Contractor | Closed
8. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B70-Q1 | Are cooling units and controls on emergency/backup power? | VA / Designer | Closed |  |  | Cannot confirm continuity of operations
B70-Q2 | Are future rack loads included in HVAC sizing for B27, 125A, and 262A? | Designer | Closed |  |  | Cooling may be undersized after expansion
B70-Q3 | Are extinguisher cabinet locations identified within 75 feet of each TR? | Contractor / COR | Closed |  |  | Acceptance / life safety risk
B70-Q4 | Are all wall/floor penetrations and speed sleeves shown and firestopped? | Contractor / Designer | Closed |  |  | Fire/smoke spread risk
B70-Q5 | What phasing is required to keep existing low-voltage/analog systems operational? | Contractor / OIT | Closed |  |  | Potential communications interruption
9. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B70-P001 | B27 | Existing Condition | Existing basement TR / utility condition |  | Paul |  | B70-R3 | Closed
B70-P002 | 125A | Existing Condition | Existing first-floor TR condition |  | Paul |  |  | Closed
B70-P003 | 262A | Existing Condition | Existing second-floor TR condition |  | Paul |  |  | Closed
B70-P004 | All | Firestop | Penetration/firestopping photo |  | Paul |  | B70-R2 | Closed
B70-P005 | All | HVAC | Cooling unit/condensate photo |  | Paul |  | B70-R1/B70-R5 | Closed
10. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B27 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow
125A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow
262A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
SOURCE / DRAWING REVIEW NOTES
Source package | 518-22-700.Bedford.EHRM.IFC.B70.20260316.pdf
TR locations identified | B27 basement, 125A first floor, 262A second floor based on architectural, fire protection, mechanical, and telecom drawing references.
Fire protection basis | Building 70 is fully sprinklered. TRs require sprinkler modifications, fire alarm devices, extinguisher coverage within 75 feet, and firestopping at penetrations.
HVAC basis | New indoor units, condensate routing, thermostat, and BACnet adapter are noted for TR spaces; emergency power and operational continuity should be field verified.
Telecom basis | TR rack elevations show 1 rack plus future rack at B-27, 125-A, and 262-A with UPS/PDU/cable management/grounding requirements.
Based on the Building 70 IFC review, the telecom scope is very similar to Building 62, but Building 70 appears to have three TRs (B27, 125A, and 262A) instead of a single room. The project introduces new racks, UPS equipment, dedicated cooling, fire alarm modifications, sprinkler modifications, grounding, cable management, and access control while maintaining hospital operations.
Building 70 – Telecom Room Infrastructure Scope
Existing Conditions Survey
Verify existing conditions of TR-B27, TR-125A, and TR-262A.
Document existing racks, power, HVAC, fire protection, grounding, and pathway systems.
Photograph all existing conditions.
Verify existing active services and identify systems requiring uninterrupted operation.
Verify room dimensions and equipment clearances.
Architectural
Prepare rooms for new telecom infrastructure.
Patch and repair walls, ceilings, and penetrations as required.
Maintain or restore all fire-rated assemblies.
Verify door hardware, access control, and room security.
Label rooms and equipment per VA standards.
Fire Protection
Verify sprinkler coverage within each TR.
Reconfigure sprinkler piping and heads where required.
Verify no obstructions to sprinkler discharge.
Provide fire extinguisher cabinet and clean-agent or CO₂ extinguisher within 75 feet of each TR.
Firestop all penetrations through rated assemblies.
Verify compliance with NFPA 13 and VA Fire Protection Design Manual requirements.
Fire Alarm
Verify smoke detection coverage.
Verify horn/strobe coverage.
Coordinate relocation or addition of devices as required.
Verify monitoring and reporting through existing fire alarm systems.
Test and document final operation.
Mechanical / HVAC
Verify dedicated cooling units serving each telecom room.
Verify thermostat installation.
Verify BACnet integration and controls.
Verify condensate routing and drainage.
Verify emergency power requirements for cooling equipment.
Verify continuous cooling capability during hospital operations.
Perform startup and commissioning.
Electrical
Verify new electrical distribution serving telecom equipment.
Verify dedicated panel assignments.
Verify UPS installation and ratings.
Verify rack power distribution units.
Verify emergency power source.
Verify grounding and bonding requirements.
Verify circuit identification and labeling.
Telecommunications
Install and/or verify new equipment racks.
Install vertical and horizontal cable management.
Install grounding busbars.
Install fiber termination shelves.
Install patch panels.
Verify Cat6A and fiber terminations.
Verify cable labeling.
Test and certify all copper and fiber cabling.
Verify compliance with OIT standards.
Security
Verify PACS access control for all TR doors.
Verify card reader operation.
Verify door position monitoring.
Verify camera coverage where required.
Verify integration with existing VA security systems.
Operational Risk Review
Identify systems requiring uninterrupted operation.
Develop cutover strategy.
Review outage requirements with VA OIT.
Review shutdown requirements with facilities staff.
Verify no active services are removed before migration.
Commissioning & Acceptance
HVAC commissioning.
Electrical commissioning.
Telecom testing and certification.
Fire alarm testing.
Fire protection testing.
Security testing.
Final owner acceptance walkthrough.
Turnover documentation.
Owner Risks Identified
High Risk
1. Cooling system failure after cutover.
2. Emergency power path not verified for cooling equipment.
3. Active communications disruption during migration.
4. Fire-rated penetrations left incomplete.
5. Condensate leaks above telecom equipment.
Medium Risk
1. Insufficient rack growth capacity.
2. Incomplete labeling.
3. Incomplete grounding and bonding.
4. Access control integration issues.
5. Existing undocumented field conditions.
Low Risk
1. Cosmetic room deficiencies.
2. Minor equipment relocation conflicts.
3. Documentation turnover delays.
Note on B86: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B95: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B107: Compare installed materials against approved submittals/spec sections.
Note on B116: Planned vs actual production supports delay/time-extension rebuttal.
Note on B124: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B78_Assessment (hidden)
BUILDING 78 / 78A │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 78 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 19:17 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 78_78A | Responsible Party | GCC / VA / Contractor | Rooms / Scope | B30 / B35 / 1232 / 227A / 342 / 401 / existing 15E, 1234, 353, 308A, 408A
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 78/78A is a very large full-scope TR building with basement through fourth-level telecom rooms, existing telecom rooms, hazardous abatement, architectural, fire protection, mechanical, electrical, security, telecom, rack elevations and photo references. Major open issues include active service cutover, dedicated HVAC validation, panel/UPS/PDU coordination, 4,849 ft cable tray routes, firestopping, PACS/CCTV, existing rack transfers, and turnover testing.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify rooms B30, B35, 1232, 227A, 342, 401 and existing telecom rooms 15E, 1234, 353, 308A, 408A; confirm active equipment, rack transfers, HVAC units, panel sources, UPS/PDU power, FEC locations, FA/FP modifications, PACS/CCTV, hazardous material impacts, cable tray routes, firestopping, and cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
78/78A | B30 | Basement | Basement telecom area / existing rack transfer | Telecom Room | 2 | 1 | Verify | 78_78AA-400 / 78_78AE-401 / 78_78AT-100 / 78_78AT-604 / 78_78AT-701 | Basement primary TR. Schedule identifies RM B30 with 210 WAO total, 23 active ports, 311 scheduled ports, 342 total ports with 10% allowance. Rack IDs include TR01-B30-1 and TR01-B30-2.
78/78A | B35 | Basement | Basement telecom area / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AT-100 / 78_78AT-605 / 78_78AT-702 | Basement TR/closet. Schedule identifies RM B35 with 53 WAO total, 23 active ports, 64 scheduled ports, 70 total ports with 10% allowance. Verify relationship to existing basement telecom room 15E photo reference.
78/78A | 1232 | First | First-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-401 / 78_78AE-402 / 78_78AT-101 / 78_78AT-606 / 78_78AT-702/703 | First-level TR. Schedule identifies RM 1232 with 301 WAO total, 388 active ports, 404 scheduled ports, 444 total ports with 10% allowance. Existing photo references show first-level existing telecom room 1234; verify room-name mapping.
78/78A | 227A | Second | Second-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-401 / 78_78AE-402 / 78_78AT-102 / 78_78AT-606 / 78_78AT-703/704 | Second-level TR. Schedule identifies RM 227A with 256 WAO total, 153 active ports, 348 scheduled ports, 383 total ports with 10% allowance. Existing photo references show second-level existing telecom room 1234; verify field room ID.
78/78A | 342 | Third | Third-level telecom room / existing rack transfer | Telecom Room | 2 | 1 | Verify | 78_78AA-402 / 78_78AE-403 / 78_78AT-103 / 78_78AT-607 / 78_78AT-704 | Third-level TR. Schedule identifies RM 342 with 158 WAO total, 163 active ports, 289 scheduled ports, 318 total ports with 10% allowance. Rack IDs include TR01-342-1 and TR01-342-2.
78/78A | 401 | Fourth | Fourth-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-402 / 78_78AE-404 / 78_78AT-104 / 78_78AT-607 / 78_78AT-705 | Fourth-level TR. Schedule identifies RM 401 with 89 WAO total, 65 active ports, 123 scheduled ports, 135 total ports with 10% allowance.
78/78A | 15E / 1234 / 353 / 308A / 408A | Existing levels | Existing telecom rooms / photo references | Existing telecom transition points | 5 | 0 | Verify | 78_78AR-900 / 901 / 902 / 903 | Photo references identify existing telecom rooms: basement 15E, first-level 1234, second-level 1234, third-level 353, fourth-level 308A and 408A. Protect active equipment and verify transfer/abandonment scope.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
B30 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify rated enclosure/open-to-deck conditions, door/PACS, future rack space, wall backing, ladder rack, and basement pathway entry points.
B35 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR/closet; verify existing conditions, rack transfer, floor/wall conditions, clearance, pathway and firestop scope.
1232 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify rated construction, door hardware/access, ceiling/deck, rack/future rack clearance, wall backing and pathway entries.
227A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR; verify rated construction, door hardware/access, rack/future rack clearance and vertical riser/firestop conditions.
342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Third-level TR; verify rack/future rack clearances, access control, firestopping and pathway routes.
401 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fourth-level TR; verify rack/future rack clearances, access control, firestopping and pathway routes.
Existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom rooms must be field verified for active equipment, protection-in-place and final abandonment/transfer condition.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
B30 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, and rated penetrations.
B35 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify FP/FA modifications, FEC location, temporary firestopping and final UL systems.
1232 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify first-level TR sprinkler/FA work, FEC location and cable tray penetrations.
227A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR sprinkler/FA work, FEC location, vertical riser penetrations and firestopping.
342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify third-level TR fire protection/fire alarm coordination and firestop work.
401 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify fourth-level TR fire protection/fire alarm coordination and firestop work.
Existing rooms | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing rooms remain protected during cutover and no unsealed penetrations remain.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
B30 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical sheets included for basement. Verify dedicated cooling equipment, capacity, condensate, emergency source, controls/BACnet and high-temperature alarm.
B35 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify dedicated cooling and relationship to B30/B35 telecom buildout.
1232 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify first-level TR cooling, controls, emergency power and alarm tie-in.
227A | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR cooling, condensate route and 24/7 operation.
342 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify third-level TR cooling and control/alarm integration.
401 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify fourth-level TR cooling and control/alarm integration.
Existing rooms | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom rooms likely have legacy cooling dependencies. Verify active equipment temperature and any protect-in-place cooling requirements.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
B30 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TRB30 panels / verify | Verify | Verify | Verify | Rack elevations identify new rack UPS/PDU and future rack. Verify panelboard/source, SPD, rack receptacles, PDU feeds, labels, load measurement and LOTO.
B35 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TRB35 panels / verify | Verify | Verify | Verify | Verify rack UPS/PDU source, spare/future rack provisions and grounding/bonding.
1232 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TR1232 panels / verify | Verify | Verify | Verify | Verify first-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling.
227A | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TR227A panels / verify | Verify | Verify | Verify | Verify second-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling.
342 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TR342 panels / verify | Verify | Verify | Verify | Verify third-level rack receptacles for two racks, UPS/PDU, panel sources and labels.
401 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TR401 panels / verify | Verify | Verify | Verify | Verify fourth-level rack receptacles, UPS/PDU, panel sources and labels.
Existing rooms | Existing / Verify | Existing UPS / PDU | Existing / Verify | Verify | Existing / verify | Verify | Verify | Verify | Existing rack elevations show wall-mounted racks/2-post racks, existing UPS/PDU and demarc/fiber equipment. Confirm active power and transfer needs.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
B30 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-701: 210 WAO total, 23 active ports, 311 scheduled ports, 342 with allowance; rack IDs TR01-B30-1/-2. Basement cable tray total 1,702 ft.
B35 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-702: 53 WAO total, 23 active ports, 64 scheduled ports, 70 with allowance. Confirm rack ID/room relation and active services.
1232 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-702/703: 301 WAO total, 388 active ports, 404 scheduled ports, 444 with allowance. Large active port count; high cutover risk.
227A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-703/704: 256 WAO total, 153 active ports, 348 scheduled ports, 383 with allowance. Verify second-level test records and riser labels.
342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-704: 158 WAO total, 163 active ports, 289 scheduled ports, 318 with allowance. Rack IDs TR01-342-1/-2.
401 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-705: 89 WAO total, 65 active ports, 123 scheduled ports, 135 with allowance.
Existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Photo references identify existing telecom rooms 15E, 1234, 353, 308A and 408A; verify all active services and transfer plan.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
B30 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | TR scope includes wall-mounted CCTV cameras and PACS for TR doors. Verify CR/RX/DC/ES/MD, controller and VMS integration.
B35 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify PACS/CCTV integration and door hardware coordination.
1232 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify first-level TR PACS/CCTV and VMS integration.
227A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR PACS/CCTV and VMS integration.
342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify third-level TR PACS/CCTV and VMS integration.
401 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify fourth-level TR PACS/CCTV and VMS integration.
Existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify existing PACS/security devices are protected-in-place or recabled without VMS/PACS disruption.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B78-R1 | All | Existing conditions and active equipment across six TRs and existing telecom rooms not field verified | High | Medium | 6 | Perform detailed room-by-room existing condition survey with photos and active-service inventory | GCC / Contractor | Closed | B78/78A has six major TR areas and several existing transition rooms.
B78-R2 | Basement / Third | Hazardous material abatement plans exist for basement and third level | High | Medium | 6 | Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or MEP installation | GC / IH / COR | Closed | Drawing index includes 78_78AH-100 and 78_78AH-103.
B78-R3 | Existing rooms | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, OIT windows, rack inventory, temporary utilities and rollback plan | Telecom / OIT | Closed | Photo references include 15E, 1234, 353, 308A, 408A.
B78-R4 | All TRs | Dedicated cooling sequence, emergency power, condensate and alarms not verified | Critical | Medium | 8 | Confirm HVAC equipment serving each TR, emergency source, condensate, controls/BACnet and high-temp alarms | Mechanical / Electrical | Closed | Mechanical sheets are included for basement through fourth level.
B78-R5 | All TRs | Panel source, UPS/PDU and rack receptacle coordination could delay energization | Critical | Medium | 8 | Verify telecom panelboards, breakers, rack receptacles, UPS/PDU sources, SPDs, labels and LOTO requirements | Electrical / GCC | Closed | Electrical plans/schedules are extensive; confirm all panel IDs in field.
B78-R6 | All | Large cable tray scope creates coordination and firestop risk | High | Medium | 6 | Verify 4,849 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 1,702 ft, first 959 ft, second 804 ft, third 695 ft, fourth 689 ft.
B78-R7 | All | Telecom/fiber cutover could affect active hospital communications across B78 and B78A | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | Total scheduled ports exceed 1,300 across the primary schedules.
B78-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope 102-sheet IFC package with multiple divisions.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B78-Q1 | Confirm final telecom room list and PMIS mapping: B30, B35, 1232, 227A, 342, 401 plus existing rooms 15E/1234/353/308A/408A? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B78-Q2 | What active services currently remain in each existing telecom room/photo reference location? | OIT / Contractor | Closed |  |  | Potential outage/cutover risk
B78-Q3 | Are Room 1232 and existing Room 1234 separate rooms or naming/mapping references for the same telecom space? | VA / Designer / OIT | Closed |  |  | PMIS mapping risk
B78-Q4 | Which dedicated cooling units serve each TR and are they on emergency/backup power? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B78-Q5 | Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? | GC / COR | Closed |  |  | Life-safety acceptance risk
B78-Q6 | Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B78-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and temporary firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B78-Q8 | Which third-party inspections, commissioning forms and OIT acceptance records are required before turnover? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B78-P001 | B30 | Existing Condition | Basement RM B30 walls, ceiling/deck, floor, door, racks/future rack, power, HVAC, cable tray and penetrations |  | Paul |  | B78-R1/B78-R6 | Closed
B78-P002 | B35 | Existing Condition | Basement RM B35 and relationship to existing telecom room 15E; rack/equipment, pathway, power, HVAC and penetrations |  | Paul |  | B78-R1/B78-R3 | Closed
B78-P003 | 1232 / 1234 | Existing Condition | First-level RM 1232/new TR and existing telecom room 1234 photo reference, active equipment, cable paths and rack transfer scope |  | Paul |  | B78-R1/B78-R3 | Closed
B78-P004 | 227A / 1234 | Existing Condition | Second-level RM 227A/new TR and existing telecom room 1234 photo reference, active equipment, cable paths and rack transfer scope |  | Paul |  | B78-R1/B78-R3 | Closed
B78-P005 | 342 / 353 | Existing Condition | Third-level RM 342/new TR and existing telecom room 353 photo reference, active equipment, cable paths and rack transfer scope |  | Paul |  | B78-R1/B78-R3 | Closed
B78-P006 | 401 / 308A / 408A | Existing Condition | Fourth-level RM 401 and existing telecom rooms 308A/408A photo references, active equipment, cable paths and transfer scope |  | Paul |  | B78-R1/B78-R3 | Closed
B78-P007 | All | Cable Tray / Firestop | Basement through fourth-level cable tray routes, supports, seismic bracing, penetrations and before/after firestopping |  | Paul |  | B78-R6 | Closed
B78-P008 | All | Telecom / Security / HVAC | Racks, Fiber LIU, Cat6A, patch panels, UPS/PDU, labels/test records, CCTV, PACS, HVAC units and existing transfer work |  | Paul |  | B78-R4/B78-R7/B78-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
B30 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR with 342 total ports including allowance, dedicated cooling, UPS/PDU and 1,702 ft basement cable tray scope.
B35 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Basement TR/closet with 70 total ports including allowance and active transition scope.
1232 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | First-level TR with 444 total ports including allowance and high active port count.
227A | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Second-level TR with 383 total ports including allowance and riser/firestop coordination.
342 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Third-level TR with 318 total ports including allowance and two-rack configuration.
401 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Fourth-level TR with 135 total ports including allowance and existing 308A/408A transition points.
Existing rooms | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing telecom room inventory; protect active services until cutover and acceptance complete.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B78_78A.20260316.pdf
Drawing Index | 102-sheet Building 78_78A IFC package includes general, hazardous abatement, architectural, interiors, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, fiber risers and photo references.
Architectural / Hazardous Basis | Drawing index includes 78_78AH-100 basement hazardous material abatement plan and 78_78AH-103 third-level hazardous material abatement plan, with architectural enlarged views 78_78AA-400/401/402 for basement through fourth levels.
Mechanical / FP Basis | Mechanical and fire protection packages are included for basement through fourth level. Verify dedicated cooling, condensate, controls, fire sprinkler modifications, FA devices and clean-agent FECs for each TR.
Electrical Basis | 78_78AE-401 through 404 and 78_78AE-701 through 704 provide enlarged electrical plans and schedules; verify telecom panelboard IDs, UPS/PDU rack circuits, SPDs, cooling equipment circuits, labels and load measurements.
Telecom Basis | 78_78AT-701 through 705 provide schedules: B30 210/23/311/342; B35 53/23/64/70; 1232 301/388/404/444; 227A 256/153/348/383; 342 158/163/289/318; 401 89/65/123/135. Cable tray totals 4,849 ft.
Existing Room / Photo Basis | 78_78AR-900 through 903 identify existing telecom rooms 15E, 1234 first/second level, 353, 308A and 408A. Field verify active services and relation to new TR room numbers.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
Note on B134: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B143: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B155: Compare installed materials against approved submittals/spec sections.
Note on B164: Planned vs actual production supports delay/time-extension rebuttal.
Note on B172: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B80_Assessment (hidden)
BUILDING 80 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 80 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-25 19:36 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 80 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 102 / existing 127A / existing 126 photo ref
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 80 includes a new first-level Telecom Room 102 and existing Tel Closet 127A / photo-reference Room 126 transition point. Field verification, active equipment transfer, dedicated cooling IU-1-01/CU-1-01, B80-TR102A/B power, 811 ft cable tray, firestopping, PACS/CCTV, existing two-post rack migration, and room-number mapping remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify Telecom Room 102 and existing 127A/126; confirm active services, existing rack/equipment transfer, B80-TR102A/B panel sources, IU-1-01/CU-1-01 cooling, fire alarm/sprinkler impacts, FEC location, PACS/CCTV scope, cable tray route, and telecom cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
80 | 102 | First | Telecom Room / new TR build area | Telecom Room | 1 | 1 | Verify | 80A-401 / 80E-101 / 80E-401 / 80T-101 / 80T-604 / 80T-701 | Primary Building 80 TR. Plans identify Telecom Room 102 at 140 SF, new Rack ID TR01-102-1 plus future rack, panels B80-TR102A/B, 5kW 208V UPS/PDU rack power, IU-1-01/CU-1-01 dedicated cooling, camera 102-CAM-1, and 215 total ports with 10% allowance.
80 | 127A / 126 | First | Existing Tel Closet / existing telecom room photo reference | Existing telecom transition point | 1 | 0 | Verify | 80T-101 / 80T-604 / 80R-900 | Existing Tel Closet 127A shown at 9 SF with existing plywood backboard, ground bar, patch panel, equipment box and two-post TR. Rack elevation/photo reference identify existing room 126/127-A with existing wall/wall-mount TE, Cisco switches, legacy optical Fiber LIU, multiple legacy Ortronics patch panels, Cat5e patch panel and APC floor UPS. Verify room-number mapping and active services.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, floor sealer, rack/future rack clearances, wall backing, cable tray and fiber path A/B entry points.
127A / 126 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing telecom closet/room; verify active equipment status, two-post rack/wall rack, backboard, UPS, patch panels, Fiber LIU, and transition/abandonment scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, and temporary firestopping during cable pulls.
127A / 126 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom closet/room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
102 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 102 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet interface, thermostat/control point, condensate pump/path, disconnects, and high-temperature alarm.
127A / 126 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom room/closet may remain active during cutover. Verify existing environmental condition and whether any active equipment remains after migration to Room 102.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
102 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B80-TR102A / B80-TR102B | Verify | Verify | Verify | Electrical plans/schedules identify B80-TR102A fed from BUS-B80-MDP and B80-TR102B fed from BUS-B80-E1, with rack receptacles, normal/emergency circuits, CU-1-01, SPD requirements and 30-day load measurement requirements.
127A / 126 | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 80T-701 identifies RM102 with 117 WAO total, 98 active ports per survey, 195 total ports per schedule, and 215 total ports with 10% allowance. Rack IDs include TR01-102-1 and TR01-102-2; rack elevation shows 1 new rack plus future rack with switches, Cat6A patch panels, Cat5e patch panel, Fiber LIU, UPS and PDU.
127A / 126 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing rack elevation shows Cisco switches, legacy optical Fiber LIU on wall, multiple legacy Ortronics 24/48-port patch panels, legacy Cat5e 24-port patch panel, and APC floor UPS. Contractor must transfer existing devices to new rack and protect active services.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical/telecom plans show access-control scope and camera 102-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, electric strike, camera/VMS integration, and door hardware coordination.
127A / 126 | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/PACS equipment conditions and whether any existing camera/security device is protected, recabled, or removed during cutover.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B80-R1 | All | Existing conditions for Room 102 and existing 127A/126 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B80 includes new TR plus existing telecom transition point.
B80-R2 | 127A / 126 | Existing telecom equipment may remain active during transfer to Room 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing and rollback plan | Telecom / OIT | Closed | Existing rack elevation shows Cisco switches, legacy patch panels, Fiber LIU and APC floor UPS.
B80-R3 | 102 / 127A | Room-number mismatch between Tel Closet 127A and photo/rack reference Room 126/127-A | High | Medium | 6 | Track both IDs in PMIS and confirm field room signage/owner mapping before punch list and turnover | GCC / VA / Designer | Closed | 80T-101 calls Tel Closet 127A; 80R-900 photo reference calls existing telecom room 126; 80T-604 lists room 126/127-A.
B80-R4 | 102 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness.
B80-R5 | 102 | B80-TR102A/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panel sources BUS-B80-MDP and BUS-B80-E1, breakers, receptacles, SPD, labels, load measurement and LOTO needs | Electrical / GCC | Closed | B80-TR102A/B panel schedules and one-line show normal/emergency source split.
B80-R6 | All | 811 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | 80T-701 cable tray schedule: basement 122 ft, first level 688 ft, grand total 811 ft.
B80-R7 | All | Telecom/fiber cutover could affect active hospital communications on first-level operations | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | RM102 supports 215 total ports including allowance and existing rack transfer.
B80-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope 52-sheet IFC package with mechanical, electrical, FP and telecom work.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B80-Q1 | Confirm final telecom scope: new Room 102 with existing 127A/126 transition only? | VA / OIT / Designer | Closed |  |  | Room inventory could miss scope
B80-Q2 | What active services are currently fed from existing Room 127A/126 equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B80-Q3 | Are Room 127A and Room 126 the same telecom room, or separate locations? | VA / Designer / OIT | Closed |  |  | PMIS mapping and turnover risk
B80-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B80-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 102? | GC / COR | Closed |  |  | Life-safety acceptance risk
B80-Q6 | Are B80-TR102A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B80-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed |  |  | Fire/smoke spread risk
B80-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B80-P001 | 102 | Existing Condition | Room 102 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, fiber path A/B, cable tray and penetrations |  | Paul |  | B80-R1/B80-R4 | Closed
B80-P002 | 127A / 126 | Existing Condition | Existing Tel Closet/telecom room with plywood backboard, ground bar, patch panel, equipment box, two-post rack/wall TE and cable entries |  | Paul |  | B80-R1/B80-R2 | Closed
B80-P003 | 127A / 126 | Existing Equipment | Cisco switches, legacy Fiber LIU, Ortronics patch panels, Cat5e patch panel, APC floor UPS and active service labels |  | Paul |  | B80-R2/B80-R3 | Closed
B80-P004 | 102 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B80-R4 | Closed
B80-P005 | 102 | Electrical | B80-TR102A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels |  | Paul |  | B80-R5 | Closed
B80-P006 | All | Cable Tray / Firestop | Basement and first-level cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping |  | Paul |  | B80-R6 | Closed
B80-P007 | 102 / 127A | Telecom | New rack/future rack, Fiber LIU, Cat6A, patch panels, labels/test records and existing rack transfer work |  | Paul |  | B80-R7 | Closed
B80-P008 | 102 | Security | 102-CAM-1, card reader, electric strike, door position, motion sensor, existing security devices and VMS/PACS integration |  | Paul |  | B80-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
102 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | New first-level TR with 215 total ports including allowance, dedicated cooling, UPS/PDU, cable tray, PACS/CCTV and fire/life-safety scope.
127A / 126 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Existing telecom transition point; protect active services until cutover complete and confirm room-number mapping.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B80.20260316.pdf
Drawing Index | 52-sheet Building 80 IFC package includes general, architectural, interiors, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, risers, cutsheets and photo reference.
Architectural Basis | 80A-400/401 identify enlarged views for Building 80 basement/first level and Telecom Room 102. 80G notes confirm no lead or asbestos material designed into project and general requirements for field verification and fire/life safety.
Mechanical Basis | 80M sheets include dedicated split-system cooling for Telecom Room 102 using IU-1-01 and CU-1-01 with BACnet control integration, condensate pump and FMS alarm/control requirements; verify emergency power and high-temp alarm in field.
Electrical Basis | 80E-101/401/601/701/702 identify B80-TR102A and B80-TR102B, rack receptacles, CU-1-01, SPD requirements, load measurement requirements, normal/emergency source paths from BUS-B80-MDP and BUS-B80-E1.
Telecom Basis | 80T-101 identifies Telecom Room 102 at 140 SF, existing Tel Closet 127A at 9 SF, fiber paths A/B, 10 new Cat6A cable legend and room 102 camera. 80T-604 identifies existing Room 126/127-A rack equipment and new Room 102 rack plus future rack. 80T-701 identifies 117 WAO, 98 active ports, 195 scheduled ports, 215 with 10% allowance and 811 ft total cable tray.
Photo Basis | 80R-900 identifies First Level Existing Telecom Room 126. Coordinate this photo reference with plan/rack labels for Tel Closet 127A / 126-127A.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B93: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B102: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B114: Compare installed materials against approved submittals/spec sections.
Note on B123: Planned vs actual production supports delay/time-extension rebuttal.
Note on B131: Final owner acceptance gate. These fields can feed PMIS_Data later.

## B82_Assessment (hidden)
BUILDING 82 │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | 82 | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-26 11:02 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC Building 82 | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 102 / existing B01-A / Telecom Enclosure
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Building 82 is identified as a Telecom Enclosure (TE) building on the cover sheet, with fire protection scope excluded, but mechanical sheets show IU-1-01/CU-1-01 dedicated cooling for Room 102 and electrical drawings show B82-MDP/B82-P-EMER power. Scope centers on new first-level Telecom Room 102 / 12RU enclosure and existing first-level Telecom Room B01-A transition point. Field verification, active-equipment transfer, 278 ft cable tray, firestopping, UPS/PDU power, HVAC controls, fiber/copper cutover, and room/equipment mapping remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Excluded / Firestop Only | Fire Alarm Status | Verify Existing
Security Status | Excluded / Verify Existing | Next Action | Field verify Room 102 new TE location, existing B01-A, active services, TR01-102-01 schedule, 278 ft cable tray route, 10 Cat6A cable legend, UPS/PDU source, B82-MDP/B82-P-EMER connections, IU-1-01/CU-1-01 cooling, fiber paths A/B, firestopping/sleeves, existing cameras and TE cutover plan.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
82 | 102 | First | Telecom Room / new TE location | Telecom Enclosure | 1 | 0 | Verify | 82A-401 / 82M-101 / 82E-101 / 82T-101 / 82T-604 / 82T-701 | Primary Building 82 TE. Plans identify Telecom Room 102 at 86 SF with new 12RU telecom enclosure, Rack ID TR01-102-01, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, IU-1-01/CU-1-01 cooling, and 40 total ports with 10% allowance.
82 | B01-A | First | Existing telecom room / wall rack and patch panels | Existing telecom transition point | 1 | 0 | Verify | 82T-101 / 82T-604 / 82R-900 | Existing first-level telecom room B01-A shown with existing wall rack, Cisco switches, cable management, Ortronics 24-port patch panels, APC floor UPS, and photo reference. Protect active services and verify transfer to Room 102 TE.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
102 | Verify | Verify | N/A / TE Room | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in Telecom Room 102; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, ceiling/deck conditions and that 86 SF is adequate for equipment maintenance.
B01-A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing telecom room; verify active equipment status, wall rack, UPS, patch panels, cable management, pathway, and transition/abandonment scope.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
102 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 82 receives a Telecom Enclosure and fire protection scope is excluded. Still verify rated penetrations, 4-inch sleeve, wall/floor openings, temporary firestopping, and life-safety device impacts.
B01-A | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing telecom room; verify protection-in-place and firestopping after cable transfer or reuse.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
102 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical and electrical drawings show IU-1-01 in/near Telecom Room 102 and CU-1-01 outdoor unit. Mechanical notes call for BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency/standby source, condensate pump/path, disconnects, controls, and high-temp alarm.
B01-A | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom room may remain active during cutover. Verify existing environmental conditions and whether active equipment remains after transfer to Room 102.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
102 | Verify | APC UPS / 12RU enclosure | Verify | Verify | B82-MDP / B82-P-EMER source to verify | Verify | Verify | Verify | Electrical plans/schedules identify TE receptacle, CU-1-01, B82-MDP and B82-P-EMER sources, with SPD devices integral to new telecom panelboards. Verify receptacle type, grounding/bonding, emergency source, labels, and circuit loading.
B01-A | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 82T-701 identifies RM102 with 26 WAO total, 31 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. Rack ID TR01-102-01. Cable tray schedule totals 278 ft on first level. New enclosure includes APC UPS, two PDUs, network switch, Cat6A patch panel and Fiber LIU.
B01-A | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B01-A elevations identify Cisco switches, cable management, two Ortronics 24-port patch panels with 11 and 6 used, existing patch panels and APC floor UPS. Field verify active services and transfer plan to new TE.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
102 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 82 appears to create a TE enclosure rather than a full TR door/PACS package. Verify existing cameras/security devices in Room 102 and ensure no camera angle or VMS integration is disrupted.
B01-A | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Keynotes indicate existing cameras are to be retained and re-used. Verify security/access conditions and whether any legacy security equipment is present at existing telecom room.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
B82-R1 | All | Existing conditions for new Room 102 TE and existing B01-A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B82 has a compact TE scope but still depends on field conditions and existing equipment transfer.
B82-R2 | 102 / B01-A | Existing equipment in B01-A may remain active during transfer to new TE in 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 82T-101 keynotes require phasing plan and transfer of existing devices to new rack/enclosure.
B82-R3 | 102 | Cover sheet says TE, but mechanical cooling is included for Room 102 | High | Medium | 6 | Confirm scope interpretation with VA/AE and ensure cooling is commissioned if it serves active TE equipment | GCC / VA / Designer | Closed | Unlike some TE buildings, B82 includes IU-1-01/CU-1-01 mechanical/electrical scope.
B82-R4 | 102 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling appears included and must be verified before acceptance.
B82-R5 | 102 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding, SPD and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs.
B82-R6 | All | 278 feet of first-level cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | 82T-701 cable tray schedule lists first level estimated length of 278 ft.
B82-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | Cover excludes fire protection; telecom notes require fire caulk and rated penetrations.
B82-R8 | All | Commissioning/test documentation may be overlooked due to TE-only scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification, HVAC startup/controls and owner signoff | GC / Cx Manager | Closed | General notes still require testing, acceptance and documentation.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
B82-Q1 | Confirm final scope: new 12RU wall-mount TE enclosure in Room 102 and existing B01-A transition only? | VA / OIT / Designer | Closed |  |  | Room inventory or PMIS mapping could miss scope
B82-Q2 | What active services are currently fed from existing B01-A equipment? | OIT / Contractor | Closed |  |  | Potential communications/security outage
B82-Q3 | Is Room 102 officially a TE-only scope or a conditioned telecom room with mechanical support? | VA / AE / COR | Closed |  |  | Scope and commissioning responsibility unclear
B82-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? | Mechanical / Electrical / VA | Closed |  |  | Cooling continuity unclear
B82-Q5 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
B82-Q6 | Are all 278 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed |  |  | Install delay or firestop gap
B82-Q7 | Are existing cameras/security devices protected and retained with no VMS/PACS disruption? | Security / OIT | Closed |  |  | Security continuity unclear
B82-Q8 | Which test records, HVAC startup records and turnover documents are required for TE acceptance? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
B82-P001 | 102 | Existing Condition | Room 102 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location |  | Paul |  | B82-R1/B82-R3 | Closed
B82-P002 | B01-A | Existing Condition | Existing first-level telecom room B01-A wall rack, Cisco switches, cable management, Ortronics patch panels, APC floor UPS and cable entries |  | Paul |  | B82-R1/B82-R2 | Closed
B82-P003 | 102 / B01-A | Pathway | 278 ft first-level cable tray route, 4-inch sleeve, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns |  | Paul |  | B82-R6/B82-R7 | Closed
B82-P004 | 102 | HVAC | IU-1-01/CU-1-01, condensate pump/path, thermostat, BACnet adapter, disconnects, high-temp alarm and power source |  | Paul |  | B82-R4 | Closed
B82-P005 | 102 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, B82-MDP/B82-P-EMER connections, grounding/bonding, SPD, labels and access |  | Paul |  | B82-R5 | Closed
B82-P006 | 102 / B01-A | Telecom | TR01-102-01 enclosure, cross-connect/cutover cabling, Fiber LIU, patch panels, labels, test results and existing equipment transfer |  | Paul |  | B82-R2/B82-R8 | Closed
B82-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos |  | Paul |  | B82-R7 | Closed
B82-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition |  | Paul |  | B82-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
102 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | New first-level TE/telecom room with 12RU wall enclosure, UPS/PDU, dedicated cooling shown, 278 ft cable tray and 40 total ports including allowance.
B01-A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | Existing first-level telecom room and transition point; protect active services until cutover complete.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B82.20260316(1).pdf
Drawing Index | 36-sheet Building 82 IFC package includes general, architectural, mechanical, electrical, telecommunications, rack elevations, schedules, fiber risers, cutsheets and photo references.
Scope Basis | Cover sheet note 4 states Building 82 is to receive a Telecom Enclosure (TE) and fire protection scope has been excluded. Mechanical drawings are included and show IU-1-01/CU-1-01 support.
Telecom Basis | 82T-101 identifies Telecom Room 102 at 86 SF, fiber paths A/B and new wall-mounted telecom enclosure. 82T-604 identifies existing B01-A rack/equipment and new Room 102 12RU TE enclosure. 82T-701 identifies Rack ID TR01-102-01, 26 WAO total, 31 active ports, 36 ports per schedule, 40 ports with 10% allowance and 278 ft first-level cable tray.
Existing Equipment Basis | 82T-604 existing B01-A elevations identify Cisco switches, cable management, Ortronics 24-port patch panels with 11 and 6 used, existing patch panels, and APC UPS floor. 82R-900 provides first-level existing telecom room B01A photo reference.
Mechanical Basis | 82M-101/701/801/802 identify IU-1-01 and CU-1-01 split-system cooling with BACnet adapter/control integration; verify power source, condensate, start-up and alarm points.
Electrical Basis | 82E-101/601/701 provide electrical plan, one-line and schedule references including B82-MDP, B82-P-EMER, TE receptacle, CU-1-01 and SPD requirements; verify power source, receptacle, grounding/bonding, circuit capacity and labels in field.
Operational Basis | General notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, testing/labeling/documentation, VA/OIT acceptance before active connections, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B93: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B102: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B114: Compare installed materials against approved submittals/spec sections.
Note on B123: Planned vs actual production supports delay/time-extension rebuttal.
Note on B131: Final owner acceptance gate. These fields can feed PMIS_Data later.

## BCH_Assessment (hidden)
CRESCENT HOUSE (BCH) │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | BCH | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-26 11:25 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC BCH / Crescent House | Responsible Party | GCC / VA / Contractor | Rooms / Scope | 107 / Room 00-107 / Telecom Enclosure / New Telecom Room
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Crescent House/BCH is a Telecom Enclosure (TE) scope with mechanical and fire protection excluded by the cover sheet. Scope centers on first-level Room 107 and rack/equipment location shown as Room 00-107 / BCH Crescent House. Field verification, room naming, wall-mounted TE versus 45RU room/rack elevation conflict, active-service cutover, power/UPS/PDU source, firestopping, fiber A/B routing, and cable tray/WAO quantities remain open.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Excluded / Firestop Only | Fire Alarm Status | Verify Existing
Security Status | Verify Existing | Next Action | Field verify Room 107, Room 00-107 rack/elevation reference, new TE/enclosure location, active services, cable tray route, power/UPS/PDU source, grounding/bonding, fiber Path A/B, 4-inch sleeve/firestop scope, camera/VMS scope, and confirm whether the BCH rack elevation is TE-only or new telecom room buildout.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
BCH | 107 | First | Existing Crescent House room area / telecom work area | Telecom Enclosure / Telecom Room | 1 | 0 | Verify | BCHGA-401 / BCHE-101 / BCHT-101 / BCHT-604 | Primary BCH telecom location. Architectural/electrical/telecom plans reference first-level Room 107. BCHT-101 enlarged plan identifies RM 107 new telecom work. BCHT-604 shows BCH Crescent House Room 107 as new telecom room / no existing elevations.
BCH | 00 / 107 | First | Rack/elevation reference location | Telecom Enclosure | 1 | 0 | Verify | BCHT-604 | Rack elevation shows 12RU telecom enclosure with APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and first-level mounting. Also includes separate BCH Crescent House Room 107 / new telecom room elevation; field confirm correct configuration.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
107 | Verify | Verify | N/A / TE Scope | Verify | Verify Existing | Verify | Verify | Verify | Verify wall backing, mounting height, access clearance, cable tray/sleeve entry, rated wall/firestop requirements, floor/ceiling conditions, ICRA barriers, and whether Room 107 functions as a TE-only space or a telecom room.
00 / 107 | Verify | Verify | N/A / TE Scope | Verify | Verify Existing | Verify | Verify | Verify | Rack elevation conflict requires field/AE confirmation before PMIS closeout. Confirm whether the 12RU wall enclosure or 45RU telecom room rack configuration is the governing installation.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
107 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states BCH receives a Telecom Enclosure and mechanical/fire protection scope has been excluded. Still verify existing life-safety protection, rated penetrations, 4-inch sleeve fire caulk, temporary firestopping and abandoned penetration patching.
00 / 107 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | TE-only scope does not appear to require new FEC/fire sprinkler work, but all wall/floor/ceiling penetrations must be sealed and rated assemblies maintained.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
107 | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Cover sheet explicitly excludes mechanical scope. Verify existing room ambient conditions are acceptable for TE equipment and that no active network equipment will overheat.
00 / 107 | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | If the final scope is a 45RU new telecom room rather than a small TE, HVAC exclusion should be confirmed with VA/AE because telecom-room heat load may differ from TE assumptions.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
107 | Verify | APC UPS / TE enclosure | Verify | Verify | BCHE-101 / BCHE-601 source to verify | Verify | Verify | Verify | Electrical plan includes first-level electrical work and notes for new wall-mount telecom enclosure, grounding/bonding and camera. Verify circuit source, receptacle type, UPS/PDU load, emergency source if required, grounding/bonding and labels.
00 / 107 | Verify | APC UPS / 12RU enclosure or 5kW rack UPS if room rack governs | Verify | Verify | Verify | Verify | Verify | Verify | BCHT-604 shows 12RU TE equipment with APC UPS and PDUs and also a BCH 45RU new telecom room elevation. Confirm exact UPS/PDU/rack power requirement before acceptance.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | BCHT-101 identifies telecom plan first level and enlarged Room 107. BCHT-604 identifies new telecom room/no existing elevations. There is no BCHT-701 schedule in the drawing index, so WAO/cable-tray totals must be field verified from plans and contractor coordination drawings.
00 / 107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | BCHT-604 identifies a 12RU TE elevation: APC UPS, two PDUs, network switch, 48-port Cat6A patch panel and Fiber LIU. Also shows BCH Crescent House Room 107 new telecom room elevation. Confirm governing rack/enclosure and labeling.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
107 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify | Verify | Verify | Verify | Telecom/electrical notes reference new IP-addressable camera with wall mount at 8'-6" A.F.F. and VMS integration. Verify whether PACS applies; TE buildings typically do not create full TR door/PACS scope.
00 / 107 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify | Verify | Verify | Verify | Verify existing camera/security conditions, protection-in-place, and any recabling or VMS integration required.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
BCH-R1 | All | Existing conditions for Crescent House Room 107 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | BCH is off-site at 15 Veterans Way, Lowell and requires careful field verification.
BCH-R2 | 107 | Mechanical and fire protection are excluded despite telecom/electronics installation | High | Medium | 6 | Verify existing environmental and life-safety conditions support TE equipment; confirm no dedicated HVAC/FP requirement applies | GCC / VA / AE | Closed | Cover sheet explicitly excludes mechanical and fire protection.
BCH-R3 | 107 / 00 | Rack/elevation conflict: TE 12RU enclosure versus BCH Room 107 new telecom room elevation | High | Medium | 6 | Submit RFI/confirm with AE which elevation governs and map room/equipment in PMIS | Telecom / Designer | Closed | BCHT-604 includes both TE enclosure and BCH 45RU new telecom room/no existing elevations.
BCH-R4 | 107 | Active services and existing devices may require phasing/temporary service | Critical | Medium | 8 | Document active services, maintain existing service, use phasing plan, temporary utilities and OIT cutover windows | Telecom / OIT | Closed | General telecom notes require transfer/phasing and avoiding shutdowns.
BCH-R5 | 107 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | Electrical sheets included but no full mechanical/FP package.
BCH-R6 | All | Cable tray, sleeve and pathway quantities not scheduled in a BCHT-701 sheet | High | Medium | 6 | Require coordination drawings showing route, supports, fill, penetrations, sleeves and cable counts | Telecom / GC | Closed | Drawing index does not list BCHT-701 telecom schedules.
BCH-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch sleeves, rated penetrations, fire caulk, temporary firestopping and patching even without FP scope | GC / Firestop | Closed | Telecom plan notes still require fire caulk and rated penetration protection.
BCH-R8 | All | Turnover documentation may be incomplete due to TE-only/off-site scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification and owner signoff | GC / Cx Manager | Closed | Commissioning/testing requirements still apply to impacted systems.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
BCH-Q1 | Confirm final BCH scope: Room 107 TE enclosure only, or a new telecom room/rack buildout? | VA / AE / OIT | Closed |  |  | PMIS scope and acceptance criteria unclear
BCH-Q2 | Why does BCHT-604 show a T78 12RU TE enclosure and a separate BCH Crescent House Room 107 new telecom room elevation? | VA / Designer | Closed |  |  | Rack/equipment mapping conflict
BCH-Q3 | What active services currently serve Crescent House and where are existing terminations located? | OIT / Contractor | Closed |  |  | Cutover/outage risk
BCH-Q4 | What is the approved power source, receptacle type and circuit capacity for the new UPS/PDU? | Electrical / Designer | Closed |  |  | Electrical readiness unknown
BCH-Q5 | Is existing HVAC/ambient condition acceptable for TE/network equipment since mechanical scope is excluded? | VA / OIT / Facilities | Closed |  |  | Heat/load risk
BCH-Q6 | Are cable tray route, sleeve locations, supports and firestopping details shown/field verified without a BCHT-701 schedule? | Telecom / GC / Firestop | Closed |  |  | Install delay or firestop gap
BCH-Q7 | Are camera/security devices required, protected and integrated into VMS for Room 107? | Security / OIT | Closed |  |  | Security continuity unclear
BCH-Q8 | Which test records and turnover documents are required for BCH TE/off-site acceptance? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
BCH-P001 | 107 | Existing Condition | Room 107 walls, ceiling, floor, wall backing, clearances, existing devices, power source, cable path, and proposed TE/rack location |  | Paul |  | BCH-R1/BCH-R3 | Closed
BCH-P002 | 107 | Electrical | Panel/source, receptacles, UPS/PDU location, grounding/bonding bar, labels and access clearance |  | Paul |  | BCH-R5 | Closed
BCH-P003 | 107 | Telecom | 12RU enclosure or rack location, Fiber LIU, patch panel, network switch, Cat6A terminations, labels and test records |  | Paul |  | BCH-R3/BCH-R8 | Closed
BCH-P004 | 107 | Pathway | Cable tray route, 4-inch sleeves, wall/floor penetrations, support points and 40% fill concerns |  | Paul |  | BCH-R6/BCH-R7 | Closed
BCH-P005 | 107 | Firestop | Rated penetrations, fire caulk and temporary/final firestopping before/after photos |  | Paul |  | BCH-R7 | Closed
BCH-P006 | 107 | HVAC / Existing Environment | Existing room cooling/ventilation and ambient condition for TE equipment |  | Paul |  | BCH-R2/BCH-R5 | Closed
BCH-P007 | 107 | Security / CCTV | Camera location, existing/security devices, VMS integration, access conditions and protection-in-place |  | Paul |  | BCH-R8 | Closed
BCH-P008 | All | Off-site Coordination | Site access, staging, ICRA/dust control, work area barriers and temporary service conditions |  | Paul |  | BCH-R1/BCH-R4 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
107 | 0.5 | 0.5 | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | BCH first-level Room 107 telecom scope; verify final TE versus telecom room configuration, power, pathway, firestopping and active service transition.
00 / 107 | 0.5 | 0.5 | N/A / Verify | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Rack/elevation reference requiring confirmation before turnover and PMIS import.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.BCH.20260316(1).pdf
Drawing Index | 26-sheet BCH/Crescent House IFC package includes general, architectural, electrical, telecommunications, fiber risers, rack elevations and telecom cutsheets. Mechanical and fire protection drawing packages are excluded for this building.
Scope Basis | BCHG-000 note 4 states this building is to receive a Telecom Enclosure (TE), and mechanical and fire protection scope has been excluded.
Architectural / Electrical Basis | BCHGA-401 and BCHE-101 identify first-level Room 107 work area and new condition. Electrical notes identify new wall-mount telecom enclosure, grounding/bonding, camera and coordination requirements.
Telecom Basis | BCHT-101 identifies first-level telecommunications plan and enlarged Room 107 new plan. BCHT-102 identifies second-level telecommunications plan. BCHT-604 identifies new TE enclosure/equipment plus BCH Crescent House Room 107 new telecom room/no existing elevations. No BCHT-701 schedule is listed in the index.
Riser Basis | BCHT-602/603A/603B show existing and new fiber riser diagrams. BCH appears as Crescent House / Room 107 in the new fiber riser relationship, with redundant fiber Path A/B requirements tied to the MCR strategy.
Operational Basis | General notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, testing/labeling/documentation, VA/OIT acceptance before active connections, and shutdowns limited one at a time.
Off-site Basis | Cover sheet identifies BCH/Crescent House project location at 15 Veterans Way, Lowell, MA 01852; include access/staging and off-site coordination in field review.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B94: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B103: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B115: Compare installed materials against approved submittals/spec sections.
Note on B124: Planned vs actual production supports delay/time-extension rebuttal.
Note on B132: Final owner acceptance gate. These fields can feed PMIS_Data later.

## MCR_Assessment (hidden)
MAIN COMPUTER ROOM (MCR) │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | MCR | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-26 11:39 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC MCR | Responsible Party | GCC / VA / Contractor | Rooms / Scope | New MCR Building / Room 107 / Room 031 / MDA / HDA A / HDA B / UPS A-B / Existing 137
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | MCR is the most critical EHRM infrastructure building. Scope includes new Main Computer Room, new MDA A/B rows, HDA A/B rows, existing server/MCR equipment transfer from 107/137, redundant fiber Path A/B, new CRAC cooling, UPS A/B, electrical service/ATS/generator integration, clean-agent fire suppression, wet sprinkler/fire alarm interfaces, PACS/CCTV, 359 ft cable tray, and MCR activation window. Major risk is service continuity during backbone/core migration and VA activation.
HVAC Status | Verify | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | Verify | Fire Alarm Status | Verify
Security Status | Verify | Next Action | Field verify new MCR Room 107 / Room 031 naming, MDA-A/B and HDA-A/B rack rows, existing MCR/server equipment in 107/137, UPS-A/B, CRAC units, clean-agent/preaction/fire alarm systems, MCR panel/ATS/generator sources, camera/access control devices, fiber Path A/B, service provider entrance, cable tray/firestop scope, third-party inspections, and phased activation/cutover sequence.
1. ROOM INVENTORY
Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes
MCR | 107 / MCR | Ground | New Main Computer Room / MCR building | Main Computer Room | 12 | 0 | Verify | MCRA-101 / MCRT-100 / MCRT-101 / MCRT-401 / MCRT-607-609 / MCRT-701 | Primary new MCR space. Telecom plans show MDA-A1/A2/A3, MDA-B1/B2/B3, HDA-A, HDA-B, UPS-A and UPS-B. Rack elevations identify MDA A/B racks, HDA A/B server cabinets, existing server cabinet transfer references, 10 WAO total and 359 ft cable tray.
MCR | 031 / Fiber Entrance Room 1 | Ground | Fiber entrance / telecom pathway space | Fiber Entrance / support room | 1 | 0 | Verify | MCRT-401 / MCRT-701 | MCRT-701 schedule is titled Data Device and Circuit Schedule - Fiber Entrance Room 1 and identifies Rack ID TR01-031-1, four data outlets 31-A/B/C/D and security camera/data devices 07-CAM-03/04/07/08/11.
MCR | MDA-A1/A2/A3 | Ground | New MDA row A | Main Distribution Area A | 3 | 0 | Verify | MCRT-607 | New MDA A racks: MDA-A-1, MDA-A-2, MDA-A-3. MDA A-2 includes 1RU LIU for hybrid FOC to HDA and 48x Cat6A to HDA. MDA A-1/A-3 reserved for LAN elements/leaf/access or spine/aggregation.
MCR | MDA-B1/B2/B3 | Ground | New MDA row B | Main Distribution Area B | 3 | 0 | Verify | MCRT-607 | New MDA B racks: MDA-B-1, MDA-B-2, MDA-B-3. MDA B-2 includes 1RU LIU for hybrid FOC to HDA and 48x Cat6A to HDA. Supports redundant B-side backbone/distribution.
MCR | HDA-A | Ground | New HDA A row | Horizontal Distribution Area A | 1 | 0 | Verify | MCRT-608 | HDA A-1 new server cabinet front/rear elevation, 48-port Cat6A patch panels, HD fiber LIUs, HD Cat6A patch panel to MDA-A2, and backbone side A/B LIU. Also includes existing B61 server cabinet transfer references.
MCR | HDA-B | Ground | New HDA B row | Horizontal Distribution Area B | 1 | 0 | Verify | MCRT-609 | HDA B-1 new server cabinet front/rear elevation, 48-port Cat6A patch panels, HD fiber LIUs, HD Cat6A patch panel to MDA-B2, and duplicate existing B61 server cabinet transfer references.
MCR | Existing 107 / 137 Server MCR | Existing / transition | Existing MCR/server/core equipment | Existing equipment transition point | 20 | 0 | Verify | MCRT-604 / MCRT-605 / MCRT-606 / MCRT-608 / MCRT-609 | Existing MCR elevations include Rows 1-3 and existing server cabinet B61 equipment, Cisco core, WAN aggregation, NetScout, Canoga Perkins, Cisco switches, legacy Ortronics patch panels, LIUs, APC/Chatsworth/HP PDUs and UPS equipment. Protect and phase transfer.
2. ROOM READINESS
Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments
107 / MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New MCR building requires final architectural envelope, rated walls/doors, roof/ceiling, floor finish, equipment clearances, row spacing, lighting coordination, grounding/bonding, and path separation.
031 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fiber Entrance Room 1 schedule requires confirmation of room naming, wall/backbox locations, penetration/firestop detail, rack/cabinet location and service provider interface.
MDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MDA racks must be installed with mandatory blank panels, bonding, overhead tray, fiber/copper routing and A/B side path separation.
HDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | HDA server cabinets require front/rear access, blanking panels, cooling airflow coordination, patch panel/LIU arrangement and clearance for future expansion.
Existing 107/137 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing equipment rooms/racks must remain operational until cutover. Verify active equipment inventory, PDUs, UPS sources, cable labels, and safe transfer pathway.
3. FIRE PROTECTION
Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes
107 / MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCR has full fire protection scope including wet pipe and clean-agent fire suppression system. Verify preaction/clean-agent design, agent release interface, fire alarm matrix, detection, abort/release stations, room integrity and acceptance testing.
031 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Verify fiber entrance room protection, rated penetrations, firestopping, detector/strobe coverage and no gaps after cable tray installation.
MDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify sprinkler/clean-agent coverage around MDA equipment, fire alarm devices, rack clearance and final firestop assemblies.
HDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify clean-agent coverage, detector placement, alarm interfaces, and open cabinet airflow protection.
Existing 107/137 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing systems must remain protected during temporary fiber, umbilical cord and core relocation work. Verify no impairment without approved fire watch/impairment plan.
4. HVAC / COOLING
Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes
107 / MCR | CRAC units / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom notes call for indoor computer room air conditioner (CRAC) units tied to building management system. Mechanical sheets included; verify redundant capacity, setpoints, humidity, condensate, controls, alarms and emergency power.
UPS-A / UPS-B | Dedicated cooling / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | UPS rooms/equipment require thermal load validation, ventilation, emergency power and alarm integration. Verify battery/UPS environmental requirements.
MDA-A/B | CRAC-served MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify airflow/cold aisle/hot aisle assumptions, blanking panels, floor/ceiling distribution and temperature monitoring.
HDA-A/B | CRAC-served MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Server cabinets and patch fields require stable 24/7 cooling and monitoring. Confirm no local hot spots at dense LIU/patch panel zones.
Existing 107/137 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | During split-core temporary phase, existing MCR/server equipment remains active. Verify existing cooling remains in service until cutover and decommissioning are complete.
5. ELECTRICAL / UPS
Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes
107 / MCR | UPS-A / UPS-B | Verify | Verify | Verify | MCRE-401/402/403/601/701/702 | Verify | Verify | Verify | Electrical set includes site plan, enlarged MCR plans, one-lines and schedules. Verify switchboard/service, ATS/generator integration, normal/emergency/UPS distribution, grounding, lightning protection, SPD, load measurements and commissioning.
MDA-A/B | Verify | Rack/PDU dependent | Verify | Verify | MCR telecom panels / verify | Verify | Verify | Verify | MDA rack elevations include new 4-post floor cabinets, LIUs and network elements. Verify redundant A/B power feeds and PDU arrangements.
HDA-A/B | Verify | Cabinet/PDU dependent | Verify | Verify | MCR telecom/UPS panels / verify | Verify | Verify | Verify | HDA cabinets include server cabinet front/rear elevations with patch panels and active equipment. Confirm A/B feed separation, PDU mounting, load capacity and labels.
Existing 107/137 | Existing / Verify | Existing rack UPS/PDU | Existing / Verify | Verify | Existing / verify | Verify | Verify | Verify | Existing rack elevations identify multiple APC/Chatsworth/HP PDUs, APC Smart UPS and Eaton 9PX units. Verify what transfers, what stays, and temporary power during migration.
Site / Utility | Verify | N/A | N/A | N/A | MCRES / MCRE site one-line | Verify | Verify | Verify | New MCR is standalone critical infrastructure. Verify utility service, generator/ATS paths, emergency distribution, grounding electrode and ductbank/site electrical coordination.
6. TELECOMMUNICATIONS
Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes
107 / MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-101 shows new MCR with MDA-A/B, HDA-A/B, UPS-A/B, cameras and fiber path legend. MCRT-701 shows 10 WAO total, 720 WAO available, 98.1% expansion capacity, 10 total ports with 20% allowance and 359 ft cable tray.
031 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-701 Data Device and Circuit Schedule - Fiber Entrance Room 1: outlets 31-A/B/C/D plus security devices 07-CAM-03/04/07/08/11; Rack ID TR01-031-1.
MDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-607: MDA A/B racks contain horizontal distribution LIUs, hybrid FOC, 48x Cat6A to HDA, and reserved LAN/spine/aggregation elements. Maintain A/B path separation.
HDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-608/609: HDA A/B include 48-port Cat6A patch panels, HD fiber LIUs, backbone side A/B LIU and server cabinet arrangements.
Existing 107/137 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing MCR rows 1-3 and B61 server cabinet transfer references are extensive. Maintain service using temporary fiber/umbilical cords and phased core relocation.
7. SECURITY / PACS / CCTV
Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes
107 / MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-101 identifies cameras 07-CAM-01 through 07-CAM-12 around the MCR. Telecom notes call for IP-addressable network cameras integrated into existing VMS and PACS/access-control systems including iSTAR Edge/Avigilon ACM controller.
031 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-701 includes security camera/data devices assigned to TR01-031-1. Confirm camera IDs, mounting, cabling, and VMS commissioning.
MDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify camera coverage, door/access points, VMS monitoring and access control zones for critical equipment.
HDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify coverage of HDA cabinets, doors, motion detection and any lockable cabinet/security requirements.
Existing 107/137 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Existing security systems must remain functional during transition; protect existing camera angles and access controls until final turnover.
8. OWNER RISKS
Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
MCR-R1 | All | MCR is a new standalone critical facility with 120-sheet multi-discipline scope | Critical | Medium | 8 | Use discipline-by-discipline pre-install checklist, coordination drawings, third-party inspections and commissioning tracker | GCC / VA / Cx | Closed | New MCR cannot depend on another project or funding source to be usable.
MCR-R2 | Existing 107/137 | Existing MCR/server/core equipment transfer may interrupt hospital network operations | Critical | Medium | 8 | Require detailed OIT cutover plan, temporary fiber/umbilicals, rollback plan, VA activation windows and after-hours phasing | OIT / Telecom | Closed | Notes state MCR activation may need 3-6 months and WAO activation depends on fiber/core connections.
MCR-R3 | MDA/HDA | A/B fiber path diversity and backbone commissioning not verified | Critical | Medium | 8 | Verify OSP/ISP Path A/B routing, no intermediate splices, test results, labeling and geographic diversity | Telecom / OIT | Closed | New fiber risers require A-side and B-side redundant paths to every TR.
MCR-R4 | MCR / UPS | UPS-A/B, ATS/generator, panel source and PDU coordination could delay activation | Critical | Medium | 8 | Verify one-line, load banks, breaker settings, panel labels, generator/ATS tests, UPS start-up and A/B power mapping | Electrical / Cx | Closed | Electrical scope includes site electrical, enlarged MCR plans, one-lines and schedules.
MCR-R5 | MCR | CRAC capacity, redundancy, condensate, BMS/FMS alarms and emergency power not verified | Critical | Medium | 8 | Confirm mechanical schedules, CRAC start-up, controls, alarm points, emergency source, environmental monitoring and hot/cold aisle performance | Mechanical / Cx | Closed | Telecom notes explicitly call for indoor computer room air conditioner CRAC units and BMS coordination.
MCR-R6 | MCR | Clean-agent/preaction/fire alarm interface and room integrity acceptance risk | Critical | Medium | 8 | Track clean-agent calculations, room integrity test, release/abort stations, FA matrix, sprinkler/preaction tests and AHJ/third-party acceptance | FP / FA / Cx | Closed | MCR receives new fire alarm and clean-agent fire suppression system.
MCR-R7 | MCR / Site | Civil/site/utility ductbank, drainage, grading and security envelope could affect substantial completion | High | Medium | 6 | Track civil utility plan, stormwater, grading, ductbank, site fiber conduit encasement, access and landscape/hardscape restoration | Civil / Site / GC | Closed | MCR package includes civil, structural and architectural site work.
MCR-R8 | All | Commissioning/turnover package may be incomplete across all divisions | High | Medium | 6 | Maintain MCR-specific turnover matrix for electrical, mechanical, FP, FA, telecom, security, civil, structural and architectural systems | GC / Cx Manager | Closed | General notes require commissioning/recommissioning, third-party inspections and written reports.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
MCR-Q1 | Confirm final room naming and PMIS mapping: MCR Room 107, Fiber Entrance Room 031, Existing 107/137 server/MCR references. | VA / OIT / Designer | Closed |  |  | Room inventory and turnover mapping could be wrong
MCR-Q2 | What existing core/server/rack equipment is being relocated from the existing MCR/server rooms, and what remains? | OIT / Contractor | Closed |  |  | Cutover and outage risk
MCR-Q3 | What is the approved MCR activation sequence and required VA/OIT hold points? | VA / OIT / COR | Closed |  |  | Schedule/cutover impact |  |  | General phasing notes mention 3-6 month MCR activation and split core operation.
MCR-Q4 | Are UPS-A/B, generator/ATS and emergency power paths commissioned and mapped to each rack/PDU? | Electrical / Cx | Closed |  |  | Electrical readiness unknown
MCR-Q5 | Are CRAC units fully commissioned with BMS/FMS alarms, redundancy and emergency power? | Mechanical / Cx | Closed |  |  | Cooling continuity risk
MCR-Q6 | Are clean-agent/preaction/fire alarm systems fully designed, tested and accepted? | FP / FA / AHJ | Closed |  |  | Life-safety acceptance risk
MCR-Q7 | Are redundant Path A/B fiber routes geographically diverse, tested, labeled and accepted? | Telecom / OIT | Closed |  |  | Backbone redundancy risk
MCR-Q8 | Which third-party inspections, commissioning reports and OIT validation records are required before turnover/activation? | GC / Cx Manager / OIT | Closed |  |  | Turnover package gap
10. PHOTO LOG
Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
MCR-P001 | MCR 107 | Existing / New Condition | Full room envelope, doors, rated walls, ceiling/roof, floors, row layout, UPS-A/B, MDA/HDA, access points and cameras |  | Paul |  | MCR-R1/MCR-R6 | Closed
MCR-P002 | 031 | Fiber Entrance | Fiber Entrance Room 1, outlet locations 31-A/B/C/D, rack/cabinet location, sleeve/firestop and service entrance pathways |  | Paul |  | MCR-R3 | Closed
MCR-P003 | MDA-A/B | Rack / Fiber | MDA-A1/A2/A3 and MDA-B1/B2/B3 rack fronts/rears, LIUs, hybrid FOC, Cat6A to HDA, grounding and cable management |  | Paul |  | MCR-R3/MCR-R4 | Closed
MCR-P004 | HDA-A/B | Rack / Server Cabinets | HDA-A1/HDA-B1 front/rear, patch panels, HD LIUs, cabinet blanking panels, server cabinet airflow and labels |  | Paul |  | MCR-R3/MCR-R5 | Closed
MCR-P005 | Existing 107/137 | Existing Equipment | Existing rows 1-3 and B61 server cabinet transfer equipment, Cisco core, WAN aggregation, NetScout, Canoga, Ortronics, LIUs, UPS/PDU labels |  | Paul |  | MCR-R2 | Closed
MCR-P006 | MCR / Electrical | Electrical / UPS | UPS-A/B, switchboards, panels, ATS, generator tie, PDUs, rack receptacles, grounding, SPDs and load measurement labels |  | Paul |  | MCR-R4 | Closed
MCR-P007 | MCR / Mechanical | HVAC / Controls | CRAC units, condensate, controls/BACnet/BMS/FMS points, alarms, environmental monitoring and emergency power source |  | Paul |  | MCR-R5 | Closed
MCR-P008 | MCR / Life Safety | Fire / Security | Clean-agent cylinders/piping/nozzles, preaction/sprinkler, fire alarm, release/abort devices, cameras 07-CAM series, PACS/controller and door hardware |  | Paul |  | MCR-R6/MCR-R8 | Closed
11. OWNER READINESS SCORE
Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes
107 / MCR | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New critical MCR facility with full architectural/civil/structural/MEP/FP/telecom/security scope; not construction-ready until coordination and commissioning plan are verified.
031 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Fiber Entrance Room 1 schedule and camera/data points require field verification and firestop/pathway coordination.
MDA-A/B | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New main distribution rows; A/B fiber diversity and rack/PDU mapping are critical.
HDA-A/B | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | New horizontal distribution/server cabinet rows; airflow, patching, labeling and redundancy must be validated.
Existing 107/137 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Existing MCR/server equipment transition point; protect active service until final activation.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.MCR.20260316.pdf
Drawing Index | 120-sheet MCR IFC package includes general, life safety, civil, structural, architectural, interiors, equipment, fire protection, plumbing, mechanical, electrical, telecommunications, rack elevations, telecom schedules and cutsheets.
Scope Basis | Cover sheet identifies the New Main Computer Room Building as a project scope item with new MCR, temporary and new fiber, new HVAC, CCTV, fire protection/fire alarm, PACS, UPS, electrical distribution and commissioning.
Telecom Basis | MCRT-101/401 show new MCR layout with UPS-A, UPS-B, HDA-A, HDA-B and MDA-A1/A2/A3/B1/B2/B3. MCRT-607 through 609 identify MDA/HDA rack elevations. MCRT-701 identifies Fiber Entrance Room 1, 10 WAO total, 720 WAO available, 98.1% expansion capacity and 359 ft cable tray.
Existing Equipment Basis | MCRT-604 through MCRT-606 identify existing MCR Rows 1-3 with existing rack/PDU/UPS/server/core equipment. MCRT-608/609 include existing B61 server cabinet transfer/duplicate references tied to 137/107 Server MCR.
Fiber / Phasing Basis | MCRT-601/603A/603B describe temporary fiber, MCR activation, A/B redundant fiber routes, no intermediate fiber splices, new MCR umbilical cords, and VA activation windows. WAO activation depends on new fiber and core connection.
Mechanical / FP Basis | MCRM sheets include MCR mechanical/CRAC and controls scope; MCRFX sheets include clean-agent and fire protection plans/details. Fire alarm notes require clean-agent system interface with building fire alarm.
Electrical / Security Basis | MCRE sheets include site electrical, MCR electrical plans, one-line diagrams and schedules. MCRT notes call for IP cameras integrated to VMS and PACS/access-control devices/controllers for secured spaces.
Operational Basis | General notes require third-party inspections, testing, written reports, commissioning/recommissioning, coordination drawings, VA/OIT acceptance before active connection, and shutdowns limited one at a time.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B120: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B129: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B141: Compare installed materials against approved submittals/spec sections.
Note on B150: Planned vs actual production supports delay/time-extension rebuttal.
Note on B158: Final owner acceptance gate. These fields can feed PMIS_Data later.

## SITE_Assesment (hidden)
SITE │ EHRM ASSESSMENT │ PMIS DASHBOARD FEED
Building | SITE | Building Phase | Drawing Review | Overall Status | Yellow | Readiness | 50% | Construction Ready | No
Review Date | 2026-06-26 11:56 | Reviewer | Paul Thibodeau | Source Package | 518-22-700 IFC SITE | Responsible Party | GCC / VA / Contractor | Rooms / Scope | Campus fiber Path A/B / ductbank / handholes / manholes / MCR connectivity
Open Risks | 0 | Open Questions | 0 | Shutdowns | 0 | Major Blocker | Site package controls the redundant telecommunications backbone for the full EHRM campus. Scope includes site survey, electrical site plans, telecom site plans, enlarged views, plan/profile sheets for Path A/B, concrete ductbank, direct-bury conduit, handholes THH #1-#19, communication manholes with locking covers, concrete pullboxes, trench restoration, and the site one-line fiber diagram. Major risks are existing utility conflicts, A/B path separation, ductbank inspection before backfill, MCR activation sequencing, and coordination of multiple building tie-ins.
HVAC Status | N/A | Electrical Status | Verify | Telecom Status | Verify | Fire Protection Status | N/A / Maintain Access | Fire Alarm Status | N/A
Security Status | Verify Site Access | Next Action | Field verify all THH/manhole locations, utility depths, trench routes, concrete ductbank sizes, Path A/B conduit counts, building tie-in points, site electrical conflicts, MCR/provider entrance points, restoration limits, traffic/pedestrian controls, inspection hold points, and fiber testing/acceptance sequence.
1. SITE ROUTE INVENTORY
Area / Segment | Buildings / Nodes | Path | Primary Scope | Handholes / Structures | Conduit / Ductbank | Status | Drawing Ref | Station / Length | Notes
Overall Site | Campus-wide / MCR / all EHRM buildings | Path A & B | Redundant site fiber backbone | THH #1-#19, communication manholes, concrete pullboxes | 4-inch PVC conduit in concrete ductbank; direct-bury communication conduit where noted | Verify | TS100 / T-601 / G-000 | Campus wide | New site fiber conduit must be concrete encased. Base bid is trenching with concrete ductbank and hand digging at existing utility crossings; directional boring requires Government approval.
B12 to B16 | B12 / B16 | Path A & B | Telecom plan and profile | THH #15-#19 | 2x4-inch PVC concrete ductbank | Verify | TS201 | 00+00 to 7+91.21 | Plan/profile shows B12 to B16 route with vertical ductbank angle transitions and concrete ductbank notes.
B1 to B70 | B1 / B70 backbone segment | Path A & B | Telecom plan and profile | THH #1-#7 plus pullbox | 2x4-inch and 4x4-inch PVC concrete ductbank | Verify | TS202 / TS203 / TS207 | 00+00 to 15+92.04 | Long backbone route with multiple THHs, concrete pullbox, and B70/B81 branches. Confirm all utility crossings and trench restoration limits.
B20 / B22 | B20 / B22 | Path A & B | Telecom plan and profile | THH #2, #8-#12 | 2x4-inch PVC concrete ductbank | Verify | TS204 | B20 00+00 to 7+34.47; B22 00+00 to 1+98.18 | Route feeds Building 20 and 22. Confirm common ductbank has separate conduits for A/B path where shown.
B15 / B9 | B15 / B9 | Path A & B | Telecom plan and profile | THH #14-#18 | 2x4-inch PVC concrete ductbank | Verify | TS205 | B15 00+00 to 1+70.82; B9 00+00 to 2+01.32 | Route includes ductbank transitions and utility verification requirements.
B13 / B14 | B13 / B14 | Path A & B | Telecom plan and profile | THH #15-#17 | 2x4-inch PVC concrete ductbank | Verify | TS206 | B13 00+00 to 1+67.85; B14 00+00 to 1+79.01 | Coordinate with nearby B12/B16/B15 infrastructure and handhole locations.
B70 / B81 | B70 / B81 | Path A & B | Telecom plan and profile | THH #7 / #14 | 2x4-inch PVC concrete ductbank | Verify | TS207 | B70 15+52.38 to 15+92.04; B81 00+00 to 1+49.54 | B70/B81 extension from B1-B70 backbone; verify west-campus access and restoration.
B33 / B17 | B33 / B17 | B33 Path A & B / B17 Path A | Telecom plan and profile | THH #8, #10, #13 | 2x4-inch PVC concrete ductbank | Verify | TS208 | B33 00+00 to 0+78.16; B17 00+00 to 1+16.82 | B17 Path A only on this sheet; Path B appears on TS210. Ensure PMIS tracks both A and B legs.
B18 / B19 | B18 / B19 | B18 Path A / B19 Path A & B | Telecom plan and profile | THH #9 / #10 | 2x4-inch PVC concrete ductbank | Verify | TS209 | B18 00+00 to 0+36.94; B19 00+00 to 0+42.25 | B18 Path A only on this sheet; Path B appears on TS210. Verify B19 A/B separation and building penetration.
B81 / B17 to B01 / B18 | B81 / B17 / B01 / B18 | Path B | Telecom plan and profile | THH #7 / #13 | 2x4-inch PVC concrete ductbank | Verify | TS210 | B17 to B01 00+00 to 1+63.50; B18 00+00 to 0+87.25 | Completes B-path routing for B17 and B18 and B81/B17-to-B01 interconnection. Critical for redundancy verification.
2. SITE READINESS
Scope Area | Survey / Layout | Utility Locate | Access / Traffic | Excavation Permit | Ductbank Forms | Inspection Hold | Restoration | Overall | Comments
Campus Backbone | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Survey notes state utility locations are approximate and conditions may vary; contractor must provide utility location service before excavation and verify location/depth of all utilities.
THH / Manholes | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Field verify THH #1-#19, communication manholes, existing manholes, locking covers, drainage, elevations and pull radius before ductbank install.
Concrete Ductbank | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Trench must remain open until inspection of concrete duct. Confirm conduit quantity per T-601 and ductbank size/detail per T-501.
Building Tie-ins | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Each building sheet T-101 and T-601 riser diagram are continuation references. Confirm sleeve/penetration, firestop, patching and building downtime coordination.
Restoration / Site | Verify | Verify | Verify | Verify | N/A | Verify | Verify | Verify | Restore trench/sidewalk/asphalt/landscape to match existing. Maintain fire lanes, hydrants, access and pedestrian controls.
3. FIRE / LIFE SAFETY / SITE ACCESS
Area | Fire Lane | Hydrants / FDC | Egress | Temp Barriers | Hot Work | Impairment | Fire Watch | Overall | Risk / Notes
Campus Work Areas | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | General notes require fire lanes, hydrants and fire department access roads operational at all times; maintain egress and provide fire watch/temporary protection when required.
Trenching / Excavation | Verify | Verify | Verify | Verify | N/A | N/A | Verify | Verify | Trench barricades, accessible parking/public access and right-of-way impacts must be coordinated with owner prior to construction.
Building Penetrations | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Rated wall/floor penetrations must be firestopped; temporary firestopping required if penetrations remain open between shifts.
MCR / Critical Backbone | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Backbone work affects facility operations. Any required shutdowns must be limited to one at a time and coordinated with approved phasing plan.
4. CIVIL / DUCTBANK / RESTORATION
Segment | Excavation Method | Ductbank Type | Concrete / Backfill | Structures | Profile Verified | Restoration | Testing / Inspection | Overall | Risk / Notes
All New Site Fiber | Trenching base bid | Concrete encased conduit | Verify | THH / manholes / pullboxes | Verify | Verify | Verify | Verify | General notes require all utilities installed with this project to be in concrete ductbank; directional boring must be approved by Government.
B1-B70 Backbone | Trench / hand dig at crossings | 2x4 and 4x4 PVC ductbank | Verify | THH #1-#7 / pullbox | Verify | Verify | Verify | Verify | Longest route and highest exposure to existing utilities and surface restoration.
B12-B16 / South/East Branches | Trench / hand dig at crossings | 2x4 PVC ductbank | Verify | THH #15-#19 | Verify | Verify | Verify | Verify | Verify vertical ductbank angles and utility crossing depths before concrete placement.
B20/B22/B33/B17/B18/B19 | Trench / hand dig at crossings | 2x4 PVC ductbank | Verify | THH #8-#13 | Verify | Verify | Verify | Verify | Dense campus area with multiple building tie-ins; coordinate outages and building access.
Restoration | Match existing | N/A | Concrete/asphalt/landscape | N/A | N/A | Verify | Verify | Verify | T-501 details include trenching, concrete edge, pullbox, locking cover and concrete mix details. Confirm patch widths, tie bars and replacement limits.
5. ELECTRICAL / SITE UTILITIES
Area | Electrical Conflict | Telecom Conflict | Storm/Sanitary Conflict | Utility Locate | Grounding/Bonding | Site Lighting | Power Source | Overall | Notes
Overall Site | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical site plans ES101/ES401 are included. Existing utility locations are approximate; coordinate electrical vaults, underground electrical, storm drain manholes and sanitary manholes.
THH / Manholes | Verify | Verify | Verify | Verify | Verify | N/A | N/A | Verify | Locking covers and handhole/manhole locations must be field verified. Confirm bonding/grounding requirements where metallic components are present.
MCR / Provider Entrance | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | T-601 shows WAN/provider fiber entrances and new fiber Path A/B to the MCR. Coordinate with Century Link/service provider and MCR activation.
Building Tie-ins | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Coordinate conduit penetrations with building electrical/telecom/firestop scope and avoid conflicts with existing services.
6. TELECOMMUNICATIONS / FIBER
Scope | Path A | Path B | Fiber Type | Conduit Separation | Riser / Continuation | Testing | VA Acceptance | Overall | Notes
Campus Backbone | Verify | Verify | 24F OS2 10GB to each TR/building | Separate conduit where common ductbank shown | T-601 / building T-101 sheets | Verify | Verify | Verify | Legend identifies new fiber in A route, B route, and A+B routes in separate conduits. Confirm no cross-connect gaps at THHs/manholes.
MCR Provider / WAN | Verify | Verify | 48F OS2 temporary and provider extension noted | Verify | T-601 / MCR sheets | Verify | Verify | Verify | Site one-line shows WAN fiber from service provider and temporary/provider extension pathways. Coordinate with MCR activation and OIT.
Building Drops | Verify | Verify | 24F OS2 to each TR in each building | Verify | Building T-101 and T-601 | Verify | Verify | Verify | Each building tie-in must be tested, labeled, and accepted before connection to active operations.
THH Network | Verify | Verify | Varies by segment | Verify | T-601 | Verify | Verify | Verify | T-601 one-line lists THH #1-#19 and path counts such as 6 Path A + 4 Path B, 6 Path A + 6 Path B, 7 Path A + 7 Path B, 5 Path A + 4 Path B, and 9 Path A + 7 Path B.
7. SECURITY / SITE CONTROL
Area | Access Control | Barricades | Traffic Control | Pedestrian Control | After-hours Work | VA Escort | Public Impact | Overall | Notes
Campus Site Work | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Coordinate staging, access, material storage, noisy work, utility interruption, trench barricades and public access with owner.
Road / Parking Impacts | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | General notes specifically identify accessible parking and public right-of-way impacts; temporary barricades must prevent injury and protect parking signage.
Critical Utility Crossings | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Hand digging at existing utility crossings is in base bid. Confirm permits, Dig Safe, VA utility locate and escort requirements before excavation.
8. OWNER RISKS
Risk ID | Area | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
SITE-R1 | All | Existing utility locations are approximate and field conditions may vary from survey | Critical | High | 9 | Complete utility locate, GPR review, potholing/hand-digging at crossings and VA utility coordination before excavation | GC / Civil / VA | Closed | Multiple sheets repeat that survey conditions may vary and utility location service is required prior to excavation.
SITE-R2 | All | A/B fiber path separation may not be maintained through common ductbank or congested areas | Critical | Medium | 8 | Verify separate conduits, route diversity, THH labels, T-601 path counts and as-built documentation | Telecom / OIT | Closed | Legend allows A+B in common ductbank but separate conduits; redundancy must be validated.
SITE-R3 | All | Concrete ductbank could be backfilled before inspection | High | Medium | 6 | Establish inspection hold point; trench remains open until concrete duct inspection and photos are accepted | GC / QA / COR | Closed | Site notes state trench to remain open until inspection of concrete duct.
SITE-R4 | MCR / Provider | WAN/provider fiber and MCR activation sequence could delay campus cutover | Critical | Medium | 8 | Coordinate Century Link/service provider, temporary fiber, provider extension, MCR readiness and OIT activation plan | OIT / Telecom | Closed | T-601 references WAN fiber, temporary fiber and provider extension.
SITE-R5 | Roads / Parking / Pedestrian Areas | Trenching/restoration may disrupt accessible parking, fire lanes, public access and campus traffic | High | Medium | 6 | Submit traffic/pedestrian/staging plan, maintain fire lanes/hydrants and restore surfaces to match existing | GC / Site | Closed | General notes require coordination with owner and protection of accessible parking/public access.
SITE-R6 | All Building Tie-ins | Building entry penetrations/firestopping may not align with building PMIS packages | High | Medium | 6 | Cross-check every site tie-in against building assessment, T-101 continuation sheets and firestop photos | Telecom / Firestop / QA | Closed | Every building continuation references building T-101 and T-601.
SITE-R7 | Civil Restoration | Asphalt/concrete/landscape restoration quantities and limits may be underestimated | Medium | Medium | 4 | Verify trench patch details, tie bars, concrete/asphalt specs, landscape protection and final surface restoration photo log | GC / Civil | Closed | T-501 includes trenching/restoration details and concrete requirements.
SITE-R8 | Commissioning / Turnover | Fiber testing, labels, as-builts and site utility commissioning may be incomplete | High | Medium | 6 | Track OTDR/power meter tests, conduit as-builts, THH labels, route photos, redlines, third-party inspections and VA/OIT acceptance | GC / Cx / OIT | Closed | Commissioning and third-party inspection requirements apply to site utilities and communications.
9. OPEN QUESTIONS
Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes
SITE-Q1 | Confirm final list of all site fiber buildings and whether Buildings 1-22, 33, 61, 62, 70, 78/78A, 80, 81, 82, Crescent House and MCR are included in one site backbone turnover package. | VA / OIT / Designer | Closed |  |  | Scope and turnover package mapping unclear
SITE-Q2 | Which THH/manhole numbers are new versus existing, and which require locking cover replacement only? | Telecom / Civil | Closed |  |  | Structure inventory and inspection scope unclear
SITE-Q3 | Are all A and B routes physically diverse enough and in separate conduit wherever common ductbank is used? | OIT / Designer | Closed |  |  | Redundancy risk
SITE-Q4 | What are the approved utility-locate/potholing requirements before excavation at each crossing? | GC / VA / Civil | Closed |  |  | Utility strike risk
SITE-Q5 | What inspection hold points are required for ductbank forms, conduit placement, concrete pour, pull string, mandrel and backfill? | QA / COR / Civil | Closed |  |  | QA acceptance risk
SITE-Q6 | Are directional boring alternatives allowed anywhere, or is all base-bid work trenching unless separately approved by Government? | VA / COR | Closed |  |  | Means/methods and cost/schedule risk
SITE-Q7 | What exact fiber test package is required for each path and building tie-in before connection to active operations? | OIT / Telecom / Cx | Closed |  |  | Acceptance/activation risk
SITE-Q8 | How will MCR/provider temporary fiber, new fiber and campus building activation be sequenced to limit shutdowns to one at a time? | OIT / GC / COR | Closed |  |  | Operational outage risk
10. PHOTO LOG
Photo ID | Area | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes
SITE-P001 | Overall Site | Existing Conditions | Campus-wide route photos before excavation, including pavement, sidewalks, landscaping, parking, fire lanes and building entry areas |  |  |  | SITE-R1/SITE-R5 | Closed
SITE-P002 | THH #1-#19 | Structures | Each handhole/manhole/pullbox location, cover, label, depth, drainage, conduit entry, and final installed condition |  |  |  | SITE-R2/SITE-R8 | Closed
SITE-P003 | Ductbank | Pre-pour Inspection | Conduit count, separation, supports/spacers, depth, utility crossings, warning tape, pull strings and concrete encasement before pour |  |  |  | SITE-R1/SITE-R3 | Closed
SITE-P004 | Utility Crossings | Existing Utilities | Potholing/hand-dig photos showing electric, storm, sanitary, water, gas/unknown utilities and clearance to new ductbank |  |  |  | SITE-R1 | Closed
SITE-P005 | Building Tie-ins | Penetrations / Firestop | Exterior entry points, wall/floor penetrations, sleeves, firestop, weatherproofing and interior continuation to building TR/TE |  |  |  | SITE-R6 | Closed
SITE-P006 | Fiber Pull / Testing | Telecom | Fiber reels, pull setup, mandrel/rope, splice/termination points, labels, OTDR/power meter screenshots and OIT acceptance |  |  |  | SITE-R8 | Closed
SITE-P007 | Restoration | Civil | Asphalt/concrete trench patches, sidewalk panels, landscaping, turf, drainage, curb/edge details and final cleanup |  |  |  | SITE-R5/SITE-R7 | Closed
SITE-P008 | MCR / Provider Entrance | Critical Cutover | Provider handoff, WAN fiber route, temporary fiber, Path A/B into MCR and activation/cutover coordination photos |  |  |  | SITE-R4/SITE-R8 | Closed
11. OWNER READINESS SCORE
Area | Site Readiness | Utility Locate | Ductbank | Telecom | Restoration | Documentation | Total Score | Readiness | Notes
Overall Site | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Campus-wide fiber backbone is not construction-ready until utility locates, path routing, inspection holds and phasing plan are confirmed.
Path A/B Backbone | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Redundant A/B path separation, conduit counts and T-601 one-line coordination require field verification.
THH / Manholes | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | THH #1-#19 and locking manholes/pullboxes need inventory, labels, photos and acceptance.
Building Tie-ins | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Building T-101 continuation, penetration/firestop and fiber acceptance must match each building assessment.
MCR / Provider Entrance | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Verify | 0.5 | Partial / Yellow | Provider fiber, temporary fiber and new MCR activation sequence are critical path items.
12. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.SITE.20260316.pdf
Drawing Index | 29-sheet SITE IFC package includes general notes, infection control, indoor air quality, survey plans, electrical site plans, telecom site plans, enlarged views, plan/profile sheets TS201-TS210, telecom utility details T-501 and site one-line T-601.
Scope Basis | Cover sheet identifies site infrastructure upgrades, new redundant site infrastructure, temporary fiber between existing entrance room/data center and new MCR, new site fiber conduit encased in concrete, base-bid trenching/concrete ductbank/hand digging at crossings, and Government approval required for directional boring.
Telecom Basis | TS100-TS104 show site telecom plans and enlarged views. TS201-TS210 show Path A/B plan-profile segments for B12-B16, B1-B70, B20/B22, B15/B9, B13/B14, B70/B81, B33/B17, B18/B19, and B81/B17-to-B01/B18. T-601 shows Path A/B one-line and THH counts.
Ductbank Basis | T-501 details show primary ductbank/trenching, 2x4-inch and 4x4-inch PVC conduit arrangements, concrete ductbank, concrete pullbox, locking cover on existing manhole, concrete edge detail and 5000 PSI concrete mix references.
Survey / Utility Basis | Survey notes state site data was based on VA as-builts, photographic/visual/LIDAR survey, GPR/GNSS/GPS where noted, and conditions may vary. Contractor must verify utility location and depth before excavation.
Operational Basis | General notes require all systems commissioned/recommissioned, third-party inspections/testing/written reports, coordination drawings before work, shutdowns limited to one at a time, and all telecom cabling tested/approved/accepted by VA before connecting to active operations.
Safety / Access Basis | General notes require fire lanes, hydrants and FDCs to remain clear, public access and accessible parking impacts to be coordinated, infection control/dust measures used, and temporary barriers/fire watch/temporary firestopping as required.
12. PAYMENT VERIFICATION
SOV Item | Status | Contractor % | Inspector % | Recommended % | Variance | Evidence / Comments
Telecom Room Build | Not Started | 0% | 0% | 🟡 | 0%
Cooling Installation | Not Started | 100% | 0% | 🟢 | -100%
UPS Installation | Not Started | 100% | 0% | 🟢 | -100%
Fiber Installation | Not Started | 100% | 0% | 🟢 | -100%
Firestopping | Not Started | 100% | 0% | 🟢 | -100%
Payment Confidence |  | 80% | 0% | Success: Recommended payment aligns with observed progress and evidence is documented.
13. OIT ACTIVATION READINESS
Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref.
Telecom Room Complete | Not Started | N/A | N/A | 0
Rack Installed | Not Started | N/A | N/A | 0
Fiber Tested | Not Started | N/A | N/A | 0
UPS Operational | Not Started | N/A | N/A | 0
Network Equipment Received | Not Started | N/A | N/A | 0
National OIT Approval | Not Started | N/A | N/A | 0
Local OIT Ready | Not Started | N/A | N/A | 0
Activation Scheduled | Not Started | N/A | N/A | 0
OIT Readiness |  |  |  | Success: Required OIT activation prerequisites are complete or formally coordinated.
14. SUBMITTAL / MATERIAL VERIFICATION
Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence
Telecom Equipment | Not Started | No | No | No | Pending
Cable Tray | Not Started | No | No | No | Pending
Firestop System | Not Started | No | No | No | Pending
HVAC Equipment | Not Started | No | No | No | Pending
Electrical Equipment | Not Started | No | No | No | Pending
Inspection Compliance |  | 0% |  | Success: Installed materials match approved submittals and deficiencies are documented.
15. PRODUCTIVITY OBSERVATIONS
Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause
Electrical | Not Started
Telecom | Not Started
Mechanical | Not Started
Firestop | Not Started
Contractor Performance |  |  |  | Success: Actual production is on or above baseline, or delay cause is documented.
16. OWNER ACCEPTANCE READINESS
Requirement | Status | Required | Complete | Score | Comments | Evidence Ref.
Construction Complete | Not Started | Yes | No | 0
QA/QC Complete | Not Started | Yes | No | 0
Deficiencies Closed | Not Started | Yes | No | 0
OIT Ready | Not Started | Yes | No | 0
Documentation Complete | Not Started | Yes | No | 0
Recommended for Acceptance | Not Started | Yes | No | 0
Acceptance Readiness |  | 0% |  | Success: Building is ready for turnover when all required gates are complete.
16. SOURCE / DRAWING REVIEW NOTES
Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf
Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references.
Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels.
Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms.
Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits.
Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft.
Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination.
Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time.
PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK
Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete.
How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column.
Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal
Approved Submittals | No |  |  |  |  | 🟡
ICRA / PCRA | No |  |  |  |  | 🟡
QA/QC Reports | No |  |  |  |  | 🟡
Firestopping | No |  |  |  |  | 🟡
Cable Tests | No |  |  |  |  | 🟡
OIT Acceptance | No |  |  |  |  | 🟡
Photos | No |  |  |  |  | 🟡
Zero Critical Punch Items | No |  |  |  |  | 🟡
Requirement | What it Means |  |  | Verification
Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. |  |  | Verify approved submittals exist for all installed systems and that field installations match the approved documents.
ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. |  |  | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures.
QA/QC Reports | Contractor quality inspections have been completed and documented. |  |  | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation.
Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. |  |  | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos.
Cable Tests | All network, fiber, and communication cabling has passed required testing. |  |  | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation.
OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. |  |  | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable.
Photos | Construction has been photographically documented. |  |  | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized.
Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. |  |  | Walk the space and confirm all critical deficiencies have been corrected prior to turnover.
Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN
Open Gate Count | 8
Gate Completion | 0 / 8 Complete
Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN.
Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW")
17. OWNER DECISION SUMMARY
Recommended Payment
☐ Full
☐ Partial
☐ Withhold
18. Construction Status
☐ On Schedule
☐ Behind Schedule
☐ Critical Delay
19. OIT
☐ Ready
☐ Waiting on Contractor
☐ Waiting on Local OIT
☐ Waiting on National OIT
20. Acceptance
☐ Ready for Turnover
☐ Ready with Punch List
☐ Not Ready
Inspector Comments
Note on B118: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B127: Dropdown status drives visual cue. Percent fields and evidence support payment defense.
Note on B139: Compare installed materials against approved submittals/spec sections.
Note on B148: Planned vs actual production supports delay/time-extension rebuttal.
Note on B156: Final owner acceptance gate. These fields can feed PMIS_Data later.

## SPEC_Assessment (hidden)
SPECIFICATIONS ASSESSMENT │ COMBINED SINGLE-SHEET PMIS WORKBOOK
Source Workbook | Specifications_Assessment.xlsx | Combined On | 2026-06-26 13:00 | Original Sheet Count | 15 | Output | Single worksheet
Source PDF | 518-22-700.Bedford.MA.EHRM.Specifications.IFC.20260413.pdf | Project | 518-22-700 | Spec Date | 04/13/2026 | Pages | 2363
Purpose | Stacked all original workbook tabs into one sheet for PMIS import/use.
INDEX | Original Sheet | Start Row | End Row | Rows
| Dashboard | 8 | 29 | 22
| Spec Matrix | 32 | 70 | 39
| General Reqs | 73 | 90 | 18
| Submittal Matrix | 93 | 107 | 15
| QA QC | 110 | 120 | 11
| Commissioning | 123 | 133 | 11
| Safety ICRA | 136 | 144 | 9
| MEP Electrical | 147 | 158 | 12
| Div27 Comms | 161 | 173 | 13
| Security | 176 | 183 | 8
| Civil Site | 186 | 195 | 10
| Owner Risks | 198 | 210 | 13
| Open Questions | 213 | 225 | 13
| Deliverables | 228 | 240 | 13
| Source Notes | 243 | 253 | 11
Dashboard | 01 91 00 Commissioning | 3 | Cx tracker and turnover readiness | Verify | CxA / GCC | Systems not commissioned | Cx plan, tests, checklists | Commissioning | Commissioning plan included as 01 91 00.A. | TOC p.3
Dashboard | 21 22 00 Clean Agent Fire Suppression | 5 | MCR/special fire suppression acceptance | Verify | FP / FA / Cx | Clean agent acceptance failure | Room integrity, test reports | Fire Life Safety | Critical for MCR. | TOC p.5
Dashboard | 23 81 23 Computer-Room Air-Conditioners | 5 | MCR/TR cooling readiness | Verify | Mechanical / Cx | Cooling failure | Startup, TAB, alarms | HVAC Matrix | Critical cooling section. | TOC p.5
Dashboard | 26 33 53.10 Static UPS for Telecom | 6 | UPS/PDU acceptance | Verify | Electrical / Telecom | Power failure/cutover risk | Startup, load test, labels | Electrical Matrix | Telecom UPS spec dated 08-2025. | TOC p.6
Dashboard | 27 10 00 Structured Cabling | 6 | Telecom test and labeling baseline | Verify | Telecom / OIT | Cable acceptance failure | Test records, labels, as-builts | Div27 Comms | Core PMIS section for all buildings. | TOC p.6
Dashboard | 28 13 00 / 28 23 00 Security | 6 | PACS/CCTV acceptance | Verify | Security / OIT | Security system gaps | VMS/PACS tests | Security Matrix | Includes physical access control and video surveillance. | TOC p.6
Dashboard | 33 08 00 Site Utilities Cx |  | Site utility commissioning | Verify | Site / Cx | Fiber/site turnover gaps | Inspection/test/as-built records | Civil Site | Covers commissioning of site utilities. | TOC p.7
Dashboard | Bid Form / Estimate Breakdown | 9 | Cost breakdown and contracting reference | Info | Contractor / VA | Cost coding mismatch | CLIN cost breakdown | Cost Matrix | Bid form and construction estimate breakdown pages included. | PDF p.9-18+
SECTION: Spec Matrix
Spec Matrix | SPECIFICATION MATRIX │ DIVISION / SECTION CROSS REFERENCE
Spec Matrix | Section | Title | Division | Date | Spec Page | PMIS Priority | Status | Owner / Reviewer | Required PMIS Action | Source
Spec Matrix | 00 01 10 | - 1 |  |  |  | Medium | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | Spec Book TOC
Spec Matrix | 00 01 10 | - 2 | DIVISION 04 — MASONRY |  |  | Medium | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | Spec Book TOC
Spec Matrix | 00 01 10 | - 3 | DIVISION 12 — FURNISHINGS |  |  | Medium | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | Spec Book TOC
Spec Matrix | 00 01 10 | - 4 | DIVISION 26 — ELECTRICAL |  |  | Medium | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | Spec Book TOC
Spec Matrix | 00 01 10 | - 5 | DIVISION 28 — ELECTRONIC SAFETY AND SECURITY |  |  | Medium | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | Spec Book TOC
Spec Matrix | 01 00 00 | General Requirements | DIVISION 01 — GENERAL REQUIREMENTS | 05-2021 | 29 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 00 00.A | Appendix A - OIT-InfrastrucStdTelecomSpaces | DIVISION 01 — GENERAL REQUIREMENTS |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 00 00.B | Appendix B – Submittal Log | DIVISION 01 — GENERAL REQUIREMENTS |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 00 00.C | Appendix C - VHA ICRA-1.3 | DIVISION 01 — GENERAL REQUIREMENTS | 12-2024 |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 00 00.D | Appendix D - VHA PCRA 2024 | DIVISION 01 — GENERAL REQUIREMENTS | 2024 |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 00 00.E | Appendix E - ACM Inspection / LCP Testing Report | DIVISION 01 — GENERAL REQUIREMENTS | 11-2024 |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 00 00.F | Appendix F - GPRS Report | DIVISION 01 — GENERAL REQUIREMENTS |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 00 00.G | Appendix G - Geotechnical and Boring Reports | DIVISION 01 — GENERAL REQUIREMENTS |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 32 16.15 | Project Schedules | DIVISION 01 — GENERAL REQUIREMENTS | 12-2025 | 3 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 33 23 | Shop Drawings, Product Data, and Samples | DIVISION 01 — GENERAL REQUIREMENTS | 06-2025 | 3 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 33 24 | Electronic Submittal Procedures | DIVISION 01 — GENERAL REQUIREMENTS |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 35 26 | Safety Requirements | DIVISION 01 — GENERAL REQUIREMENTS | 05-2024 | 3 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 45 00 | Quality Control | DIVISION 01 — GENERAL REQUIREMENTS | 05-2021 | 3 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 45 29 | Testing Laboratory Services | DIVISION 01 — GENERAL REQUIREMENTS |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 45 35 | Special Inspections | DIVISION 01 — GENERAL REQUIREMENTS | 06-2021 |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 01 91 00 | General Commissioning Requirements | DIVISION 01 — GENERAL REQUIREMENTS | 04-2022 | 3 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.3
Spec Matrix | 21 22 00 | Clean Agent Fire Suppression Systems | DIVISION 21 — FIRE SUPPRESSION | 05-2015 | 5 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.5
Spec Matrix | 23 81 23 | Computer-Room Air-Conditioners | DIVISION 23 — HVAC | 03-2023 |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.5
Spec Matrix | 26 33 53.10 | Static UPS for Telecom | DIVISION 26 — ELECTRICAL | 08-2025 |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 27 05 00 | Common Work Results for Communications | DIVISION 27 — COMMUNICATIONS | 04-2026 | 6 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 27 05 36 | Cable Trays for Communications Systems | DIVISION 27 — COMMUNICATIONS | 04-2026 | 6 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 27 10 00 | Structured Cabling | DIVISION 27 — COMMUNICATIONS | 04-2026 | 6 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 27 11 16 | Communications Cabinets, Racks, Frames, and Enclosures | DIVISION 27 — COMMUNICATIONS | 04-2026 | 6 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 27 13 23 | Communications Optical Fiber Backbone Cabling | DIVISION 27 — COMMUNICATIONS | 04-2026 | 6 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 27 15 13 | Communications Copper Horizontal Cabling | DIVISION 27 — COMMUNICATIONS | 04-2026 | 6 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 28 13 00 | Physical Access Control Systems | DIVISION 28 — ELECTRONIC SAFETY AND SECURITY |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 28 23 00 | Video Surveillance | DIVISION 28 — ELECTRONIC SAFETY AND SECURITY | 09-2011 | 6 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.6
Spec Matrix | 28 31 00 | Fire Detection and Alarm | DIVISION 28 — ELECTRONIC SAFETY AND SECURITY |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.7
Spec Matrix | 31 20 00 | Earthwork | DIVISION 31 — EARTHWORK |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.7
Spec Matrix | 32 12 16 | Asphalt Paving | DIVISION 32 — EXTERIOR IMPROVEMENTS |  |  | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.7
Spec Matrix | 33 08 00 | Commissioning of Site Utilities | DIVISION 33 — UTILITIES |  | 3 | High | Verify | GCC / QA / Discipline Lead | Track requirements in PMIS; confirm submittals/testing/inspection evidence. | TOC p.7
SECTION: General Reqs
General Reqs | DIVISION 01 / GENERAL REQUIREMENTS │ PMIS CONTROLS
General Reqs | Spec Section | Requirement Area | PMIS Deliverable | Frequency / Timing | Responsible Party | Status | Required Evidence | Risk if Missed | Related Building/Site | Source
General Reqs | 01 00 00 | General Requirements | Master compliance checklist | Project duration | GCC / PM / QA | Verify | Approved project controls, coordination records | Baseline requirements missed | All | TOC p.3
General Reqs | 01 00 00.A | OIT Infrastructure Standards Telecom Spaces | Telecom room acceptance checklist | Before TR/TE acceptance | Telecom / OIT | Verify | OIT standard checklist, TR/TE inspection | TR/TE acceptance failure | All TR/TE/MCR | TOC p.3
General Reqs | 01 00 00.B | Submittal Log | Submittal tracker | Before procurement/install | GCC / Submittal Manager | Verify | Current approved submittal log | Unapproved products installed | All | TOC p.3
General Reqs | 01 00 00.C | VHA ICRA | ICRA permit/containment tracker | Before intrusive work | GCC Safety / VA ICRA | Verify | ICRA forms, barrier inspections | Infection control incident | Interior work | TOC p.3
General Reqs | 01 00 00.D | VHA PCRA | PCRA permit/utility risk tracker | Before utility/fire/life safety work | GCC Safety / VA | Verify | PCRA form, shutdown plan | Patient/campus safety disruption | MEP/Site | TOC p.3
General Reqs | 01 00 00.E | ACM/LCP Report | Hazardous materials tracker | Before disturbance | GCC / IH | Verify | Abatement plan, clearance reports | Hazmat exposure / delay | Bldg 05/61/78 etc. | TOC p.3
General Reqs | 01 00 00.F | GPRS Report | Utility/existing conditions tracker | Before excavation/coring | GC / Civil / QA | Verify | GPR records, potholing photos | Utility strike | SITE / interior coring | TOC p.3
General Reqs | 01 00 00.G | Geotechnical / Boring Reports | Civil/site risk reference | Before site/civil work | GC / Civil | Verify | Boring/geotech review | Unexpected soil conditions | MCR/SITE | TOC p.3
General Reqs | 01 32 16.15 | Project Schedule | Baseline and look-ahead schedule | Weekly/monthly | GCC / Scheduler | Verify | Baseline schedule, updates, fragnet for cutovers | Critical path not visible | All | TOC p.3
General Reqs | 01 33 23 | Shop Drawings, Product Data, Samples | Submittals by discipline | Before procurement/install | GCC / Designer | Verify | Approved submittals | Rework/unapproved materials | All | TOC p.3
General Reqs | 01 35 26 | Safety Requirements | Safety/AHA/JHA/ICRA/PCRA controls | Daily/Activity-specific | GCC Safety | Verify | AHA/JHA, permits, toolbox records | Safety event | All | TOC p.3
General Reqs | 01 45 00 | Quality Control | QC plan and inspection log | Daily/weekly | GCC QA | Verify | QC reports, inspections, NCRs | Defects not tracked | All | TOC p.3
General Reqs | 01 45 29 | Testing Laboratory Services | Third-party testing tracker | As required | Testing Lab / GCC | Verify | Lab reports | Unverified work | Concrete/site/special inspections | TOC p.3
General Reqs | 01 45 35 | Special Inspections | Special inspection register | At hold points | SI / GCC / COR | Verify | SI reports, template | Failed code/QA acceptance | MCR/Site/Structural | TOC p.3
General Reqs | 01 91 00 | General Commissioning Requirements | Commissioning tracker | Pre-functional through turnover | CxA / GCC | Verify | Cx plan, checklists, issues log | Systems not ready | MEP/FP/Electrical/Comms | TOC p.3
SECTION: Submittal Matrix
Submittal Matrix | SUBMITTAL MATRIX │ SPEC-DRIVEN REQUIRED SUBMITTALS
Submittal Matrix | Spec | Submittal | Discipline | Timing | Owner | Status | Evidence | Risk | Priority | Source
Submittal Matrix | 01 33 23 | Master Submittal Register | All disciplines | Before procurement | GCC / Submittal Manager | Verify | Approved log from Appendix B and project updates | Unapproved work installed | High | TOC p.3
Submittal Matrix | 01 35 26 | Safety / ICRA / PCRA Submittals | Safety | Before work | GCC Safety | Verify | AHA/JHA, ICRA, PCRA, permits | Unsafe / unauthorized work | Critical | TOC p.3
Submittal Matrix | 02 82 / 02 83 | Hazmat Abatement Plans | Existing conditions | Before disturbance | IH / Abatement Contractor | Verify | Asbestos/LBP submittals, clearance reports | Exposure / shutdown | Critical | TOC p.3
Submittal Matrix | 07 84 00 | Firestopping Systems | Architectural / FP | Before penetrations closed | GC / Firestop | Verify | UL systems, product data, installer certs | Unrated penetrations | Critical | TOC p.4
Submittal Matrix | 21 22 00 | Clean Agent Fire Suppression | Fire suppression | Before MCR work | FP Contractor | Verify | Calculations, agent, cylinders, sequence | MCR acceptance failure | Critical | TOC p.5
Submittal Matrix | 23 81 23 | Computer-Room Air-Conditioners | HVAC | Before procurement/startup | Mechanical | Verify | CRAC/IU/CU product data, controls, startup | Cooling failure | Critical | TOC p.5
Submittal Matrix | 26 33 53.10 | UPS for Telecom | Electrical | Before procurement/startup | Electrical | Verify | UPS/PDU data, batteries, startup | Power failure | Critical | TOC p.6
Submittal Matrix | 27 10 00 | Structured Cabling | Communications | Before cable install | Telecom | Verify | Cable, patch panels, test procedures | Telecom rejection | Critical | TOC p.6
Submittal Matrix | 27 13 23 | Optical Fiber Backbone | Communications | Before fiber pull/splice | Telecom / OIT | Verify | Fiber, LIU, test plan, OTDR | Backbone failure | Critical | TOC p.6
Submittal Matrix | 28 13 00 | Physical Access Control | Security | Before security install | Security | Verify | Controllers, readers, door hardware interfaces | Access failure | High | TOC p.6
Submittal Matrix | 28 23 00 | Video Surveillance | Security | Before camera install | Security / OIT | Verify | Camera, VMS, mounts, PoE | CCTV failure | High | TOC p.6
Submittal Matrix | 33 08 00 | Site Utility Commissioning | Site Utilities | Before turnover | Civil / Cx | Verify | Utility test reports, as-builts | Site turnover failure | High | TOC p.7
SECTION: QA QC
QA QC | QA/QC AND INSPECTION MATRIX
QA QC | Spec | Requirement Area | QA/QC Activity | Timing | Owner | Status | Required Evidence | Risk | Applies To | Source
QA QC | 01 45 00 | Quality Control | Daily QC report, deficiency log, corrective action tracking | Daily / weekly | GCC QA | Verify | QC reports, issue/NCR log | Defects not corrected | All | TOC p.3
QA QC | 01 45 29 | Testing Laboratory Services | Lab tests and reports | At test events | Testing Lab | Verify | Concrete/material/site reports | Unverified work | Civil/Structural/Site | TOC p.3
QA QC | 01 45 35 | Special Inspections | Special inspection checklist and reports | Hold points | SI / COR | Verify | SI reports and template | Code/contract acceptance risk | MCR/Site/Structural | TOC p.3
QA QC | 07 84 00 | Firestopping Inspection | Firestop photos and product verification | Before cover/close-in | Firestop / QA | Verify | UL system, before/after photos | Rated assembly failure | All penetrations | TOC p.4
QA QC | 26 05 73 | OCP Coordination Study | Coordination/arc/short-circuit study status | Before energization | Electrical | Verify | Approved study and settings | Electrical protection issue | MCR/TRs | TOC p.6
QA QC | 27 08 00 | Communications Commissioning | Cable test results, labels and acceptance | Before active connection | Telecom / OIT | Verify | Copper/fiber tests, OIT signoff | Network acceptance failure | All buildings | TOC p.6
QA QC | 28 08 00 | Security Commissioning | PACS/CCTV functional tests | Before turnover | Security / OIT | Verify | Functional test forms | Security acceptance failure | TR/MCR | TOC p.6
QA QC | 33 08 00 | Site Utilities Commissioning | Site utility testing and acceptance | Before turnover | Civil / Cx | Verify | As-builts, inspection reports, test records | Utility turnover risk | SITE | TOC p.7
SECTION: Commissioning
Commissioning | COMMISSIONING MATRIX
Commissioning | Spec | System | Commissioning Requirement | Timing | Owner | Status | Required Evidence | Risk | Applies To | Source
Commissioning | 01 91 00 | General Commissioning | Master commissioning plan, issues log, pre-functional and functional testing | Start-up through turnover | CxA / GCC | Verify | Cx plan, checklists, issue log, final report | Uncommissioned systems | All commissioned systems | TOC p.3
Commissioning | 21 08 00 | Fire Suppression Commissioning | Sprinkler and clean-agent testing | Acceptance | FP / Cx | Verify | Hydro/flow tests, clean-agent acceptance | FP system not accepted | MCR/TRs | TOC p.5
Commissioning | 22 08 00 | Plumbing Commissioning | Plumbing system tests where applicable | Acceptance | Plumbing / Cx | Verify | Test reports | Plumbing turnover gaps | MCR/Site if applicable | TOC p.5
Commissioning | 23 08 00 | HVAC Commissioning | Startup, TAB, controls, alarm integration | Startup/functional test | Mechanical / Cx | Verify | Startup, TAB, DDC point-to-point, trend logs | Cooling failures | MCR/TR cooling | TOC p.5
Commissioning | 26 08 00 | Electrical Commissioning | UPS, ATS, generator, panel, SPD, load testing | Energization/startup | Electrical / Cx | Verify | Startup, load tests, OCP settings | Power failures | MCR/TRs | TOC p.6
Commissioning | 27 08 00 | Communications Commissioning | Copper/fiber tests, labels, record docs, OIT acceptance | Pre-activation | Telecom / OIT | Verify | OTDR, copper tests, labels, signoff | Network failure | All TR/TE/MCR/SITE | TOC p.6
Commissioning | 28 08 00 | Security Commissioning | PACS/CCTV/fire alarm/security tests | Acceptance | Security / FA / Cx | Verify | VMS/PACS tests, reports | Security failure | TR/MCR | TOC p.6
Commissioning | 33 08 00 | Site Utilities Commissioning | Site utilities inspections/tests/as-builts | Before turnover | Civil / Cx | Verify | Ductbank/fiber/site utility records | Site utility failure | SITE | TOC p.7
SECTION: Safety ICRA
Safety ICRA | SAFETY / ICRA / PCRA MATRIX
Safety ICRA | Spec | Requirement | Control | Timing | Owner | Status | Evidence | Risk | Applies To | Source
Safety ICRA | 01 35 26 | Safety Requirements | Project safety plan, AHA/JHA, daily hazard analysis | Daily / task-specific | GCC Safety | Verify | Safety plan, AHA/JHA, toolbox talks | Safety event | All | TOC p.3
Safety ICRA | 01 00 00.C | VHA ICRA | Infection control risk assessment and barriers | Before intrusive interior work | GCC / VA ICRA | Verify | ICRA permits, barrier inspections | Infection control issue | All occupied work | TOC p.3
Safety ICRA | 01 00 00.D | VHA PCRA | Pre-construction risk assessment for utilities/life safety | Before disruptive work | GCC / VA | Verify | PCRA permit, shutdown plan | Operational disruption | MEP/Site | TOC p.3
Safety ICRA | 01 57 19 | Temporary Environmental Controls | Dust/noise/IAQ/water controls | During construction | GCC | Verify | Logs, IAQ/dust controls, barriers | Occupant impact | Interior/Site | TOC p.3
Safety ICRA | 02 82 / 02 83 | ACM/LBP | Abatement controls and clearance | Before disturbance | IH / Abatement | Verify | Abatement plan, monitoring, clearance | Hazmat exposure | Hazmat buildings | TOC p.3
Safety ICRA | 31 20 00 | Earthwork Safety | Excavation, trench, utility locate, traffic control | Before excavation | GC / Civil | Verify | Dig Safe, trench plan, permits | Utility strike / injury | SITE | TOC p.7
SECTION: MEP Electrical
MEP Electrical | MEP / ELECTRICAL / FIRE MATRIX
MEP Electrical | Spec | Requirement | Scope | Discipline | Owner | Status | Evidence | Risk | Applies To | Source
MEP Electrical | 21 13 13 | Wet-Pipe Sprinkler System | FP modifications for TR/MCR spaces | FP | FP Contractor | Verify | Shop drawings, tests, acceptance | Life-safety failure | TR/MCR | TOC p.5
MEP Electrical | 21 22 00 | Clean Agent Fire Suppression | Clean-agent system, release/abort, room integrity | FP | FP / FA / Cx | Verify | Calc, acceptance tests, room integrity | MCR acceptance failure | MCR | TOC p.5
MEP Electrical | 23 05 93 | Testing, Adjusting, and Balancing | TAB for HVAC systems | HVAC | TAB / Mechanical | Verify | TAB report | Cooling/airflow issue | MCR/TRs | TOC p.5
MEP Electrical | 23 09 23 | Direct-Digital Control System | DDC/BACnet control integration | HVAC Controls | Controls / Mechanical | Verify | Point-to-point, trends, alarms | No alarms/controls | MCR/TRs | TOC p.5
MEP Electrical | 23 81 23 | Computer-Room Air-Conditioners | CRAC units for computer room applications | HVAC | Mechanical / Cx | Verify | Startup, alarms, capacity | MCR cooling failure | MCR | TOC p.5
MEP Electrical | 26 05 26 | Grounding and Bonding | Electrical grounding/bonding | Electrical | Electrical | Verify | Test/inspection records | Grounding defects | All | TOC p.5
MEP Electrical | 26 33 53.10 | Static UPS for Telecom | Telecom UPS requirements | Electrical | Electrical / Telecom | Verify | Startup, batteries, load test | UPS failure | TR/TE/MCR | TOC p.6
MEP Electrical | 26 43 13 | Surge Protective Devices | SPD requirements | Electrical | Electrical | Verify | SPD submittals, install verification | Surge risk | TR/MCR | TOC p.6
MEP Electrical | 28 31 00 | Fire Detection and Alarm | Fire alarm modifications and clean-agent interface | FA | FA / FP | Verify | FA tests, matrix, interface tests | Life-safety acceptance issue | TR/MCR | TOC p.7
SECTION: Div27 Comms
Div27 Comms | DIVISION 27 COMMUNICATIONS MATRIX
Div27 Comms | Spec | Requirement | Scope | Category | Owner | Status | Evidence | Risk | Applies To | Source
Div27 Comms | 27 05 00 | Common Work Results for Communications | General comms requirements, coordination, workmanship | All telecom | Telecom / OIT | Verify | Submittals, install inspections | Base telecom noncompliance | All | TOC p.6
Div27 Comms | 27 05 26 | Grounding and Bonding for Communications | TGB/TMGB bonding, rack bonding | TR/TE/MCR | Telecom / Electrical | Verify | Bonding inspection, test records | Grounding defect | All telecom rooms | TOC p.6
Div27 Comms | 27 05 33 | Raceways and Boxes for Communications | Conduit, sleeves, boxes, pathways | Pathway | Telecom / GC | Verify | Sleeve/pathway inspection | Cable pathway failure | All | TOC p.6
Div27 Comms | 27 05 36 | Cable Trays for Communications | Cable tray install and supports | Pathway | Telecom / GC | Verify | Tray inspection/photos | Coordination/firestop gaps | TR/SITE/MCR | TOC p.6
Div27 Comms | 27 05 53 | Identification for Communications Systems | Labels and identifiers | All telecom | Telecom | Verify | Label schedule, field photos | Acceptance failure | All | TOC p.6
Div27 Comms | 27 10 00 | Structured Cabling | Copper/fiber structured cabling system | All telecom | Telecom / OIT | Verify | Test reports/as-builts | Network acceptance failure | All | TOC p.6
Div27 Comms | 27 11 16 | Cabinets, Racks, Frames, Enclosures | Rack/TE/TR cabinet requirements | TR/TE/MCR | Telecom | Verify | Rack/cabinet submittals, install inspection | Equipment fit/failure | All TR/TE/MCR | TOC p.6
Div27 Comms | 27 11 26 | Rack Mounted Power Protection / Power Strips | Rack PDU/power strip requirements | Rack power | Electrical / Telecom | Verify | PDU install, labels | Power acceptance failure | TR/TE/MCR | TOC p.6
Div27 Comms | 27 13 23 | Optical Fiber Backbone Cabling | OS2 backbone fiber | Backbone | Telecom / OIT | Verify | OTDR/power meter, labels | Backbone failure | SITE/MCR/Buildings | TOC p.6
Div27 Comms | 27 15 13 | Copper Horizontal Cabling | Cat6A horizontal copper | Horizontal | Telecom | Verify | Copper certification tests | Port acceptance failure | All buildings | TOC p.6
SECTION: Security
Security | DIVISION 28 SECURITY / FIRE ALARM MATRIX
Security | Spec | Requirement | Scope | Category | Owner | Status | Evidence | Risk | Applies To | Source
Security | 28 05 00 | Common Work Results for Electronic Safety and Security | General security requirements | Security | Security / OIT | Verify | Submittals, testing records | Security baseline missed | All security scope | TOC p.6
Security | 28 08 00 | Commissioning of ESS Systems | Security commissioning and testing | Security Cx | Security / Cx | Verify | Functional tests, reports | Security system not accepted | PACS/CCTV | TOC p.6
Security | 28 13 00 | Physical Access Control Systems | Card readers, controllers, door devices | PACS | Security / Door HW | Verify | Device tests, door coordination | Access failure | TR/MCR doors | TOC p.6
Security | 28 23 00 | Video Surveillance | Cameras and VMS integration | CCTV | Security / OIT | Verify | Camera tests, VMS screenshots | Surveillance failure | TR/MCR/SITE | TOC p.6
Security | 28 31 00 | Fire Detection and Alarm | Fire alarm changes and interfaces | FA | FA / FP | Verify | FA reports, interface tests | Life-safety issue | TR/MCR | TOC p.7
SECTION: Civil Site
Civil Site | CIVIL / SITE / UTILITIES MATRIX
Civil Site | Spec | Requirement | Scope | Category | Owner | Status | Evidence | Risk | Applies To | Source
Civil Site | 31 20 00 | Earthwork | Excavation, trenching, backfill | Site | Civil / GC | Verify | Utility locates, trench inspections | Utility strike | SITE/MCR | TOC p.7
Civil Site | 31 23 19 | Dewatering | Dewatering controls | Site | Civil | Verify | Plan/logs if needed | Water in excavation | SITE/MCR | TOC p.7
Civil Site | 31 23 23.33 | Flowable Fill | Controlled fill | Site | Civil | Verify | Tickets/reports | Backfill failure | SITE | TOC p.7
Civil Site | 32 05 23 | Cement and Concrete for Exterior Improvements | Concrete restoration/ductbank areas | Site | Civil | Verify | Concrete tickets/tests | Restoration failure | SITE | TOC p.7
Civil Site | 32 12 16 | Asphalt Paving | Asphalt restoration | Site | Civil | Verify | Paving reports/photos | Poor restoration | SITE | TOC p.7
Civil Site | 33 08 00 | Commissioning of Site Utilities | Utility turnover commissioning | Site utilities | Civil / Cx | Verify | Commissioning records | Utility turnover gap | SITE | TOC p.7
Civil Site | 33 40 00 | Storm Sewer Utilities | Storm utility protection/coordination | Site | Civil | Verify | Utility locate/as-builts | Storm conflict | SITE | TOC p.7
SECTION: Owner Risks
Owner Risks | OWNER RISK REGISTER │ SPECIFICATIONS
Owner Risks | Risk ID | Area | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes
Owner Risks | SPEC-R1 | All | Spec package is 2,363 pages and can drive missed submittals/inspections if not indexed | High | Medium | 6 | Use Spec Matrix as PMIS master checklist; tie every building deficiency to spec section | GCC / QA | Closed | Master risk
Owner Risks | SPEC-R2 | Submittals | Appendix B submittal log may not be reconciled with current shop drawings | High | Medium | 6 | Request current submittal register and compare to spec matrix | GCC / Submittal Manager | Closed | 01 00 00.B / 01 33 23
Owner Risks | SPEC-R3 | Safety/ICRA | ICRA/PCRA not linked to each building/site work package | Critical | Medium | 8 | Track ICRA/PCRA by building, room and work activity | GCC Safety / VA | Closed | 01 00 00.C/D
Owner Risks | SPEC-R4 | Hazmat | ACM/LCP report not cross-referenced to drawing/building packages | Critical | Medium | 8 | Build hazmat matrix by building and disturbance type | IH / GCC | Closed | 01 00 00.E / 02 82 / 02 83
Owner Risks | SPEC-R5 | Commissioning | Commissioning scope spans MEP, FP, electrical, communications, security and site utilities | Critical | Medium | 8 | Create Cx tracker by system and hold point | CxA / GCC | Closed | 01 91 00; 21/23/26/27/28/33 Cx
Owner Risks | SPEC-R6 | Telecommunications | Division 27 testing/labeling/as-builts may not be collected uniformly across buildings | Critical | Medium | 8 | Create standard telecom acceptance packet per building | Telecom / OIT | Closed | 27 05 00 / 27 10 00
Owner Risks | SPEC-R7 | Electrical | UPS/PDU/SPD/grounding requirements may vary across TR/TE/MCR | High | Medium | 6 | Track electrical acceptance by room/panel/rack | Electrical / QA | Closed | 26 05 / 26 33 / 26 43
Owner Risks | SPEC-R8 | Firestopping | Rated penetrations could be missed across site and building tie-ins | Critical | Medium | 8 | Require firestop photos and UL system log by room/penetration | Firestop / QA | Closed | 07 84 00
Owner Risks | SPEC-R9 | MCR | MCR critical systems require integrated commissioning beyond typical building assessments | Critical | Medium | 8 | Create dedicated MCR commissioning/activation checklist | CxA / OIT | Closed | MCR + 01 91 00
Owner Risks | SPEC-R10 | Turnover | O&M, warranties, training and record docs may not be complete before turnover | High | Medium | 6 | Create closeout deliverables tracker | GCC / PM | Closed | Div 01 closeout requirements
SECTION: Open Questions
Open Questions | OPEN QUESTIONS │ SPECIFICATIONS
Open Questions | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Source
Open Questions | SPEC-Q1 | Is the Appendix B submittal log current with IFC 04/13/2026 specifications? | GCC / VA | Closed |  |  | Submittal tracking gap |  |  | 01 00 00.B
Open Questions | SPEC-Q2 | Which spec sections are assigned to each building assessment package versus site/MCR packages? | GCC / QA | Closed |  |  | PMIS mapping gap |  |  | All
Open Questions | SPEC-Q3 | What is the formal commissioning authority workflow for communications and OIT acceptance? | CxA / OIT | Closed |  |  | Turnover acceptance gap |  |  | 01 91 / 27 08
Open Questions | SPEC-Q4 | Are ICRA/PCRA permits required for each TR/TE room even for minor telecom enclosure work? | VA ICRA / GCC Safety | Closed |  |  | Safety/compliance gap |  |  | 01 00 00.C/D
Open Questions | SPEC-Q5 | How are special inspections and testing lab services being tracked against each spec requirement? | GCC QA / SI | Closed |  |  | Inspection gap |  |  | 01 45 29/35
Open Questions | SPEC-Q6 | What is the standardized acceptance package for each telecom room/enclosure? | OIT / Telecom | Closed |  |  | Inconsistent telecom acceptance |  |  | Div 27
Open Questions | SPEC-Q7 | Which systems require third-party commissioning reports before VA acceptance? | CxA / COR | Closed |  |  | Turnover risk |  |  | 01 91 / MEP
Open Questions | SPEC-Q8 | What are the minimum required electrical tests for telecom UPS/PDU and room power? | Electrical / Cx | Closed |  |  | Power readiness gap |  |  | 26 33 53.10
Open Questions | SPEC-Q9 | What are the required firestop documentation formats for site and building penetrations? | Firestop / QA | Closed |  |  | Firestop acceptance gap |  |  | 07 84 00
Open Questions | SPEC-Q10 | How will record drawings/as-builts be collected for site fiber and each building tie-in? | GCC / Telecom | Closed |  |  | As-built gap |  |  | 27 / SITE
SECTION: Deliverables
Deliverables | DELIVERABLES / DOCUMENTATION LOG
Deliverables | Doc ID | Area | Deliverable | Owner | Timing | Status | Spec Reference | PMIS Use | Applies To
Deliverables | DOC-001 | All | Approved submittal register | GCC | Before install | Open | Appendix B / 01 33 23 | Required to track approved products | All
Deliverables | DOC-002 | All | Daily QC reports and deficiency/NCR logs | GCC QA | Daily/weekly | Open | 01 45 00 | Needed for PMIS evidence | All
Deliverables | DOC-003 | All | ICRA/PCRA permits and inspections | GCC Safety / VA | Before/during work | Open | 01 00 00.C/D | Safety compliance evidence | Interior/Site
Deliverables | DOC-004 | All | Commissioning plan/checklists/issues log | CxA | Startup/turnover | Open | 01 91 00 | System acceptance evidence | MEP/FP/Comm/Security/Site
Deliverables | DOC-005 | Telecom | Copper and fiber certification tests | Telecom | Before active connection | Open | 27 08 / 27 10 / 27 13 / 27 15 | OIT acceptance evidence | All telecom
Deliverables | DOC-006 | Electrical | UPS/PDU/SPD/startup/load test records | Electrical | Before energization/turnover | Open | 26 33 / 26 43 | Power acceptance evidence | TR/MCR
Deliverables | DOC-007 | HVAC | TAB/startup/DDC/BACnet/high-temp alarm evidence | Mechanical | Before room acceptance | Open | 23 05 / 23 08 / 23 09 / 23 81 | Cooling readiness evidence | TR/MCR
Deliverables | DOC-008 | Fire/Life Safety | Fire alarm, sprinkler, clean-agent and firestop acceptance | FP/FA/Firestop | Before turnover | Open | 07 84 / 21 / 28 31 | Life safety acceptance | TR/MCR
Deliverables | DOC-009 | Site | Ductbank, utility locate, fiber route and restoration photos/as-builts | Civil/Telecom | Before backfill/turnover | Open | 31-33 / 27 | Site acceptance evidence | SITE
Deliverables | DOC-010 | Closeout | O&M manuals, warranties, training, record drawings | GCC | Turnover | Open | Div 01 closeout | Final closeout package | All
SECTION: Source Notes
Source Notes | SOURCE NOTES │ SPECIFICATIONS PDF REFERENCE
Source Notes | Source | Filename / Section | Page(s) | Relevant Content | Use in Workbook | Notes
Source Notes | PDF | Project Specifications cover | 1 | Department of Veterans Affairs, Project 518-22-700, EHRM Infrastructure Upgrades - Bedford VAMC, IFC project specifications dated 04/13/2026 | Project identity | Uploaded PDF
Source Notes | PDF | Table of Contents | 3 | Division 01 General Requirements and appendices including OIT standards, submittal log, ICRA, PCRA, ACM/LCP, GPRS and geotechnical/boring reports | General Reqs / Spec Matrix | TOC page 1
Source Notes | PDF | Table of Contents | 4 | Architectural divisions including thermal/moisture protection, firestopping, openings and finishes | Spec Matrix | TOC page 2
Source Notes | PDF | Table of Contents | 5 | Fire suppression, plumbing, HVAC and integrated automation sections including clean agent, commissioning, DDC and computer-room air conditioners | MEP / Commissioning | TOC page 3
Source Notes | PDF | Table of Contents | 6 | Electrical, Communications and Electronic Safety/Security sections including telecom UPS, Division 27, PACS and video surveillance | Electrical / Div27 / Security | TOC page 4
Source Notes | PDF | Table of Contents | 7 | Fire detection/alarm, earthwork, exterior improvements and utilities sections | Civil / Site / Fire Alarm | TOC page 5
Source Notes | PDF | Bid Form | 9 | Bid form and base bid/alternate/unit price structure | Cost/contract awareness | Not used for detailed cost
Source Notes | PDF | Construction Estimate Breakdown | 15 | CLIN 00 base bid estimate breakdown template by division and line item | Cost breakdown reference | Visible table page

## _Command_Source (hidden)
Building_ID | Assessment_Sheet | Display_Label
01 | B01_Assessment | B01
02 | B02_Assessment | B02
03 | B03_Assessment | B03
04 | B04_Assessment | B04
05 | B05_Assessment | B05
06 | B06_Assessment | B06
07 | B07_Assessment | B07
08 | B08_Assessment | B08
09 | B09_Assessment | B09
10 | B10_Assessment | B10
12 | B12_Assessment | B12
13 | B13_Assessment | B13
14 | B14_Assessment | B14
15 | B15_Assessment | B15
16 | B16_Assessment | B16
17 | B17_Assessment | B17
18 | B18_Assessment | B18
20 | B20_Assessment | B20
21 | B21_Assessment | B21
22 | B22_Assessment | B22
33 | B33_Assessment | B33
61 | B61_Assessment | B61
62 | B62_TR_Assessment | B62
70 | B70_TR_Assessment | B70
78 | B78_Assessment | B78
80 | B80_Assessment | B80
82 | B82_Assessment | B82
BCH | BCH_Assessment | BCH
MCR | MCR_Assessment | MCR
SPEC | SPEC_Assessment | SPEC
Campus | Campus | Campus
SITE | SITE_Assesment | SITE

## _Assessment_Full_View (hidden)
Building_ID | Seq | Source_Sheet | Source_Row | Section | Row_Type | Col_A | Col_B | Col_C | Col_D | Col_E | Col_F | Col_G | Col_H | Col_I | Col_J | Key
01 | 1 | B01_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦1
01 | 2 | B01_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 01¦2
01 | 3 | B01_Assessment | 10 | 1. ROOM INVENTORY | DATA | 01 | 107 | First | New Telecom Room build area | Telecom Room | 1 | 1 | Verify | 01A-401 / 01E-101 / 01E-601 / 01E-701 / 01T-101 / 01T-604 / 01T-605 / 01T-701 | Primary Building 01 TR. Plans identify Room 107 as new TR with Rack ID TR01-107-1, one new 4-post rack plus future rack, 5kW UPS, future/zone PDU, network switches, 48-port Cat6A patch panels, 24-port Cat5e patch panel, Fiber LIU, panels B01-TR107A/B, IU-1-01/CU-1-01 cooling, camera 107-CAM-1, and 161 total ports with 10% allowance. | 01¦3
01 | 4 | B01_Assessment | 11 | 1. ROOM INVENTORY | DATA | 01 | B02 | Basement | Existing telecom room / racks | Existing telecom transition point | 3 | 0 | Verify | 01T-100 / 01T-604 / 01R-900 | Existing Basement Telecom Room B02 with two 2-post floor racks and one wall TE. Existing equipment includes open rack, UPS on floor, Tripp Lite Smart Pro UPS, Tera Max/Nokia/Baseband/IRU equipment, Corning LANscape, Cisco, and Ortronics 24-port patch panels. Protect active services and transfer devices as required. | 01¦4
01 | 5 | B01_Assessment | 12 | 1. ROOM INVENTORY | DATA | 01 | 138 | First | Existing telecom room / patch panels | Existing telecom transition point | 3 | 0 | Verify | 01T-101 / 01T-604 / 01R-900 | Existing First-Level Telecom Room 138 with existing patch panels, APC UPS floor, Cisco, Corning LANscape and Ortronics 24/48-port patch panels. Protect active services and verify migration to Room 107. | 01¦5
01 | 6 | B01_Assessment | 13 | 1. ROOM INVENTORY | DATA | 01 | 282 | Second | Existing telecom room / racks | Existing telecom transition point | 2 | 0 | Verify | 01T-101 / 01T-605 / 01R-900 | Existing Second-Level Telecom Room 282 with two 2-post floor racks, Cisco switches, cable managers, legacy Ortronics 24/48-port patch panels, Corning LANscape and APC 12-port equipment. Protect active services during Room 107 cutover. | 01¦6
01 | 7 | B01_Assessment | 14 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦7
01 | 8 | B01_Assessment | 15 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦8
01 | 9 | B01_Assessment | 16 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 01¦9
01 | 10 | B01_Assessment | 17 | 2. ROOM READINESS | DATA | 107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New TR. Verify rated wall/smoke barrier conditions, door/access-control hardware, ceiling/deck, floor sealer, rack/future rack clearances, wall backing, cable tray, fiber path A/B, and working clearances around rack, panels and IU. | 01¦10
01 | 11 | B01_Assessment | 18 | 2. ROOM READINESS | DATA | B02 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing basement telecom room. Verify active equipment, rack access, existing UPS power, wall TE, pathway and transfer/abandonment scope. | 01¦11
01 | 12 | B01_Assessment | 19 | 2. ROOM READINESS | DATA | 138 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing first-level telecom transition point. Verify rack/panel condition, active services, UPS, patching and cable transfer scope. | 01¦12
01 | 13 | B01_Assessment | 20 | 2. ROOM READINESS | DATA | 282 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing second-level telecom transition point. Verify rack access, active services, pathway/riser and final condition after cutover. | 01¦13
01 | 14 | B01_Assessment | 21 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦14
01 | 15 | B01_Assessment | 22 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦15
01 | 16 | B01_Assessment | 23 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 01¦16
01 | 17 | B01_Assessment | 24 | 3. FIRE PROTECTION | DATA | 107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems. | 01¦17
01 | 18 | B01_Assessment | 25 | 3. FIRE PROTECTION | DATA | B02 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | 01¦18
01 | 19 | B01_Assessment | 26 | 3. FIRE PROTECTION | DATA | 138 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes. | 01¦19
01 | 20 | B01_Assessment | 27 | 3. FIRE PROTECTION | DATA | 282 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place. | 01¦20
01 | 21 | B01_Assessment | 28 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦21
01 | 22 | B01_Assessment | 29 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦22
01 | 23 | B01_Assessment | 30 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 01¦23
01 | 24 | B01_Assessment | 31 | 4. HVAC / COOLING | DATA | 107 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup. | 01¦24
01 | 25 | B01_Assessment | 32 | 4. HVAC / COOLING | DATA | B02 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration. | 01¦25
01 | 26 | B01_Assessment | 33 | 4. HVAC / COOLING | DATA | 138 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear. | 01¦26
01 | 27 | B01_Assessment | 34 | 4. HVAC / COOLING | DATA | 282 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating. | 01¦27
01 | 28 | B01_Assessment | 35 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦28
01 | 29 | B01_Assessment | 36 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦29
01 | 30 | B01_Assessment | 37 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 01¦30
01 | 31 | B01_Assessment | 38 | 5. ELECTRICAL / UPS | DATA | 107 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B01-TR107A / B01-TR107B | Verify | Verify | Verify | Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation. | 01¦31
01 | 32 | B01_Assessment | 39 | 5. ELECTRICAL / UPS | DATA | B02 | Existing | Existing UPS on floor / Tripp Lite Smart Pro UPS | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements. | 01¦32
01 | 33 | B01_Assessment | 40 | 5. ELECTRICAL / UPS | DATA | 138 | Existing | Existing APC UPS floor | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition. | 01¦33
01 | 34 | B01_Assessment | 41 | 5. ELECTRICAL / UPS | DATA | 282 | Existing | Existing / Verify | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope. | 01¦34
01 | 35 | B01_Assessment | 42 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦35
01 | 36 | B01_Assessment | 43 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦36
01 | 37 | B01_Assessment | 44 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 01¦37
01 | 38 | B01_Assessment | 45 | 6. TELECOMMUNICATIONS | DATA | 107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1. | 01¦38
01 | 39 | B01_Assessment | 46 | 6. TELECOMMUNICATIONS | DATA | B02 | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan. | 01¦39
01 | 40 | B01_Assessment | 47 | 6. TELECOMMUNICATIONS | DATA | 138 | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence. | 01¦40
01 | 41 | B01_Assessment | 48 | 6. TELECOMMUNICATIONS | DATA | 282 | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway. | 01¦41
01 | 42 | B01_Assessment | 49 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦42
01 | 43 | B01_Assessment | 50 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦43
01 | 44 | B01_Assessment | 51 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 01¦44
01 | 45 | B01_Assessment | 52 | 7. SECURITY / PACS / CCTV | DATA | 107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical/telecom plans show new access control, power supply/battery backup for PACS, HDP12/FIPS-compliant PIV-ready card reader with PIN pad, and camera 107-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration and door hardware coordination. | 01¦45
01 | 46 | B01_Assessment | 53 | 7. SECURITY / PACS / CCTV | DATA | B02 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/CCTV equipment and any retained cameras. Maintain camera angles where existing security cameras are recabled. | 01¦46
01 | 47 | B01_Assessment | 54 | 7. SECURITY / PACS / CCTV | DATA | 138 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/access conditions and protection-in-place during rack transfer. | 01¦47
01 | 48 | B01_Assessment | 55 | 7. SECURITY / PACS / CCTV | DATA | 282 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify second-level existing security/CCTV impacts during cabling and equipment transfer. | 01¦48
01 | 49 | B01_Assessment | 56 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦49
01 | 50 | B01_Assessment | 57 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦50
01 | 51 | B01_Assessment | 58 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 01¦51
01 | 52 | B01_Assessment | 59 | 8. OWNER RISKS | DATA | B01-R1 | All | Existing conditions for Room 107 and transition rooms B02/138/282 not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | B01 has multiple existing telecom rooms and a new TR buildout. | 01¦52
01 | 53 | B01_Assessment | 60 | 8. OWNER RISKS | DATA | B01-R2 | B02/138/282 | Existing equipment may remain active during transfer to Room 107 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | Existing rack elevations show multiple active switches, LIUs, patch panels and UPS equipment. | 01¦53
01 | 54 | B01_Assessment | 61 | 8. OWNER RISKS | DATA | B01-R3 | 107 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat, humidity and high-temp alarms | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 01¦54
01 | 55 | B01_Assessment | 62 | 8. OWNER RISKS | DATA | B01-R4 | 107 | B01-TR107A/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panels, breakers, receptacles, SPD, labels, 30-day load measurement and LOTO needs | Electrical / GCC | Closed | Electrical schedules call for new panels and 30-day load measurement prior to panel work. | 01¦55
01 | 56 | B01_Assessment | 63 | 8. OWNER RISKS | DATA | B01-R5 | All | 394 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 58 ft, first 212 ft, second 124 ft. | 01¦56
01 | 57 | B01_Assessment | 64 | 8. OWNER RISKS | DATA | B01-R6 | All | Telecom/fiber cutover could affect active hospital communications across basement/first/second levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | RM107 supports 161 total ports including allowance and transfer from multiple existing rooms. | 01¦57
01 | 58 | B01_Assessment | 65 | 8. OWNER RISKS | DATA | B01-R7 | 107 | PACS/CCTV/door hardware coordination may not be ready at room acceptance | High | Medium | 6 | Verify access-control rough-in, power supply/battery backup, reader, electric strike, door position, camera and VMS/PACS test records | Security / Electrical | Closed | Plans include new PACS and 107-CAM-1. | 01¦58
01 | 59 | B01_Assessment | 66 | 8. OWNER RISKS | DATA | B01-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | 50-sheet IFC package includes full discipline scope and third-party inspections requirement. | 01¦59
01 | 60 | B01_Assessment | 67 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦60
01 | 61 | B01_Assessment | 68 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦61
01 | 62 | B01_Assessment | 69 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 01¦62
01 | 63 | B01_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B01-Q1 | Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 01¦63
01 | 64 | B01_Assessment | 71 | 9. OPEN QUESTIONS | DATA | B01-Q2 | What active services are currently fed from existing Rooms B02, 138 and 282? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 01¦64
01 | 65 | B01_Assessment | 72 | 9. OPEN QUESTIONS | DATA | B01-Q3 | What equipment from existing racks transfers to new Room 107 versus remains/decommissions? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0 | 01¦65
01 | 66 | B01_Assessment | 73 | 9. OPEN QUESTIONS | DATA | B01-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 01¦66
01 | 67 | B01_Assessment | 74 | 9. OPEN QUESTIONS | DATA | B01-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 01¦67
01 | 68 | B01_Assessment | 75 | 9. OPEN QUESTIONS | DATA | B01-Q6 | Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 01¦68
01 | 69 | B01_Assessment | 76 | 9. OPEN QUESTIONS | DATA | B01-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 01¦69
01 | 70 | B01_Assessment | 77 | 9. OPEN QUESTIONS | DATA | B01-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 01¦70
01 | 71 | B01_Assessment | 78 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦71
01 | 72 | B01_Assessment | 79 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦72
01 | 73 | B01_Assessment | 80 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 01¦73
01 | 74 | B01_Assessment | 81 | 10. PHOTO LOG | DATA | B01-P001 | 107 | Existing / New Condition | Room 107 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, fiber path A/B, cable tray and penetrations | 0 | Paul | 0 | B01-R1/B01-R3 | Closed | 0 | 01¦74
01 | 75 | B01_Assessment | 82 | 10. PHOTO LOG | DATA | B01-P002 | B02 | Existing Equipment | Basement existing telecom room B02 racks, wall TE, Cisco/Nokia/Baseband/IRU/Corning/Ortronics equipment, UPS and cable entries | 0 | Paul | 0 | B01-R1/B01-R2 | Closed | 0 | 01¦75
01 | 76 | B01_Assessment | 83 | 10. PHOTO LOG | DATA | B01-P003 | 138 | Existing Equipment | First-level existing telecom room 138 racks, patch panels, Cisco, Corning, APC UPS and active service labels | 0 | Paul | 0 | B01-R2/B01-R6 | Closed | 0 | 01¦76
01 | 77 | B01_Assessment | 84 | 10. PHOTO LOG | DATA | B01-P004 | 282 | Existing Equipment | Second-level existing telecom room 282 racks, Cisco switches, Ortronics patch panels, cable managers and active service labels | 0 | Paul | 0 | B01-R2/B01-R6 | Closed | 0 | 01¦77
01 | 78 | B01_Assessment | 85 | 10. PHOTO LOG | DATA | B01-P005 | 107 | HVAC | IU-1-01/CU-1-01, condensate pump/line, thermostat, BACnet adapter, disconnects, FMS alarm points and power source | 0 | Paul | 0 | B01-R3 | Closed | 0 | 01¦78
01 | 79 | B01_Assessment | 86 | 10. PHOTO LOG | DATA | B01-P006 | 107 | Electrical | B01-TR107A/B panels, rack receptacles, breakers, SPD, PACS power supply, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B01-R4/B01-R7 | Closed | 0 | 01¦79
01 | 80 | B01_Assessment | 87 | 10. PHOTO LOG | DATA | B01-P007 | All | Cable Tray / Firestop | Basement/first/second cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B01-R5 | Closed | 0 | 01¦80
01 | 81 | B01_Assessment | 88 | 10. PHOTO LOG | DATA | B01-P008 | 107 / Existing Rooms | Telecom / Security | New rack/future rack, Fiber LIU, Cat6A, patch panels, labels/test records, 107-CAM-1, PACS and existing rack transfer work | 0 | Paul | 0 | B01-R6/B01-R8 | Closed | 0 | 01¦81
01 | 82 | B01_Assessment | 89 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 01¦82
02 | 1 | B02_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦1
02 | 2 | B02_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 02¦2
02 | 3 | B02_Assessment | 10 | 1. ROOM INVENTORY | DATA | 02 | 141 | First | Existing first-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-401 / 02E-101 / 02E-401 / 02E-601 / 02E-701 / 02T-101 / 02T-401 / 02T-604 / 02T-701 | Primary first-level TR. Schedules identify RM141 with 211 WAO total, 215 active ports, 322 scheduled ports and 354 total ports with 10% allowance. Rack IDs TR01-141-01/02. Enlarged plan shows Room 141 new and demo scope, 174-CAM-01, existing patch panels/fire alarm cabinet relocated to RM141 and future rack space. | 02¦3
02 | 4 | B02_Assessment | 11 | 1. ROOM INVENTORY | DATA | 02 | 236 | Second | Existing second-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-401 / 02E-102 / 02E-402 / 02E-701 / 02T-102 / 02T-401 / 02T-604 / 02T-702 | Second-level TR. Schedules identify RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approximately 345 ports with 10% allowance. Rack IDs TR01-236-01/02. Enlarged plans show 236-CAM-01 and new/demolition work at Room 236 / existing Room 282. | 02¦4
02 | 5 | B02_Assessment | 12 | 1. ROOM INVENTORY | DATA | 02 | 342 | Third | Third-level telecom room / expanded TR work area | Telecom Room | 2 | 1 | Verify | 02A-402 / 02E-103 / 02E-402 / 02E-701 / 02T-103 / 02T-401 / 02T-604 / 02T-703 | Third-level TR. Schedules identify RM342 with 274 WAO total, 96 active ports, 353 scheduled ports and 388 total ports with 10% allowance. Rack IDs TR01-342-01/02. Enlarged plans show 342-CAM-01, 342A-CK-A and new rack scope. | 02¦5
02 | 6 | B02_Assessment | 13 | 1. ROOM INVENTORY | DATA | 02 | B-06 | Basement | Existing telecom room / legacy rack equipment | Existing telecom transition point | 1 | 0 | Verify | 02T-100 / 02T-604 / 02R-900 | Existing Basement Telecom Room B-06 with legacy Ortronics 48-port patch panels. Photo reference identifies B-06 existing telecom room. Protect active services and verify transfer/abandonment scope. | 02¦6
02 | 7 | B02_Assessment | 14 | 1. ROOM INVENTORY | DATA | 02 | Existing 141 / 236 | First / Second | Existing telecom room equipment / transition points | Existing telecom transition points | 4 | 0 | Verify | 02T-604 / 02R-900 | Existing First-Level Telecom Room 141 and Second-Level Existing Telecom Room 236 shown in photo references/rack elevations. Existing devices and racks are to be protected or transferred per notes. | 02¦7
02 | 8 | B02_Assessment | 15 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦8
02 | 9 | B02_Assessment | 16 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦9
02 | 10 | B02_Assessment | 17 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 02¦10
02 | 11 | B02_Assessment | 18 | 2. ROOM READINESS | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify rated walls/smoke barriers, door/access-control hardware, ceiling/deck, floor finish, rack/future rack clearance, wall backing, cable tray, fiber path A/B, and working clearances around racks/panels/IU. | 02¦11
02 | 12 | B02_Assessment | 19 | 2. ROOM READINESS | DATA | 236 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR; verify rated construction, door/PACS, rack clearances, riser penetrations, cable tray conflicts and final room layout around existing/demo conditions. | 02¦12
02 | 13 | B02_Assessment | 20 | 2. ROOM READINESS | DATA | 342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Third-level TR; verify rated construction, door/PACS, rack clearances, cable tray, firestop, ceiling coordination and future rack space. | 02¦13
02 | 14 | B02_Assessment | 21 | 2. ROOM READINESS | DATA | B-06 / existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing telecom transition rooms must remain operational until cutover. Verify active equipment inventory, labels, access and final transfer/decommission scope. | 02¦14
02 | 15 | B02_Assessment | 22 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦15
02 | 16 | B02_Assessment | 23 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦16
02 | 17 | B02_Assessment | 24 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 02¦17
02 | 18 | B02_Assessment | 25 | 3. FIRE PROTECTION | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. | 02¦18
02 | 19 | B02_Assessment | 26 | 3. FIRE PROTECTION | DATA | 236 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping. | 02¦19
02 | 20 | B02_Assessment | 27 | 3. FIRE PROTECTION | DATA | 342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping. | 02¦20
02 | 21 | B02_Assessment | 28 | 3. FIRE PROTECTION | DATA | B-06 / existing rooms | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | 02¦21
02 | 22 | B02_Assessment | 29 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦22
02 | 23 | B02_Assessment | 30 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦23
02 | 24 | B02_Assessment | 31 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 02¦24
02 | 25 | B02_Assessment | 32 | 4. HVAC / COOLING | DATA | 141 | CU-1-01 / TR cooling assignment verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms. | 02¦25
02 | 26 | B02_Assessment | 33 | 4. HVAC / COOLING | DATA | 236 | CU-2-01 / TR cooling assignment verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm. | 02¦26
02 | 27 | B02_Assessment | 34 | 4. HVAC / COOLING | DATA | 342 | CU-3-01 / TR cooling assignment verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration. | 02¦27
02 | 28 | B02_Assessment | 35 | 4. HVAC / COOLING | DATA | B-06 / existing rooms | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete. | 02¦28
02 | 29 | B02_Assessment | 36 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦29
02 | 30 | B02_Assessment | 37 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦30
02 | 31 | B02_Assessment | 38 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 02¦31
02 | 32 | B02_Assessment | 39 | 5. ELECTRICAL / UPS | DATA | 141 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B02-TR141A / B02-TR141B | Verify | Verify | Verify | Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels. | 02¦32
02 | 33 | B02_Assessment | 40 | 5. ELECTRICAL / UPS | DATA | 236 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B02-TR236A / B02-TR236B | Verify | Verify | Verify | Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping. | 02¦33
02 | 34 | B02_Assessment | 41 | 5. ELECTRICAL / UPS | DATA | 342 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B02-TR342A / B02-TR342B | Verify | Verify | Verify | Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits. | 02¦34
02 | 35 | B02_Assessment | 42 | 5. ELECTRICAL / UPS | DATA | B-06 / existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs. | 02¦35
02 | 36 | B02_Assessment | 43 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦36
02 | 37 | B02_Assessment | 44 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦37
02 | 38 | B02_Assessment | 45 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 02¦38
02 | 39 | B02_Assessment | 46 | 6. TELECOMMUNICATIONS | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray. | 02¦39
02 | 40 | B02_Assessment | 47 | 6. TELECOMMUNICATIONS | DATA | 236 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope. | 02¦40
02 | 41 | B02_Assessment | 48 | 6. TELECOMMUNICATIONS | DATA | 342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count. | 02¦41
02 | 42 | B02_Assessment | 49 | 6. TELECOMMUNICATIONS | DATA | B-06 / existing rooms | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover. | 02¦42
02 | 43 | B02_Assessment | 50 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦43
02 | 44 | B02_Assessment | 51 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦44
02 | 45 | B02_Assessment | 52 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 02¦45
02 | 46 | B02_Assessment | 53 | 7. SECURITY / PACS / CCTV | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Plans show 174-CAM-01 associated with the first-level TR area and PACS/security requirements. Verify camera/VMS integration, access controller/power supply, CR/RX/DC/ES/MD and door hardware. | 02¦46
02 | 47 | B02_Assessment | 54 | 7. SECURITY / PACS / CCTV | DATA | 236 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Plans show 236-CAM-01. Verify camera/VMS integration, access control, door hardware, motion/detection devices and power. | 02¦47
02 | 48 | B02_Assessment | 55 | 7. SECURITY / PACS / CCTV | DATA | 342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Plans show 342-CAM-01 and 342A-CK-A. Verify camera/VMS integration and access control/security rough-in. | 02¦48
02 | 49 | B02_Assessment | 56 | 7. SECURITY / PACS / CCTV | DATA | B-06 / existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Maintain existing camera angles when re-cabling and protect existing PACS/equipment racks during transfer. | 02¦49
02 | 50 | B02_Assessment | 57 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦50
02 | 51 | B02_Assessment | 58 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦51
02 | 52 | B02_Assessment | 59 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 02¦52
02 | 53 | B02_Assessment | 60 | 8. OWNER RISKS | DATA | B02-R1 | All | Existing conditions for Rooms 141/236/342 and existing B-06/141/236 not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | B02 has multiple new TRs and existing transition rooms. | 02¦53
02 | 54 | B02_Assessment | 61 | 8. OWNER RISKS | DATA | B02-R2 | Existing rooms | Existing equipment may remain active during transfer to new TRs | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | Existing rack elevations/photos show active legacy rack/patch equipment. | 02¦54
02 | 55 | B02_Assessment | 62 | 8. OWNER RISKS | DATA | B02-R3 | 141/236/342 | Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm each IU/CU serving each TR, power source, condensate route, controls, BACnet, thermostat and high-temp alarms | Mechanical / Electrical | Closed | Electrical schedule references CU-1/2/3-01; assignments must be field verified. | 02¦55
02 | 56 | B02_Assessment | 63 | 8. OWNER RISKS | DATA | B02-R4 | All TRs | B02-TR141/236/342 A/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panels, breakers, receptacles, SPDs, labels, 30-day load measurement and LOTO needs | Electrical / GCC | Closed | Multiple new telecom panels and rack circuits. | 02¦56
02 | 57 | B02_Assessment | 64 | 8. OWNER RISKS | DATA | B02-R5 | All | 2,560 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 303 ft, first 1,069 ft, second 544 ft, third 583 ft, fourth 59 ft. | 02¦57
02 | 58 | B02_Assessment | 65 | 8. OWNER RISKS | DATA | B02-R6 | All | Telecom/fiber cutover could affect active hospital communications across several floors | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | High WAO counts: 211/179/274 WAO across Rooms 141/236/342. | 02¦58
02 | 59 | B02_Assessment | 66 | 8. OWNER RISKS | DATA | B02-R7 | 141/236/342 | PACS/CCTV/door hardware coordination may not be ready at room acceptance | High | Medium | 6 | Verify access-control rough-in, power supply/battery backup, reader, strike, door position, cameras and VMS/PACS test records | Security / Electrical | Closed | Plans include 174-CAM-01, 236-CAM-01, 342-CAM-01. | 02¦59
02 | 60 | B02_Assessment | 67 | 8. OWNER RISKS | DATA | B02-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | 66-sheet IFC package with full discipline scope and third-party inspection requirements. | 02¦60
02 | 61 | B02_Assessment | 68 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦61
02 | 62 | B02_Assessment | 69 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦62
02 | 63 | B02_Assessment | 70 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 02¦63
02 | 64 | B02_Assessment | 71 | 9. OPEN QUESTIONS | DATA | B02-Q1 | Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 02¦64
02 | 65 | B02_Assessment | 72 | 9. OPEN QUESTIONS | DATA | B02-Q2 | What active services are currently fed from existing Rooms B-06, 141 and 236? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 02¦65
02 | 66 | B02_Assessment | 73 | 9. OPEN QUESTIONS | DATA | B02-Q3 | What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0 | 02¦66
02 | 67 | B02_Assessment | 74 | 9. OPEN QUESTIONS | DATA | B02-Q4 | Which IU/CU pair serves each TR and are they on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 02¦67
02 | 68 | B02_Assessment | 75 | 9. OPEN QUESTIONS | DATA | B02-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 02¦68
02 | 69 | B02_Assessment | 76 | 9. OPEN QUESTIONS | DATA | B02-Q6 | Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 02¦69
02 | 70 | B02_Assessment | 77 | 9. OPEN QUESTIONS | DATA | B02-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 02¦70
02 | 71 | B02_Assessment | 78 | 9. OPEN QUESTIONS | DATA | B02-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 02¦71
02 | 72 | B02_Assessment | 79 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦72
02 | 73 | B02_Assessment | 80 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦73
02 | 74 | B02_Assessment | 81 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 02¦74
02 | 75 | B02_Assessment | 82 | 10. PHOTO LOG | DATA | B02-P001 | 141 | Existing / New Condition | Room 141 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 174-CAM-01, penetrations and demo/relocation conditions | 0 | Paul | 0 | B02-R1/B02-R3 | Closed | 0 | 02¦75
02 | 76 | B02_Assessment | 83 | 10. PHOTO LOG | DATA | B02-P002 | 236 | Existing / New Condition | Room 236 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 236-CAM-01, penetrations and existing transfer conditions | 0 | Paul | 0 | B02-R1/B02-R6 | Closed | 0 | 02¦76
02 | 77 | B02_Assessment | 84 | 10. PHOTO LOG | DATA | B02-P003 | 342 | Existing / New Condition | Room 342 walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, 342-CAM-01, penetrations and 342A-CK-A | 0 | Paul | 0 | B02-R1/B02-R7 | Closed | 0 | 02¦77
02 | 78 | B02_Assessment | 85 | 10. PHOTO LOG | DATA | B02-P004 | B-06 | Existing Equipment | Basement existing telecom room B-06 legacy rack/patch panels, active service labels and cable entries | 0 | Paul | 0 | B02-R2 | Closed | 0 | 02¦78
02 | 79 | B02_Assessment | 86 | 10. PHOTO LOG | DATA | B02-P005 | Existing 141 / 236 | Existing Equipment | Existing first/second-level telecom rooms 141 and 236, existing patch panels, relocated/removed equipment and fire alarm cabinet conditions | 0 | Paul | 0 | B02-R2/B02-R6 | Closed | 0 | 02¦79
02 | 80 | B02_Assessment | 87 | 10. PHOTO LOG | DATA | B02-P006 | All TRs | Electrical / HVAC | B02-TR141/236/342 A/B panels, rack receptacles, breakers, SPD, UPS/PDU, CU/IU equipment, condensate, disconnects and labels | 0 | Paul | 0 | B02-R3/B02-R4 | Closed | 0 | 02¦80
02 | 81 | B02_Assessment | 88 | 10. PHOTO LOG | DATA | B02-P007 | All | Cable Tray / Firestop | Basement/first/second/third/fourth cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B02-R5 | Closed | 0 | 02¦81
02 | 82 | B02_Assessment | 89 | 10. PHOTO LOG | DATA | B02-P008 | All TRs | Telecom / Security | Racks, Fiber LIU, Cat6A, patch panels, labels/test records, cameras, PACS and existing rack transfer work | 0 | Paul | 0 | B02-R6/B02-R8 | Closed | 0 | 02¦82
02 | 83 | B02_Assessment | 90 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 02¦83
03 | 1 | B03_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦1
03 | 2 | B03_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 03¦2
03 | 3 | B03_Assessment | 10 | 1. ROOM INVENTORY | DATA | 03 | 101E | First | New telecom room buildout / relocated TR function | Telecom Room | 2 | 1 | Verify | 03A-401 / 03E-101 / 03E-401 / 03E-601 / 03E-701 / 03T-101 / 03T-401 / 03T-604 / 03T-701 | Primary Building 03 TR. Schedules identify RM101E with 143 WAO total, 213 active ports, 187 scheduled ports, 206 total ports with 10% allowance, Rack IDs TR01-101E-1 and TR01-101E-2, 5kW UPS, Zone PDU, fiber LIU, Cat6A patch panels, and future rack/switch capacity. | 03¦3
03 | 4 | B03_Assessment | 11 | 1. ROOM INVENTORY | DATA | 03 | 107 | Basement | Existing telecom room / legacy rack equipment | Existing telecom transition point | 1 | 0 | Verify | 03T-100 / 03T-403 / 03T-604 / 03R-900 | Existing Basement Telecom Room 107. Rack elevation identifies Building 3 existing B3-LB-B13-TC-FIBER rack with UPS on floor, Cisco switch, legacy 48-port patch panels, and fiber LIU wall-mounted. 03T-403 provides Room 107 inventory list for reference. | 03¦4
03 | 5 | B03_Assessment | 12 | 1. ROOM INVENTORY | DATA | 03 | 101C | First | Existing DMARC / telecom room | Existing DMARC transition point | 1 | 0 | Verify | 03T-101 / 03T-401 / 03T-604 / 03R-900 | First-floor existing DMARC Room 101C / telecom room. Enlarged plan shows existing/removal patch panels, existing branch panel, telecom cabinet, 101C-CAM-01, 101C-CK-A, 101C-A/B/C/D and AP locations. Protect active DMARC/fiber until new service is operational. | 03¦5
03 | 6 | B03_Assessment | 13 | 1. ROOM INVENTORY | DATA | 03 | 108 / 107A / 101C related WAO areas | First | Work area outlets and WAP/camera locations | WAO recabling / device support | 0 | 0 | Verify | 03T-101 / 03T-701 | WAO schedule includes first-level outlets such as 108-A/B/C, 108-CK-A, 108-AP-A, 107A-AP-A, 101C-CAM-01, 101C-A/B/C/D and AP locations served from TR01-101E-1/2. | 03¦6
03 | 7 | B03_Assessment | 14 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦7
03 | 8 | B03_Assessment | 15 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦8
03 | 9 | B03_Assessment | 16 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 03¦9
03 | 10 | B03_Assessment | 17 | 2. ROOM READINESS | DATA | 101E | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New/renovated TR. Verify rated walls/smoke barriers, door/access-control hardware, ceiling/deck, floor finish, rack/future rack clearances, wall backing, cable tray, fiber path A/B, and working clearances around rack, panels and cooling equipment. | 03¦10
03 | 11 | B03_Assessment | 18 | 2. ROOM READINESS | DATA | 107 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing basement telecom room must remain operational until cutover. Verify active equipment, rack access, existing UPS on floor, wall/floor rack conditions, and transfer/abandonment scope. | 03¦11
03 | 12 | B03_Assessment | 19 | 2. ROOM READINESS | DATA | 101C | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing DMARC/telecom transition point; verify active provider/fiber/DMARC services, branch panel, patch panels, cabinet and protection-in-place. | 03¦12
03 | 13 | B03_Assessment | 20 | 2. ROOM READINESS | DATA | WAO Areas | Existing / Verify | Existing / Verify | Existing / Verify | Verify | N/A / Verify | Verify | Verify | Verify | Verify existing conduit reuse, surface raceway where needed, 40% fill, WAP protection-in-place, access above ceilings, and infection-control controls. | 03¦13
03 | 14 | B03_Assessment | 21 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦14
03 | 15 | B03_Assessment | 22 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦15
03 | 16 | B03_Assessment | 23 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 03¦16
03 | 17 | B03_Assessment | 24 | 3. FIRE PROTECTION | DATA | 101E | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. | 03¦17
03 | 18 | B03_Assessment | 25 | 3. FIRE PROTECTION | DATA | 107 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse. | 03¦18
03 | 19 | B03_Assessment | 26 | 3. FIRE PROTECTION | DATA | 101C | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer. | 03¦19
03 | 20 | B03_Assessment | 27 | 3. FIRE PROTECTION | DATA | WAO Areas | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A | Verify | Verify | Verify | Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations. | 03¦20
03 | 21 | B03_Assessment | 28 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦21
03 | 22 | B03_Assessment | 29 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦22
03 | 23 | B03_Assessment | 30 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 03¦23
03 | 24 | B03_Assessment | 31 | 4. HVAC / COOLING | DATA | 101E | CU-01 / TR cooling assignment verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm. | 03¦24
03 | 25 | B03_Assessment | 32 | 4. HVAC / COOLING | DATA | 107 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete. | 03¦25
03 | 26 | B03_Assessment | 33 | 4. HVAC / COOLING | DATA | 101C | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains. | 03¦26
03 | 27 | B03_Assessment | 34 | 4. HVAC / COOLING | DATA | WAO Areas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements. | 03¦27
03 | 28 | B03_Assessment | 35 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦28
03 | 29 | B03_Assessment | 36 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦29
03 | 30 | B03_Assessment | 37 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 03¦30
03 | 31 | B03_Assessment | 38 | 5. ELECTRICAL / UPS | DATA | 101E | Verify | 5 kW / 208V rack UPS | Verify | Verify | B03-TR101CA / B03-TR101CB | Verify | Verify | Verify | Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements. | 03¦31
03 | 32 | B03_Assessment | 39 | 5. ELECTRICAL / UPS | DATA | 107 | Existing | UPS on floor | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements. | 03¦32
03 | 33 | B03_Assessment | 40 | 5. ELECTRICAL / UPS | DATA | 101C | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Existing branch panel / B03-TR101CA/B transition | Verify | Verify | Verify | Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer. | 03¦33
03 | 34 | B03_Assessment | 41 | 5. ELECTRICAL / UPS | DATA | WAO Areas | N/A | N/A | N/A | N/A | Existing / new outlet circuits as needed | N/A | Verify labels | Verify | Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations. | 03¦34
03 | 35 | B03_Assessment | 42 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦35
03 | 36 | B03_Assessment | 43 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦36
03 | 37 | B03_Assessment | 44 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 03¦37
03 | 38 | B03_Assessment | 45 | 6. TELECOMMUNICATIONS | DATA | 101E | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2. | 03¦38
03 | 39 | B03_Assessment | 46 | 6. TELECOMMUNICATIONS | DATA | 107 | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover. | 03¦39
03 | 40 | B03_Assessment | 47 | 6. TELECOMMUNICATIONS | DATA | 101C | Existing / Transfer | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted. | 03¦40
03 | 41 | B03_Assessment | 48 | 6. TELECOMMUNICATIONS | DATA | WAO Areas | N/A | Verify route | N/A | N/A | Verify | Verify | Verify | Verify | Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced. | 03¦41
03 | 42 | B03_Assessment | 49 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦42
03 | 43 | B03_Assessment | 50 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦43
03 | 44 | B03_Assessment | 51 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 03¦44
03 | 45 | B03_Assessment | 52 | 7. SECURITY / PACS / CCTV | DATA | 101E | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Plans require PACS for TR doors and electrical details include access-controlled door rough-in. Verify access controller, power supply/battery backup, CR/RX/DC/ES/MD devices, reader, strike and door hardware coordination. | 03¦45
03 | 46 | B03_Assessment | 53 | 7. SECURITY / PACS / CCTV | DATA | 101C | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | 101C-CAM-01 Verify | Verify | Verify | Verify | Enlarged plan and schedule identify 101C-CAM-01 and 101C-CK-A. Verify camera/VMS integration, existing camera angles and protection-in-place. | 03¦46
03 | 47 | B03_Assessment | 54 | 7. SECURITY / PACS / CCTV | DATA | 107 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/CCTV/PACS impacts during basement telecom room transfer. | 03¦47
03 | 48 | B03_Assessment | 55 | 7. SECURITY / PACS / CCTV | DATA | WAO Areas | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Maintain existing camera angles when re-cabling; verify WAP/security/clock/Centrak devices are relabeled and tested. | 03¦48
03 | 49 | B03_Assessment | 56 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦49
03 | 50 | B03_Assessment | 57 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦50
03 | 51 | B03_Assessment | 58 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 03¦51
03 | 52 | B03_Assessment | 59 | 8. OWNER RISKS | DATA | B03-R1 | All | Existing conditions for Room 101E and transition rooms 107/101C not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | B03 has new TR work tied to existing basement telecom and first-floor DMARC. | 03¦52
03 | 53 | B03_Assessment | 60 | 8. OWNER RISKS | DATA | B03-R2 | 107 / 101C | Existing DMARC/fiber/telecom equipment may remain active during transfer to Room 101E | Critical | Medium | 8 | Document active services, protect in place, identify OIT/provider cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | Existing 107 rack and 101C DMARC/patch panels must not be disrupted before new services are operational. | 03¦53
03 | 54 | B03_Assessment | 61 | 8. OWNER RISKS | DATA | B03-R3 | 101E | Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm CU-01/IU serving Room 101E, power source, condensate, controls, BACnet, thermostat and high-temp alarms | Mechanical / Electrical | Closed | CU-01 is referenced in electrical schedules; mechanical assignment must be verified. | 03¦54
03 | 55 | B03_Assessment | 62 | 8. OWNER RISKS | DATA | B03-R4 | 101E | B03-TR101CA/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panels, breakers, receptacles, SPDs, PXR20 trip units, labels, 30-day load measurement and LOTO needs | Electrical / GCC | Closed | New telecom panels and rack circuits must be proven before acceptance. | 03¦55
03 | 56 | B03_Assessment | 63 | 8. OWNER RISKS | DATA | B03-R5 | All | 961 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 615 ft and first level 346 ft. | 03¦56
03 | 57 | B03_Assessment | 64 | 8. OWNER RISKS | DATA | B03-R6 | All | Telecom/fiber cutover could affect active hospital communications and provider/DMARC services | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT/provider coordination and VA acceptance before active connection | Telecom / OIT | Closed | Room 101E supports 206 total ports with allowance and replacement of basement/first-level WAOs. | 03¦57
03 | 58 | B03_Assessment | 65 | 8. OWNER RISKS | DATA | B03-R7 | 101E / 101C | PACS/CCTV/door hardware coordination may not be ready at room acceptance | High | Medium | 6 | Verify access-control rough-in, power supply/battery backup, reader, strike, door position, 101C-CAM-01 and VMS/PACS test records | Security / Electrical | Closed | Plans identify 101C-CAM-01 and PACS/access control requirements. | 03¦58
03 | 59 | B03_Assessment | 66 | 8. OWNER RISKS | DATA | B03-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | 50-sheet IFC package with full discipline scope and third-party inspection requirements. | 03¦59
03 | 60 | B03_Assessment | 67 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦60
03 | 61 | B03_Assessment | 68 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦61
03 | 62 | B03_Assessment | 69 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 03¦62
03 | 63 | B03_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B03-Q1 | Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 03¦63
03 | 64 | B03_Assessment | 71 | 9. OPEN QUESTIONS | DATA | B03-Q2 | What active services are currently fed from existing Room 107 and DMARC Room 101C? | OIT / Contractor / Provider | Closed | 0 | 0 | Potential communications/provider outage | 0 | 0 | 0 | 03¦64
03 | 65 | B03_Assessment | 72 | 9. OPEN QUESTIONS | DATA | B03-Q3 | What existing equipment transfers to new Room 101E versus remains/decommissions? | OIT / Telecom | Closed | 0 | 0 | Cutover and rack elevation risk | 0 | 0 | 0 | 03¦65
03 | 66 | B03_Assessment | 73 | 9. OPEN QUESTIONS | DATA | B03-Q4 | Which IU/CU pair serves Room 101E and is it on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 03¦66
03 | 67 | B03_Assessment | 74 | 9. OPEN QUESTIONS | DATA | B03-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 03¦67
03 | 68 | B03_Assessment | 75 | 9. OPEN QUESTIONS | DATA | B03-Q6 | Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 03¦68
03 | 69 | B03_Assessment | 76 | 9. OPEN QUESTIONS | DATA | B03-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 03¦69
03 | 70 | B03_Assessment | 77 | 9. OPEN QUESTIONS | DATA | B03-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 03¦70
03 | 71 | B03_Assessment | 78 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦71
03 | 72 | B03_Assessment | 79 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦72
03 | 73 | B03_Assessment | 80 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 03¦73
03 | 74 | B03_Assessment | 81 | 10. PHOTO LOG | DATA | B03-P001 | 101E | Existing / New Condition | Room 101E walls, ceiling/deck, floor, door, racks/future rack, panels, HVAC, cable tray, penetrations, PACS and final TR layout | 0 | Paul | 0 | B03-R1/B03-R3 | Closed | 0 | 03¦74
03 | 75 | B03_Assessment | 82 | 10. PHOTO LOG | DATA | B03-P002 | 107 | Existing Equipment | Basement existing telecom room 107 rack, UPS on floor, Cisco switch, legacy patch panels, fiber LIU, active service labels and cable entries | 0 | Paul | 0 | B03-R1/B03-R2 | Closed | 0 | 03¦75
03 | 76 | B03_Assessment | 83 | 10. PHOTO LOG | DATA | B03-P003 | 101C | Existing DMARC | First-floor existing DMARC Room 101C, patch panels, telecom cabinet, branch panel, provider/fiber equipment, 101C-CAM-01 and active service labels | 0 | Paul | 0 | B03-R2/B03-R6 | Closed | 0 | 03¦76
03 | 77 | B03_Assessment | 84 | 10. PHOTO LOG | DATA | B03-P004 | 101E / 101C | Electrical / Security | B03-TR101CA/B panels, rack receptacles, breakers, SPD, UPS/PDU, access controller, CU-01, 101C-CAM-01 and labels | 0 | Paul | 0 | B03-R4/B03-R7 | Closed | 0 | 03¦77
03 | 78 | B03_Assessment | 85 | 10. PHOTO LOG | DATA | B03-P005 | 101E | HVAC | IU/CU-01, condensate route, thermostat, BACnet adapter, disconnects, alarm points and emergency power source | 0 | Paul | 0 | B03-R3 | Closed | 0 | 03¦78
03 | 79 | B03_Assessment | 86 | 10. PHOTO LOG | DATA | B03-P006 | All | Cable Tray / Firestop | Basement and first-level cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B03-R5 | Closed | 0 | 03¦79
03 | 80 | B03_Assessment | 87 | 10. PHOTO LOG | DATA | B03-P007 | WAO Areas | Telecom Devices | Representative outlets/WAPs/Centrak/clock/camera locations including 108-A/B/C, 108-CK-A, 107A-AP-A, 101C-CAM-01 and related labels | 0 | Paul | 0 | B03-R6 | Closed | 0 | 03¦80
03 | 81 | B03_Assessment | 88 | 10. PHOTO LOG | DATA | B03-P008 | 101E / Existing Rooms | Telecom Acceptance | New racks TR01-101E-1/2, Fiber LIU, Cat6A, patch panels, labels/test records and existing rack transfer work | 0 | Paul | 0 | B03-R6/B03-R8 | Closed | 0 | 03¦81
03 | 82 | B03_Assessment | 89 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 03¦82
04 | 1 | B04_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦1
04 | 2 | B04_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 04¦2
04 | 3 | B04_Assessment | 10 | 1. ROOM INVENTORY | DATA | 04 | B05 | Basement | Existing telecom / service area | TR | 2 | 0 | Verify | 04A-400 / 04T-604 / 04E-701 | Rack elevations show B05 with Rack 1 of 2 and Rack 2 of 2; new B04-TRB05A/B panels and NPA-TR feed shown. | 04¦3
04 | 4 | B04_Assessment | 11 | 1. ROOM INVENTORY | DATA | 04 | 141 | First | Existing room to be converted / upgraded | TR | 1 | 1 | Verify | 04A-401 / 04T-604 / 04E-701 | Architectural enlarged views identify Room 141; new 45-minute rated door/frame, 1-hour/smoke-rated envelope, open-to-deck TR, and future rack. | 04¦4
04 | 5 | B04_Assessment | 12 | 1. ROOM INVENTORY | DATA | 04 | 244A | Second | Existing or renovated telecom area | TR | 1 | 1 | Verify | 04T / 04E-701 | Panel schedule identifies B04-TR244A; room requires field verification of rack count, cooling, pathways, fire protection, and PACS/CCTV requirements. | 04¦5
04 | 6 | B04_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦6
04 | 7 | B04_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦7
04 | 8 | B04_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 04¦8
04 | 9 | B04_Assessment | 16 | 2. ROOM READINESS | DATA | B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify existing utilities, abatement, wall/firestop conditions, and two-rack layout. | 04¦9
04 | 10 | B04_Assessment | 17 | 2. ROOM READINESS | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing wall to become 1-hour fire/smoke rated; open to deck; new 45-minute rated door and access-control hardware coordination. | 04¦10
04 | 11 | B04_Assessment | 18 | 2. ROOM READINESS | DATA | 244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-floor TR referenced by electrical panel schedule; field verify room conditions and plan locations. | 04¦11
04 | 12 | B04_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦12
04 | 13 | B04_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦13
04 | 14 | B04_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 04¦14
04 | 15 | B04_Assessment | 22 | 3. FIRE PROTECTION | DATA | B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning. | 04¦15
04 | 16 | B04_Assessment | 23 | 3. FIRE PROTECTION | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies. | 04¦16
04 | 17 | B04_Assessment | 24 | 3. FIRE PROTECTION | DATA | 244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations. | 04¦17
04 | 18 | B04_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦18
04 | 19 | B04_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦19
04 | 20 | B04_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 04¦20
04 | 21 | B04_Assessment | 28 | 4. HVAC / COOLING | DATA | B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up. | 04¦21
04 | 22 | B04_Assessment | 29 | 4. HVAC / COOLING | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control. | 04¦22
04 | 23 | B04_Assessment | 30 | 4. HVAC / COOLING | DATA | 244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify cooling unit, routing, condensate, controls, and emergency/backup power path. | 04¦23
04 | 24 | B04_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦24
04 | 25 | B04_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦25
04 | 26 | B04_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 04¦26
04 | 27 | B04_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | B05 | Verify | 5 kW | Verify | Verify | B04-NPA-TR / B04-TRB05A / B04-TRB05B | Verify | Verify | Verify | Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits. | 04¦27
04 | 28 | B04_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | 141 | Verify | 5 kW | Verify | Verify | B04-TR141A | Verify | Verify | Verify | Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting. | 04¦28
04 | 29 | B04_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | 244A | Verify | 5 kW | Verify | Verify | B04-TR244A | Verify | Verify | Verify | Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source. | 04¦29
04 | 30 | B04_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦30
04 | 31 | B04_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦31
04 | 32 | B04_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 04¦32
04 | 33 | B04_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. | 04¦33
04 | 34 | B04_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. | 04¦34
04 | 35 | B04_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | 244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | TR/panel identified; verify rack elevation and pathway details against 04T sheets. | 04¦35
04 | 36 | B04_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦36
04 | 37 | B04_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦37
04 | 38 | B04_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 04¦38
04 | 39 | B04_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | B05 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify access-controlled TR door, camera, and VMS/PACS integration. | 04¦39
04 | 40 | B04_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | 141 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural notes require door/access control coordination; verify card reader/electric strike rough-in. | 04¦40
04 | 41 | B04_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | 244A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify room security details and device integration with VA systems. | 04¦41
04 | 42 | B04_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦42
04 | 43 | B04_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦43
04 | 44 | B04_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 04¦44
04 | 45 | B04_Assessment | 52 | 8. OWNER RISKS | DATA | B04-R1 | All | Existing conditions across basement/first/second TR areas not verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / GC | Closed | B04 has multiple TR work areas. | 04¦45
04 | 46 | B04_Assessment | 53 | 8. OWNER RISKS | DATA | B04-R2 | B05 | Basement TR routing may conflict with existing utilities / abatement areas | High | Medium | 6 | Coordinate hazardous material survey, utility locations, penetrations, and pathway routing | GCC / Contractor | Closed | Hazardous drawings included for basement and first levels. | 04¦46
04 | 47 | B04_Assessment | 54 | 8. OWNER RISKS | DATA | B04-R3 | 141 | 1-hour fire/smoke-rated envelope and 45-minute door not field verified | High | Medium | 6 | Inspect rated walls, door/frame, ceiling/open-to-deck conditions, and penetrations | GCC / GC | Closed | Architectural notes identify new 45-minute door/frame and rated wall work. | 04¦47
04 | 48 | B04_Assessment | 55 | 8. OWNER RISKS | DATA | B04-R4 | All | Cooling emergency power / 24/7 continuity not verified | Critical | Medium | 8 | Confirm source power for indoor/outdoor units, controls, condensate pumps, and alarms | GCC / VA / Electrical | Closed | Owner continuity item. | 04¦48
04 | 49 | B04_Assessment | 56 | 8. OWNER RISKS | DATA | B04-R5 | All | UPS/PDU/rack electrical source and load coordination unresolved | High | Medium | 6 | Verify panel schedules, source, SPD, breaker sizes, labeling, and load measurements | Electrical / GCC | Closed | Panel schedule shows B04-NPA-TR, TRB05A/B, TR141A, TR244A. | 04¦49
04 | 50 | B04_Assessment | 57 | 8. OWNER RISKS | DATA | B04-R6 | All | Telecom/fiber cutover could affect active hospital communications | Critical | Medium | 8 | Require phasing plan, test results, and VA/OIT acceptance before cutover | Telecom / OIT / GC | Closed | All telecom equipment/cabling must be tested and accepted before connecting active operations. | 04¦50
04 | 51 | B04_Assessment | 58 | 8. OWNER RISKS | DATA | B04-R7 | All | Fire alarm/sprinkler impairments during construction could affect occupied operations | Critical | Medium | 8 | Track impairments, fire watch, temporary firestopping, and third-party reports | GC / FP / FA | Closed | Shutdowns limited to one at a time campus-wide. | 04¦51
04 | 52 | B04_Assessment | 59 | 8. OWNER RISKS | DATA | B04-R8 | All | Commissioning and third-party inspection reports incomplete before turnover | High | Medium | 6 | Track Cx and 3rd-party inspection deliverables by trade | GC / Cx Manager | Closed | Required by cover sheet and commissioning scope. | 04¦52
04 | 53 | B04_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦53
04 | 54 | B04_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦54
04 | 55 | B04_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 04¦55
04 | 56 | B04_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B04-Q1 | Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? | VA / OIT / Designer | Closed | 0 | 0 | Incomplete room inventory / missed scope | 0 | 0 | 0 | 04¦56
04 | 57 | B04_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B04-Q2 | Are B05, 141, and 244A cooling systems on emergency/backup power? | VA / Electrical / Mechanical | Closed | 0 | 0 | Cooling continuity not confirmed | 0 | 0 | 0 | 04¦57
04 | 58 | B04_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B04-Q3 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0 | 04¦58
04 | 59 | B04_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B04-Q4 | What is the approved migration and cutover sequence for active Building 04 services? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0 | 04¦59
04 | 60 | B04_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B04-Q5 | Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? | GC / COR | Closed | 0 | 0 | Work stoppage or exposure risk | 0 | 0 | 0 | 04¦60
04 | 61 | B04_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B04-Q6 | Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? | Electrical / Designer | Closed | 0 | 0 | Electrical delay or overload risk | 0 | 0 | 0 | 04¦61
04 | 62 | B04_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B04-Q7 | Are all rated wall/floor penetrations and speed sleeves identified and firestopped? | GC / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 04¦62
04 | 63 | B04_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B04-Q8 | Which third-party tests, commissioning forms, and acceptance documents are required before VA turnover? | GC / Cx Manager | Closed | 0 | 0 | Incomplete turnover package | 0 | 0 | 0 | 04¦63
04 | 64 | B04_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦64
04 | 65 | B04_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦65
04 | 66 | B04_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 04¦66
04 | 67 | B04_Assessment | 74 | 10. PHOTO LOG | DATA | B04-P001 | B05 | Existing Condition | Basement TR B05 existing conditions, racks, utilities, penetrations, panels | 0 | Paul | 0 | B04-R1/B04-R2 | Closed | 0 | 04¦67
04 | 68 | B04_Assessment | 75 | 10. PHOTO LOG | DATA | B04-P002 | 141 | Existing Condition | Room 141 existing conditions, door/walls/ceiling/window/floor conditions | 0 | Paul | 0 | B04-R3 | Closed | 0 | 04¦68
04 | 69 | B04_Assessment | 76 | 10. PHOTO LOG | DATA | B04-P003 | 244A | Existing Condition | Room 244A TR existing condition and panel/rack area | 0 | Paul | 0 | B04-R1 | Closed | 0 | 04¦69
04 | 70 | B04_Assessment | 77 | 10. PHOTO LOG | DATA | B04-P004 | All | Firestop | All floor/wall/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B04-R7 | Closed | 0 | 04¦70
04 | 71 | B04_Assessment | 78 | 10. PHOTO LOG | DATA | B04-P005 | All | HVAC | Cooling units, condensate routing, controls, high-temp alarms | 0 | Paul | 0 | B04-R4 | Closed | 0 | 04¦71
04 | 72 | B04_Assessment | 79 | 10. PHOTO LOG | DATA | B04-P006 | All | Electrical | Panels, breakers, UPS/PDU receptacles, SPD, grounding/bonding | 0 | Paul | 0 | B04-R5 | Closed | 0 | 04¦72
04 | 73 | B04_Assessment | 80 | 10. PHOTO LOG | DATA | B04-P007 | All | Telecom | Racks, ladder tray, fiber, Cat6A, labels, LIU, cable managers | 0 | Paul | 0 | B04-R6 | Closed | 0 | 04¦73
04 | 74 | B04_Assessment | 81 | 10. PHOTO LOG | DATA | B04-P008 | All | Security | PACS, card reader, electric strike, camera, motion sensor rough-in | 0 | Paul | 0 | B04-R3 | Closed | 0 | 04¦74
04 | 75 | B04_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 04¦75
05 | 1 | B05_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦1
05 | 2 | B05_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 05¦2
05 | 3 | B05_Assessment | 10 | 1. ROOM INVENTORY | DATA | 05 | 150 | First | Telecom / equipment location | Telecom Enclosure (TE) | 1 | 0 | Verify | 05T-604 / 05T-401 / 05E-401 | New elevation identifies Room 150 with one 12RU Telecom Enclosure; includes APC UPS, PDUs, cable managers, 48-port patch panels, Cat6A patch panel, and Fiber LIU. | 05¦3
05 | 4 | B05_Assessment | 11 | 1. ROOM INVENTORY | DATA | 05 | 153-A | First | Existing wall-mounted TE / existing rack area | Existing equipment / transition point | 1 | 0 | Verify | 05T-604 | Existing elevation shows wall or wall-mount TE at Room 153-A with Cisco switches and multiple legacy 24-port patch panels; existing floor UPS shown. | 05¦4
05 | 5 | B05_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦5
05 | 6 | B05_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Existing active telecommunications equipment remains in Room 153-A. Environmental conditioning supporting this equipment was not identified. Contractor shall verify that operating conditions comply with equipment manufacturer requirements for all active equipment remaining in service. | 05¦6
05 | 7 | B05_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 05¦7
05 | 8 | B05_Assessment | 15 | 2. ROOM READINESS | DATA | 150 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | TE installation; verify mounting wall/backing, access clearance, power location, pathway/firestop, and room readiness. | 05¦8
05 | 9 | B05_Assessment | 16 | 2. ROOM READINESS | DATA | 153-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing equipment area; verify what remains operational and how legacy equipment transitions to new TE. | 05¦9
05 | 10 | B05_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦10
05 | 11 | B05_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦11
05 | 12 | B05_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 05¦12
05 | 13 | B05_Assessment | 20 | 3. FIRE PROTECTION | DATA | 150 | N/A | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts. | 05¦13
05 | 14 | B05_Assessment | 21 | 3. FIRE PROTECTION | DATA | 153-A | N/A | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling. | 05¦14
05 | 15 | B05_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦15
05 | 16 | B05_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦16
05 | 17 | B05_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 05¦17
05 | 18 | B05_Assessment | 25 | 4. HVAC / COOLING | DATA | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling. | 05¦18
05 | 19 | B05_Assessment | 26 | 4. HVAC / COOLING | DATA | 153-A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Existing wall/wall-mount TE area; verify existing environmental conditions during field survey. | 05¦19
05 | 20 | B05_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦20
05 | 21 | B05_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦21
05 | 22 | B05_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 05¦22
05 | 23 | B05_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | 150 | Verify | APC UPS / TE scale | Verify | Verify | Verify | Verify | Verify | Verify | 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source. | 05¦23
05 | 24 | B05_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | 153-A | Existing | Existing floor UPS | Existing | Verify | Verify | Verify | Verify | Verify | Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover. | 05¦24
05 | 25 | B05_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦25
05 | 26 | B05_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦26
05 | 27 | B05_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 05¦27
05 | 28 | B05_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | 150 | Verify | N/A / TE | Verify | Verify | Verify | Verify | Verify | Verify | New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU. | 05¦28
05 | 29 | B05_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | 153-A | Existing | N/A / Wall TE | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records. | 05¦29
05 | 30 | B05_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦30
05 | 31 | B05_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦31
05 | 32 | B05_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 05¦32
05 | 33 | B05_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | 150 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Project general scope includes CCTV and PACS for telecom spaces; verify whether TE location receives camera/access control or is served by existing room controls. | 05¦33
05 | 34 | B05_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | 153-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing security protection and whether access-control work is needed for existing TE area. | 05¦34
05 | 35 | B05_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦35
05 | 36 | B05_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦36
05 | 37 | B05_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 05¦37
05 | 38 | B05_Assessment | 45 | 8. OWNER RISKS | DATA | B05-R1 | 150 | Telecom Enclosure installation details not field verified | High | Medium | 6 | Survey wall/backing, clearances, power, conduit/wireway, and access path before installation | GCC / Contractor | Closed | TE rather than full TR. | 05¦38
05 | 39 | B05_Assessment | 46 | 8. OWNER RISKS | DATA | B05-R2 | 153-A | Existing legacy equipment/cabling may remain active during cutover | Critical | Medium | 8 | Document active services, create cutover plan, protect-in-place until new TE is operational | Telecom / OIT / Contractor | Closed | Existing Cisco switches and patch panels shown. | 05¦39
05 | 40 | B05_Assessment | 47 | 8. OWNER RISKS | DATA | B05-R3 | All | Mechanical/fire protection scope excluded may hide interface risks | Medium | Medium | 4 | Confirm no added cooling/sprinkler work is required and document basis for N/A | GCC / VA / Designer | Closed | Cover sheet specifically excludes mechanical and fire protection scope. | 05¦40
05 | 41 | B05_Assessment | 48 | 8. OWNER RISKS | DATA | B05-R4 | 150 | Electrical panel/circuit source for TE equipment not confirmed | High | Medium | 6 | Verify 05E-401/501/601/701 schedules, UPS/PDU receptacles, labels, and emergency power source | Electrical / GCC | Closed | UPS/PDU devices shown in rack elevation. | 05¦41
05 | 42 | B05_Assessment | 49 | 8. OWNER RISKS | DATA | B05-R5 | All | Firestopping/penetration sealing still required despite fire protection scope exclusion | High | Medium | 6 | Inspect all new and reused conduits, sleeves, wall/floor penetrations, and temporary firestop | GC / Firestop Contractor | Closed | Cabling work can create rated assembly risk. | 05¦42
05 | 43 | B05_Assessment | 50 | 8. OWNER RISKS | DATA | B05-R6 | All | Commissioning / acceptance documentation may be treated as minor due to TE scope | Medium | Medium | 4 | Track testing, labeling, OIT acceptance, third-party inspections, and as-builts | GCC / GC / OIT | Closed | All telecom cabling must be tested and accepted. | 05¦43
05 | 44 | B05_Assessment | 51 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦44
05 | 45 | B05_Assessment | 52 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦45
05 | 46 | B05_Assessment | 53 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 05¦46
05 | 47 | B05_Assessment | 54 | 9. OPEN QUESTIONS | DATA | B05-Q1 | Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could be wrong | 0 | 0 | 0 | 05¦47
05 | 48 | B05_Assessment | 55 | 9. OPEN QUESTIONS | DATA | B05-Q2 | What active services are currently fed from the existing 153-A TE/legacy patch panels? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0 | 05¦48
05 | 49 | B05_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B05-Q3 | What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? | OIT / Contractor | Closed | 0 | 0 | Cutover risk | 0 | 0 | 0 | 05¦49
05 | 50 | B05_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B05-Q4 | Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? | Electrical / Designer | Closed | 0 | 0 | Power source cannot be verified | 0 | 0 | 0 | 05¦50
05 | 51 | B05_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B05-Q5 | Is emergency/backup power required or provided for the TE UPS/PDU source? | VA / Electrical | Closed | 0 | 0 | Continuity requirement unclear | 0 | 0 | 0 | 05¦51
05 | 52 | B05_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B05-Q6 | Are firestopping locations and surface raceway/conduit routes shown and coordinated? | GC / Designer | Closed | 0 | 0 | Rated assembly/firestop risk | 0 | 0 | 0 | 05¦52
05 | 53 | B05_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B05-Q7 | Does Room 150 or existing Room 153-A require PACS/CCTV modifications, or is existing security adequate? | Security / VA | Closed | 0 | 0 | Security acceptance risk | 0 | 0 | 0 | 05¦53
05 | 54 | B05_Assessment | 61 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦54
05 | 55 | B05_Assessment | 62 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦55
05 | 56 | B05_Assessment | 63 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 05¦56
05 | 57 | B05_Assessment | 64 | 10. PHOTO LOG | DATA | B05-P001 | 150 | Existing Condition | Room 150 wall/TE location, mounting surface, clearances, power, pathway | 0 | Paul | 0 | B05-R1/B05-R4 | Closed | 0 | 05¦57
05 | 58 | B05_Assessment | 65 | 10. PHOTO LOG | DATA | B05-P002 | 153-A | Existing Condition | Existing wall/wall-mount TE, Cisco switches, legacy patch panels, floor UPS | 0 | Paul | 0 | B05-R2 | Closed | 0 | 05¦58
05 | 59 | B05_Assessment | 66 | 10. PHOTO LOG | DATA | B05-P003 | All | Firestop | All new/reused penetrations and surface raceway/conduit routes | 0 | Paul | 0 | B05-R5 | Closed | 0 | 05¦59
05 | 60 | B05_Assessment | 67 | 10. PHOTO LOG | DATA | B05-P004 | 150 | Electrical | UPS/PDU outlet, circuit label, panel source, grounding/bonding | 0 | Paul | 0 | B05-R4 | Closed | 0 | 05¦60
05 | 61 | B05_Assessment | 68 | 10. PHOTO LOG | DATA | B05-P005 | All | Telecom | TE, patch panels, Fiber LIU, labels, testing records, as-built conditions | 0 | Paul | 0 | B05-R6 | Closed | 0 | 05¦61
05 | 62 | B05_Assessment | 69 | 10. PHOTO LOG | DATA | B05-P006 | All | Security | Door/security/CCTV/PACS conditions at TE location | 0 | Paul | 0 | B05-R6 | Closed | 0 | 05¦62
05 | 63 | B05_Assessment | 70 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 05¦63
06 | 1 | B06_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦1
06 | 2 | B06_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 06¦2
06 | 3 | B06_Assessment | 10 | 1. ROOM INVENTORY | DATA | 06 | B-01 | Basement | Existing wall/wall-mount TE and floor UPS | Existing equipment / transition point | 1 | 0 | Verify | 06T-604 | Existing basement wall/wall-mount TE with Cisco switches, legacy Ortronics 48-port patch panels, and floor UPS. | 06¦3
06 | 4 | B06_Assessment | 11 | 1. ROOM INVENTORY | DATA | 06 | 178 | First | Existing telecom room / group therapy area adjacent | Telecom Room | 2 | 0 | Verify | 06A-401 / 06E-401 / 06T-604 / 06E-701 | Room 178 shown as 114 SF Telecom Room; existing 2-post racks and new B06-TR178A/B panel work with IU-1-01 cooling. | 06¦4
06 | 5 | B06_Assessment | 12 | 1. ROOM INVENTORY | DATA | 06 | 233 | Second | Data closet / patient toilet area conversion | Telecom Room | 1 | 1 | Verify | 06A-402 / 06E-401 / 06T-604 / 06E-701 | Room 233 shown as 119 SF Telecom Room/Data Closet; future rack elevation, B06-TR233A/B panels, and IU-2-01 cooling. | 06¦5
06 | 6 | B06_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦6
06 | 7 | B06_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦7
06 | 8 | B06_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 06¦8
06 | 9 | B06_Assessment | 16 | 2. ROOM READINESS | DATA | B-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement TE/UPS; protect active services and verify transitions. | 06¦9
06 | 10 | B06_Assessment | 17 | 2. ROOM READINESS | DATA | 178 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify rated construction, door/security, equipment clearance, cooling unit, and electrical panels. | 06¦10
06 | 11 | B06_Assessment | 18 | 2. ROOM READINESS | DATA | 233 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR/Data Closet; architectural notes identify rated wall/door work and fire extinguisher requirements. | 06¦11
06 | 12 | B06_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦12
06 | 13 | B06_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦13
06 | 14 | B06_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 06¦14
06 | 15 | B06_Assessment | 22 | 3. FIRE PROTECTION | DATA | B-01 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing equipment area; verify no cabling penetrations are left unsealed. | 06¦15
06 | 16 | B06_Assessment | 23 | 3. FIRE PROTECTION | DATA | 178 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs. | 06¦16
06 | 17 | B06_Assessment | 24 | 3. FIRE PROTECTION | DATA | 233 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft. | 06¦17
06 | 18 | B06_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦18
06 | 19 | B06_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦19
06 | 20 | B06_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 06¦20
06 | 21 | B06_Assessment | 28 | 4. HVAC / COOLING | DATA | B-01 | Existing | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify basement equipment environmental condition and any heat/load issues during cutover. | 06¦21
06 | 22 | B06_Assessment | 29 | 4. HVAC / COOLING | DATA | 178 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route. | 06¦22
06 | 23 | B06_Assessment | 30 | 4. HVAC / COOLING | DATA | 233 | IU-2-01 / CU-2-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls. | 06¦23
06 | 24 | B06_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦24
06 | 25 | B06_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦25
06 | 26 | B06_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 06¦26
06 | 27 | B06_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | B-01 | Existing | Existing floor UPS | Existing | Verify | Verify | Verify | Verify | Verify | Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements. | 06¦27
06 | 28 | B06_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | 178 | Verify | 5 kW / rack equipment | Verify | Verify | B06-NP-TR / B06-EP-TR / B06-TR178A / B06-TR178B | Verify | Verify | Verify | Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation. | 06¦28
06 | 29 | B06_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | 233 | Verify | 5 kW / rack equipment | Verify | Verify | B06-TR233A / B06-TR233B | Verify | Verify | Verify | Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power. | 06¦29
06 | 30 | B06_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦30
06 | 31 | B06_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦31
06 | 32 | B06_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 06¦32
06 | 33 | B06_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | B-01 | Existing | N/A / TE | Existing | Verify | Verify | Verify | Verify | Verify | Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS. | 06¦33
06 | 34 | B06_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | 178 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification. | 06¦34
06 | 35 | B06_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | 233 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | 06¦35
06 | 36 | B06_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦36
06 | 37 | B06_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦37
06 | 38 | B06_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 06¦38
06 | 39 | B06_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | B-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing basement access/security while protecting active equipment. | 06¦39
06 | 40 | B06_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | 178 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged plan references existing card reader to remain/protect in place and new tri-tech motion sensor; verify PACS/CCTV integration. | 06¦40
06 | 41 | B06_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | 233 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify door hardware/access control, motion sensor, camera, and VA security integration. | 06¦41
06 | 42 | B06_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦42
06 | 43 | B06_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦43
06 | 44 | B06_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 06¦44
06 | 45 | B06_Assessment | 52 | 8. OWNER RISKS | DATA | B06-R1 | All | Existing conditions across B-01, 178 and 233 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | Building 06 includes basement, first and second level work. | 06¦45
06 | 46 | B06_Assessment | 53 | 8. OWNER RISKS | DATA | B06-R2 | B-01 | Existing basement equipment may remain active during cutover | Critical | Medium | 8 | Document active services and protect in place until new system is tested and accepted | Telecom / OIT | Closed | Existing Cisco/legacy patch panels and UPS shown. | 06¦46
06 | 47 | B06_Assessment | 54 | 8. OWNER RISKS | DATA | B06-R3 | 178 | Electrical panel replacement/new telecom power could interrupt active systems | Critical | Medium | 8 | Coordinate load measurement, panel renovation, shutdowns and temporary power plan | Electrical / GCC | Closed | B06-EP-TR and B06-TR178A/B panel work. | 06¦47
06 | 48 | B06_Assessment | 55 | 8. OWNER RISKS | DATA | B06-R4 | 233 | Room 233 conversion/rated wall and door work may impact adjacent patient toilet/private bath areas | High | Medium | 6 | Verify phasing, barriers, infection control and temporary life-safety provisions | GC / VA | Closed | Architectural enlarged views show TR 233 adjacent to patient toilet/private bath. | 06¦48
06 | 49 | B06_Assessment | 56 | 8. OWNER RISKS | DATA | B06-R5 | 178/233 | Dedicated cooling emergency power, controls, condensate and BACnet interface not verified | Critical | Medium | 8 | Confirm emergency power source, disconnects, condensate routes, BACnet adapter and high-temp alarms | Mechanical / Electrical | Closed | IU-1-01/CU-1-01 and IU-2-01/CU-2-01. | 06¦49
06 | 50 | B06_Assessment | 57 | 8. OWNER RISKS | DATA | B06-R6 | All | Fire alarm/sprinkler impairments and penetrations may affect occupied operations | Critical | Medium | 8 | Track impairments, fire watch, temporary firestop and third-party reports | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide. | 06¦50
06 | 51 | B06_Assessment | 58 | 8. OWNER RISKS | DATA | B06-R7 | All | Telecom/fiber cutover could affect active hospital communications | Critical | Medium | 8 | Require cutover plan, test results and VA/OIT acceptance before energizing active operations | Telecom / OIT | Closed | All cabling must be tested, approved and accepted. | 06¦51
06 | 52 | B06_Assessment | 59 | 8. OWNER RISKS | DATA | B06-R8 | All | Commissioning/third-party inspection reports may not be ready at turnover | High | Medium | 6 | Track commissioning and third-party inspection deliverables by trade | GC / Cx Manager | Closed | Required by cover sheet and commissioning sections. | 06¦52
06 | 53 | B06_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦53
06 | 54 | B06_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦54
06 | 55 | B06_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 06¦55
06 | 56 | B06_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B06-Q1 | Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 06¦56
06 | 57 | B06_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B06-Q2 | What active services are fed from existing B-01 and Room 178 legacy equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0 | 06¦57
06 | 58 | B06_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B06-Q3 | What is the approved cutover sequence for B-01, 178 and 233? | OIT / Contractor | Closed | 0 | 0 | Cutover risk | 0 | 0 | 0 | 06¦58
06 | 59 | B06_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B06-Q4 | Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 06¦59
06 | 60 | B06_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B06-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0 | 06¦60
06 | 61 | B06_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B06-Q6 | Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 06¦61
06 | 62 | B06_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B06-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 06¦62
06 | 63 | B06_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B06-Q8 | Which commissioning/third-party tests must be complete before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 06¦63
06 | 64 | B06_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦64
06 | 65 | B06_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦65
06 | 66 | B06_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 06¦66
06 | 67 | B06_Assessment | 74 | 10. PHOTO LOG | DATA | B06-P001 | B-01 | Existing Condition | Existing basement wall/wall-mount TE, Cisco switches, legacy patch panels, floor UPS | 0 | Paul | 0 | B06-R1/B06-R2 | Closed | 0 | 06¦67
06 | 68 | B06_Assessment | 75 | 10. PHOTO LOG | DATA | B06-P002 | 178 | Existing Condition | Room 178 TR, existing 2-post racks, panels, card reader/security, HVAC location | 0 | Paul | 0 | B06-R1/B06-R3 | Closed | 0 | 06¦68
06 | 69 | B06_Assessment | 76 | 10. PHOTO LOG | DATA | B06-P003 | 233 | Existing Condition | Room 233/Data Closet, adjacent toilet/bath areas, walls/door/ceiling/penetrations | 0 | Paul | 0 | B06-R4 | Closed | 0 | 06¦69
06 | 70 | B06_Assessment | 77 | 10. PHOTO LOG | DATA | B06-P004 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B06-R6 | Closed | 0 | 06¦70
06 | 71 | B06_Assessment | 78 | 10. PHOTO LOG | DATA | B06-P005 | 178/233 | HVAC | IU/CU equipment, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm | 0 | Paul | 0 | B06-R5 | Closed | 0 | 06¦71
06 | 72 | B06_Assessment | 79 | 10. PHOTO LOG | DATA | B06-P006 | All | Electrical | B06-NP-TR, B06-EP-TR, B06-TR178A/B, B06-TR233A/B, breakers, SPD, labels | 0 | Paul | 0 | B06-R3/B06-R6 | Closed | 0 | 06¦72
06 | 73 | B06_Assessment | 80 | 10. PHOTO LOG | DATA | B06-P007 | All | Telecom | Racks, ladder tray, fiber, Cat6A, LIU, patch panels, labels, test records | 0 | Paul | 0 | B06-R7 | Closed | 0 | 06¦73
06 | 74 | B06_Assessment | 81 | 10. PHOTO LOG | DATA | B06-P008 | All | Security | Card readers, electric strikes, door position, motion sensors, CCTV/PACS integration | 0 | Paul | 0 | B06-R4 | Closed | 0 | 06¦74
06 | 75 | B06_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 06¦75
07 | 1 | B07_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦1
07 | 2 | B07_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 07¦2
07 | 3 | B07_Assessment | 10 | 1. ROOM INVENTORY | DATA | 07 | B-18 | Basement | Existing office / telecom-service area | Telecom Room | 1 | 1 | Verify | 07A-400 / 07E-401 / 07T-604 / 07M-701 | Rack elevation shows B-18 as 1 of 1 + future, 4-post floor rack, UPS, future Zone PDU, network switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | 07¦3
07 | 4 | B07_Assessment | 11 | 1. ROOM INVENTORY | DATA | 07 | 228A | Second | Social worker shared / adjacent OPM storage and DOM MSA area | Telecom Room | 1 | 1 | Verify | 07A-401 / 07E-401 / 07T-604 / 07M-701 | Architectural enlarged view identifies Telecom Room 228A at 236 SF; includes fire-rated door/wall work, FEC requirement, exterior furring wall/window enclosure and temporary dust barrier. | 07¦4
07 | 5 | B07_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦5
07 | 6 | B07_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦6
07 | 7 | B07_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 07¦7
07 | 8 | B07_Assessment | 15 | 2. ROOM READINESS | DATA | B-18 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify office-to-TR conversion conditions, existing utilities, wall/ceiling/firestop conditions and future rack clearance. | 07¦8
07 | 9 | B07_Assessment | 16 | 2. ROOM READINESS | DATA | 228A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-floor TR; verify 1-hour fire/smoke-rated wall, 45-minute door/frame, open-to-deck/furring wall details, access control and equipment clearances. | 07¦9
07 | 10 | B07_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦10
07 | 11 | B07_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦11
07 | 12 | B07_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 07¦12
07 | 13 | B07_Assessment | 20 | 3. FIRE PROTECTION | DATA | B-18 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination. | 07¦13
07 | 14 | B07_Assessment | 21 | 3. FIRE PROTECTION | DATA | 228A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications. | 07¦14
07 | 15 | B07_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦15
07 | 16 | B07_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦16
07 | 17 | B07_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 07¦17
07 | 18 | B07_Assessment | 25 | 4. HVAC / COOLING | DATA | B-18 | IU-0-01 / CU-0-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm. | 07¦18
07 | 19 | B07_Assessment | 26 | 4. HVAC / COOLING | DATA | 228A | IU-2-01 / CU-2-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route. | 07¦19
07 | 20 | B07_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦20
07 | 21 | B07_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦21
07 | 22 | B07_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 07¦22
07 | 23 | B07_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | B-18 | Verify | 5 kW / rack equipment | Verify | Verify | B07-TRB18A / B07-TRB18B | Verify | Verify | Verify | Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement. | 07¦23
07 | 24 | B07_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | 228A | Verify | 5 kW / rack equipment | Verify | Verify | B07-TR228A / B07-TR228B | Verify | Verify | Verify | Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels. | 07¦24
07 | 25 | B07_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦25
07 | 26 | B07_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦26
07 | 27 | B07_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 07¦27
07 | 28 | B07_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | B-18 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU. | 07¦28
07 | 29 | B07_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | 228A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover. | 07¦29
07 | 30 | B07_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦30
07 | 31 | B07_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦31
07 | 32 | B07_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 07¦32
07 | 33 | B07_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | B-18 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify access control, door hardware and CCTV/PACS integration for basement TR. | 07¦33
07 | 34 | B07_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | 228A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural notes require access control hardware modifications at new rated door; verify card reader, electric strike, door position switch, motion sensor and camera. | 07¦34
07 | 35 | B07_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦35
07 | 36 | B07_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦36
07 | 37 | B07_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 07¦37
07 | 38 | B07_Assessment | 45 | 8. OWNER RISKS | DATA | B07-R1 | All | Existing conditions for B-18 and 228A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B07 includes basement and second-floor TR scope. | 07¦38
07 | 39 | B07_Assessment | 46 | 8. OWNER RISKS | DATA | B07-R2 | B-18 | Basement TR conversion may conflict with existing utilities, office finishes or active pathways | High | Medium | 6 | Verify routing, clearances, penetrations, existing conduit and access before work | GC / Telecom | Closed | Basement B-18 shown on rack elevation and electrical enlarged plans. | 07¦39
07 | 40 | B07_Assessment | 47 | 8. OWNER RISKS | DATA | B07-R3 | 228A | Second-floor rated wall/door work and exterior furring wall/window enclosure could affect schedule | High | Medium | 6 | Coordinate architectural work, door/frame, wall rating, furring wall, finishes and infection control barriers | GC / VA | Closed | 07A-401 notes include 45-minute rated door and new furring wall at exterior wall. | 07¦40
07 | 41 | B07_Assessment | 48 | 8. OWNER RISKS | DATA | B07-R4 | B-18/228A | Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified | Critical | Medium | 8 | Confirm IU/CU assignments, emergency source, BACnet/interface, condensate pump routing and alarm points | Mechanical / Electrical | Closed | IU-0-01/CU-0-01 and IU-2-01/CU-2-01 schedules. | 07¦41
07 | 42 | B07_Assessment | 49 | 8. OWNER RISKS | DATA | B07-R5 | All | Electrical panel/circuit source and rack load coordination unresolved | High | Medium | 6 | Verify B07-TRB18A/B and B07-TR228A/B panel schedules, circuit labels, SPDs and load measurements | Electrical / GCC | Closed | Electrical enlarged plans identify panel/circuit references. | 07¦42
07 | 43 | B07_Assessment | 50 | 8. OWNER RISKS | DATA | B07-R6 | All | Telecom/fiber cutover may affect active hospital communications | Critical | Medium | 8 | Require cutover plan, test results, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | All cabling must be tested, approved and accepted before connecting to active operations. | 07¦43
07 | 44 | B07_Assessment | 51 | 8. OWNER RISKS | DATA | B07-R7 | All | Fire alarm/sprinkler impairments and firestopping could affect occupied operations | Critical | Medium | 8 | Track impairments, temporary firestopping, fire watch, sprinkler/head changes and FA acceptance testing | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide. | 07¦44
07 | 45 | B07_Assessment | 52 | 8. OWNER RISKS | DATA | B07-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspection, testing, labels and as-built deliverables by trade | GC / Cx Manager | Closed | Required by cover/general notes. | 07¦45
07 | 46 | B07_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦46
07 | 47 | B07_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦47
07 | 48 | B07_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 07¦48
07 | 49 | B07_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B07-Q1 | Confirm final TR scope: B-18 basement and 228A second floor only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 07¦49
07 | 50 | B07_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B07-Q2 | Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? | Mechanical / Designer | Closed | 0 | 0 | Cooling scope unclear | 0 | 0 | 0 | 07¦50
07 | 51 | B07_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B07-Q3 | Are cooling units and controls on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity not confirmed | 0 | 0 | 0 | 07¦51
07 | 52 | B07_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B07-Q4 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0 | 07¦52
07 | 53 | B07_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B07-Q5 | What active services are currently fed from B-18 and/or existing pathways serving 228A? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0 | 07¦53
07 | 54 | B07_Assessment | 61 | 9. OPEN QUESTIONS | DATA | B07-Q6 | Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 07¦54
07 | 55 | B07_Assessment | 62 | 9. OPEN QUESTIONS | DATA | B07-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 07¦55
07 | 56 | B07_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B07-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 07¦56
07 | 57 | B07_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦57
07 | 58 | B07_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦58
07 | 59 | B07_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 07¦59
07 | 60 | B07_Assessment | 67 | 10. PHOTO LOG | DATA | B07-P001 | B-18 | Existing Condition | Basement TR B-18 existing room, walls, ceiling, floor, utilities, penetrations and pathway | 0 | Paul | 0 | B07-R1/B07-R2 | Closed | 0 | 07¦60
07 | 61 | B07_Assessment | 68 | 10. PHOTO LOG | DATA | B07-P002 | 228A | Existing Condition | Second-floor TR 228A, door/wall/furring/window conditions, adjacent spaces and pathway | 0 | Paul | 0 | B07-R1/B07-R3 | Closed | 0 | 07¦61
07 | 62 | B07_Assessment | 69 | 10. PHOTO LOG | DATA | B07-P003 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B07-R7 | Closed | 0 | 07¦62
07 | 63 | B07_Assessment | 70 | 10. PHOTO LOG | DATA | B07-P004 | B-18/228A | HVAC | IU/CU units, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B07-R4 | Closed | 0 | 07¦63
07 | 64 | B07_Assessment | 71 | 10. PHOTO LOG | DATA | B07-P005 | All | Electrical | B07-TRB18A/B and B07-TR228A/B panels, breakers, SPD, rack receptacles and labels | 0 | Paul | 0 | B07-R5 | Closed | 0 | 07¦64
07 | 65 | B07_Assessment | 72 | 10. PHOTO LOG | DATA | B07-P006 | All | Telecom | Racks, ladder tray, fiber, Cat6A, patch panels, LIU, labels and test records | 0 | Paul | 0 | B07-R6 | Closed | 0 | 07¦65
07 | 66 | B07_Assessment | 73 | 10. PHOTO LOG | DATA | B07-P007 | All | Security | Card reader, electric strike, door position, CCTV/PACS and motion sensors | 0 | Paul | 0 | B07-R3 | Closed | 0 | 07¦66
07 | 67 | B07_Assessment | 74 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 07¦67
08 | 1 | B08_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦1
08 | 2 | B08_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 08¦2
08 | 3 | B08_Assessment | 10 | 1. ROOM INVENTORY | DATA | 08 | B-15 | Basement | Existing wall/wall-mounted TE and floor UPS | Existing equipment / transition point | 2 | 0 | Verify | 08T-604 | Existing rack elevation identifies Building 08 basement Room B-15 with wall/wall-mounted TE, legacy patch panels, legacy Fiber LIU, and floor UPS. | 08¦3
08 | 4 | B08_Assessment | 11 | 1. ROOM INVENTORY | DATA | 08 | B12B | Basement | Office / basement cabling area | Telecom enclosure / TE cabling service area | 1 | 0 | Verify | 08A-401 / 08E-701 / 08T-701 | Door schedule identifies B12B as Office with 45-minute door; telecom schedule and electrical schedule reference TE01-B12B-1 and TE receptacle Room B12B. Field verify actual TE/equipment scope. | 08¦4
08 | 5 | B08_Assessment | 12 | 1. ROOM INVENTORY | DATA | 08 | 2065A | Second | Existing copy/office/storage area converted | Telecom Room | 2 | 0 | Verify | 08A-401 / 08E-701 / 08T-604 / 08M-701 | Telecom Room 2065A, 127 SF; new rack elevation shows two 4-post floor racks, UPS, Zone PDU, network switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | 08¦5
08 | 6 | B08_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦6
08 | 7 | B08_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦7
08 | 8 | B08_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 08¦8
08 | 9 | B08_Assessment | 16 | 2. ROOM READINESS | DATA | B-15 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom equipment; protect active services and verify legacy equipment status. | 08¦9
08 | 10 | B08_Assessment | 17 | 2. ROOM READINESS | DATA | B12B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement Office/TE area; verify wall/door rating, pathways, outlet/panel scope, firestopping and actual TE location. | 08¦10
08 | 11 | B08_Assessment | 18 | 2. ROOM READINESS | DATA | 2065A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New Telecom Room; verify 1-hour fire/smoke-rated room, 45-minute door/frame, open-to-deck construction, static-dissipative floor sealer, clearances and equipment layout. | 08¦11
08 | 12 | B08_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦12
08 | 13 | B08_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦13
08 | 14 | B08_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 08¦14
08 | 15 | B08_Assessment | 22 | 3. FIRE PROTECTION | DATA | B-15 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected. | 08¦15
08 | 16 | B08_Assessment | 23 | 3. FIRE PROTECTION | DATA | B12B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers. | 08¦16
08 | 17 | B08_Assessment | 24 | 3. FIRE PROTECTION | DATA | 2065A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades. | 08¦17
08 | 18 | B08_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦18
08 | 19 | B08_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦19
08 | 20 | B08_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 08¦20
08 | 21 | B08_Assessment | 28 | 4. HVAC / COOLING | DATA | B-15 | Existing | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing environmental conditions and whether active legacy equipment remains during cutover. | 08¦21
08 | 22 | B08_Assessment | 29 | 4. HVAC / COOLING | DATA | B12B | N/A / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Field verify whether TE equipment load requires cooling or if served by existing building HVAC. | 08¦22
08 | 23 | B08_Assessment | 30 | 4. HVAC / COOLING | DATA | 2065A | IU-2-01 / CU-2-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls. | 08¦23
08 | 24 | B08_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦24
08 | 25 | B08_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦25
08 | 26 | B08_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 08¦26
08 | 27 | B08_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | B-15 | Existing | Existing floor UPS | Existing | Verify | Verify | Verify | Verify | Verify | Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements. | 08¦27
08 | 28 | B08_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | B12B | Verify | TE scale | Verify | Verify | TE receptacle Room B12B / B08-TR2065AB reference | Verify | Verify | Verify | Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel. | 08¦28
08 | 29 | B08_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | 2065A | Verify | 5 kW / rack equipment | Verify | Verify | B08-TR2065AA / B08-TR2065AB | Verify | Verify | Verify | Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope. | 08¦29
08 | 30 | B08_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦30
08 | 31 | B08_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦31
08 | 32 | B08_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 08¦32
08 | 33 | B08_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | B-15 | Existing | N/A / TE | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS. | 08¦33
08 | 34 | B08_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | B12B | Verify | N/A / TE | Verify | Verify | Verify | Verify | Verify | Verify | Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance. | 08¦34
08 | 35 | B08_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | 2065A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS. | 08¦35
08 | 36 | B08_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦36
08 | 37 | B08_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦37
08 | 38 | B08_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 08¦38
08 | 39 | B08_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | B-15 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing basement access/security while protecting active equipment. | 08¦39
08 | 40 | B08_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | B12B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 45-minute door shown; verify access-control hardware applicability and whether TE is secured. | 08¦40
08 | 41 | B08_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | 2065A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Door schedule/hardware note requires coordination with electrical/access control; verify card reader, electric strike, door position, motion sensor, camera and VA integration. | 08¦41
08 | 42 | B08_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦42
08 | 43 | B08_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦43
08 | 44 | B08_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 08¦44
08 | 45 | B08_Assessment | 52 | 8. OWNER RISKS | DATA | B08-R1 | All | Existing conditions for B-15, B12B and 2065A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B08 includes existing equipment, TE/cabling area and new TR scope. | 08¦45
08 | 46 | B08_Assessment | 53 | 8. OWNER RISKS | DATA | B08-R2 | B-15 | Existing basement legacy equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place and define cutover/demo sequence | Telecom / OIT | Closed | Existing TE, patch panels, Fiber LIU and UPS shown. | 08¦46
08 | 47 | B08_Assessment | 54 | 8. OWNER RISKS | DATA | B08-R3 | B12B | Basement B12B appears as Office in architectural schedule but TE in telecom/electrical schedules | High | Medium | 6 | Field verify actual TE location, room name, door/wall rating and panel/cable routing | GCC / VA / Designer | Closed | Potential room/scope mismatch. | 08¦47
08 | 48 | B08_Assessment | 55 | 8. OWNER RISKS | DATA | B08-R4 | 2065A | Second-floor Telecom Room conversion includes rated wall/door/open-to-deck work and possible hazardous material impacts | High | Medium | 6 | Coordinate architectural work, dust barriers, floor abatement, FEC and rated assemblies before construction | GC / VA | Closed | Hazardous material abatement plan included for Level 2. | 08¦48
08 | 49 | B08_Assessment | 56 | 8. OWNER RISKS | DATA | B08-R5 | 2065A | Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified | Critical | Medium | 8 | Confirm IU/CU assignment, emergency source, BACnet/interface, condensate routing and alarm points | Mechanical / Electrical | Closed | IU-2-01/CU-2-01 scheduled at 36,000 BTUH. | 08¦49
08 | 50 | B08_Assessment | 57 | 8. OWNER RISKS | DATA | B08-R6 | All | Electrical panel/circuit source and rack load coordination unresolved | High | Medium | 6 | Verify B08-TR2065AA/AB panel schedules, rack receptacles, SPD, labels and load measurement requirements | Electrical / GCC | Closed | Panel schedule includes telecom panelboard notes and 30-day load measurement requirements. | 08¦50
08 | 51 | B08_Assessment | 58 | 8. OWNER RISKS | DATA | B08-R7 | All | Fire alarm/sprinkler impairments and firestopping could affect occupied operations | Critical | Medium | 8 | Track impairments, temporary firestopping, fire watch, sprinkler/device changes and FA acceptance testing | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide. | 08¦51
08 | 52 | B08_Assessment | 59 | 8. OWNER RISKS | DATA | B08-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, test records, labels, OIT acceptance and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 08¦52
08 | 53 | B08_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦53
08 | 54 | B08_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦54
08 | 55 | B08_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 08¦55
08 | 56 | B08_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B08-Q1 | Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory may miss scope | 0 | 0 | 0 | 08¦56
08 | 57 | B08_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B08-Q2 | What active services are currently fed from existing B-15 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0 | 08¦57
08 | 58 | B08_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B08-Q3 | Is B12B truly a TE/equipment location or only a cabling pathway/service area? | VA / Designer / Contractor | Closed | 0 | 0 | Scope ambiguity | 0 | 0 | 0 | 08¦58
08 | 59 | B08_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B08-Q4 | Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 08¦59
08 | 60 | B08_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B08-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0 | 08¦60
08 | 61 | B08_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B08-Q6 | Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 08¦61
08 | 62 | B08_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B08-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 08¦62
08 | 63 | B08_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B08-Q8 | Which hazardous material/abatement steps apply to Level 2 floor penetrations and flooring removal? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0 | 08¦63
08 | 64 | B08_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦64
08 | 65 | B08_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦65
08 | 66 | B08_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 08¦66
08 | 67 | B08_Assessment | 74 | 10. PHOTO LOG | DATA | B08-P001 | B-15 | Existing Condition | Existing basement TE, legacy patch panels, Fiber LIU, floor UPS and pathways | 0 | Paul | 0 | B08-R1/B08-R2 | Closed | 0 | 08¦67
08 | 68 | B08_Assessment | 75 | 10. PHOTO LOG | DATA | B08-P002 | B12B | Existing Condition | Basement B12B office/TE location, door, pathways, receptacles, panel source and penetrations | 0 | Paul | 0 | B08-R3 | Closed | 0 | 08¦68
08 | 69 | B08_Assessment | 76 | 10. PHOTO LOG | DATA | B08-P003 | 2065A | Existing Condition | Second-floor TR 2065A room, door/walls/ceiling/floor, exterior furring/window, penetrations | 0 | Paul | 0 | B08-R4 | Closed | 0 | 08¦69
08 | 70 | B08_Assessment | 77 | 10. PHOTO LOG | DATA | B08-P004 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B08-R7 | Closed | 0 | 08¦70
08 | 71 | B08_Assessment | 78 | 10. PHOTO LOG | DATA | B08-P005 | 2065A | HVAC | IU-2-01/CU-2-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power | 0 | Paul | 0 | B08-R5 | Closed | 0 | 08¦71
08 | 72 | B08_Assessment | 79 | 10. PHOTO LOG | DATA | B08-P006 | All | Electrical | B08-TR2065AA/AB panels, breakers, SPD, rack receptacles, TE receptacle B12B and labels | 0 | Paul | 0 | B08-R6 | Closed | 0 | 08¦72
08 | 73 | B08_Assessment | 80 | 10. PHOTO LOG | DATA | B08-P007 | All | Telecom | B-15 legacy equipment, B12B TE schedule, 2065A racks, fiber, Cat6A, patch panels, LIU, labels and test records | 0 | Paul | 0 | B08-R2/B08-R8 | Closed | 0 | 08¦73
08 | 74 | B08_Assessment | 81 | 10. PHOTO LOG | DATA | B08-P008 | All | Security | Card reader, electric strike, door position, CCTV/PACS and motion sensors | 0 | Paul | 0 | B08-R4 | Closed | 0 | 08¦74
08 | 75 | B08_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 08¦75
09 | 1 | B09_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦1
09 | 2 | B09_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 09¦2
09 | 3 | B09_Assessment | 10 | 1. ROOM INVENTORY | DATA | 09 | B01 | Basement | Storage / existing telecom equipment area | Telecom Room | 2 | 0 | Verify | 09A-400 / 09E-402 / 09T-604 / 09E-701 | Telecom Room B01, 200 SF; existing/new telecom equipment shown with panels B09-TRB01A/B and cooling circuits CU-0-1, CU-1-1, CU-2-1 in electrical schedule/enlarged plans. | 09¦3
09 | 4 | B09_Assessment | 11 | 1. ROOM INVENTORY | DATA | 09 | 104B | First | Interview room / existing area converted | Telecom Room | 2 | 0 | Verify | 09A-401 / 09E-401 / 09T-604 / 09E-701 | Telecom Room 104B, 85 SF; panels B09-TR104BA/B shown; first-level enlarged plans identify access control/security devices, IU-1-01, and TR receptacle/rack circuiting. | 09¦4
09 | 5 | B09_Assessment | 12 | 1. ROOM INVENTORY | DATA | 09 | 206A | Second | Nursing service / adjacent office area | Telecom Room | 2 | 0 | Verify | 09A-401 / 09E-401 / 09T-604 / 09E-701 | Telecom Room 206A, 120 SF; panels B09-TR206AA/B shown; second-level enlarged plans identify IU-2-01, TR circuits, security devices, and room layout adjacent to Nursing Service 206. | 09¦5
09 | 6 | B09_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦6
09 | 7 | B09_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦7
09 | 8 | B09_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 09¦8
09 | 9 | B09_Assessment | 16 | 2. ROOM READINESS | DATA | B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify existing storage-to-TR conversion, wall/ceiling/floor condition, active equipment, pathways, and clearances. | 09¦9
09 | 10 | B09_Assessment | 17 | 2. ROOM READINESS | DATA | 104B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated wall requirements, 45-minute door/frame, access control, security devices, and equipment clearance. | 09¦10
09 | 11 | B09_Assessment | 18 | 2. ROOM READINESS | DATA | 206A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR; verify rated wall/door, open-to-deck conditions, penetrations, cooling unit, and rack/service clearance. | 09¦11
09 | 12 | B09_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦12
09 | 13 | B09_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦13
09 | 14 | B09_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 09¦14
09 | 15 | B09_Assessment | 22 | 3. FIRE PROTECTION | DATA | B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR. | 09¦15
09 | 16 | B09_Assessment | 23 | 3. FIRE PROTECTION | DATA | 104B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft. | 09¦16
09 | 17 | B09_Assessment | 24 | 3. FIRE PROTECTION | DATA | 206A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations. | 09¦17
09 | 18 | B09_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦18
09 | 19 | B09_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦19
09 | 20 | B09_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 09¦20
09 | 21 | B09_Assessment | 28 | 4. HVAC / COOLING | DATA | B01 | IU-0-01 / CU-0-1 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms. | 09¦21
09 | 22 | B09_Assessment | 29 | 4. HVAC / COOLING | DATA | 104B | IU-1-01 / CU-1-1 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power. | 09¦22
09 | 23 | B09_Assessment | 30 | 4. HVAC / COOLING | DATA | 206A | IU-2-01 / CU-2-1 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power. | 09¦23
09 | 24 | B09_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦24
09 | 25 | B09_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦25
09 | 26 | B09_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 09¦26
09 | 27 | B09_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | B01 | Verify | 5 kW / rack equipment | Verify | Verify | B09-TRB01A / B09-TRB01B / B09-EP-TR | Verify | Verify | Verify | Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes. | 09¦27
09 | 28 | B09_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | 104B | Verify | 5 kW / rack equipment | Verify | Verify | B09-TR104BA / B09-TR104BB | Verify | Verify | Verify | Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits. | 09¦28
09 | 29 | B09_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | 206A | Verify | 5 kW / rack equipment | Verify | Verify | B09-TR206AA / B09-TR206AB | Verify | Verify | Verify | Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits. | 09¦29
09 | 30 | B09_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦30
09 | 31 | B09_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦31
09 | 32 | B09_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 09¦32
09 | 33 | B09_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover. | 09¦33
09 | 34 | B09_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | 104B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | 09¦34
09 | 35 | B09_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | 206A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | 09¦35
09 | 36 | B09_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦36
09 | 37 | B09_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦37
09 | 38 | B09_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 09¦38
09 | 39 | B09_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Enlarged plans show existing/new security boxes, network door controller, camera/security scope; verify PACS/CCTV integration and protection of active security systems. | 09¦39
09 | 40 | B09_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | 104B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 104B camera designation; verify card reader, electric strike, door contact, motion and camera. | 09¦40
09 | 41 | B09_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | 206A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 206A camera designation; verify PACS/VMS integration and commissioning. | 09¦41
09 | 42 | B09_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦42
09 | 43 | B09_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦43
09 | 44 | B09_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 09¦44
09 | 45 | B09_Assessment | 52 | 8. OWNER RISKS | DATA | B09-R1 | All | Existing conditions for B01, 104B and 206A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B09 includes basement, first and second level TR work. | 09¦45
09 | 46 | B09_Assessment | 53 | 8. OWNER RISKS | DATA | B09-R2 | B01 | Basement TR includes existing equipment and could remain active during cutover | Critical | Medium | 8 | Document active services, protect-in-place and define cutover/demo sequence | Telecom / OIT | Closed | B01 shows existing security/network/telecom equipment and panel work. | 09¦46
09 | 47 | B09_Assessment | 54 | 8. OWNER RISKS | DATA | B09-R3 | All | Hazardous material abatement plans exist for basement, first and second levels | High | Medium | 6 | Coordinate ACM/lead/abatement review before penetrations, flooring removal or ceiling/wall work | GC / IH / COR | Closed | B09 drawing index includes 09H-100, 09H-101 and 09H-102. | 09¦47
09 | 48 | B09_Assessment | 55 | 8. OWNER RISKS | DATA | B09-R4 | 104B/206A | Rated wall/door work and fire/smoke assemblies could affect schedule and acceptance | High | Medium | 6 | Verify wall ratings, door/frame rating, penetrations, smoke/fire barriers and access control hardware | GC / VA | Closed | Fire protection/architectural enlarged plans show rated wall legends and TR layouts. | 09¦48
09 | 49 | B09_Assessment | 56 | 8. OWNER RISKS | DATA | B09-R5 | All | Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified | Critical | Medium | 8 | Confirm IU/CU assignments, emergency source, BACnet/interface, condensate routing and alarms | Mechanical / Electrical | Closed | IU-0/1/2 and CU-0/1/2 appear in electrical/enlarged data. | 09¦49
09 | 50 | B09_Assessment | 57 | 8. OWNER RISKS | DATA | B09-R6 | All | Electrical panel/circuit source and rack load coordination unresolved | High | Medium | 6 | Verify B09-TRB01A/B, B09-TR104BA/B, B09-TR206AA/B schedules, SPDs, labels and load measurements | Electrical / GCC | Closed | B09 has multiple TR panels across all three levels. | 09¦50
09 | 51 | B09_Assessment | 58 | 8. OWNER RISKS | DATA | B09-R7 | All | Fire alarm/sprinkler impairments and firestopping could affect occupied operations | Critical | Medium | 8 | Track impairments, temporary firestopping, fire watch, sprinkler/head changes and FA acceptance testing | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide. | 09¦51
09 | 52 | B09_Assessment | 59 | 8. OWNER RISKS | DATA | B09-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, test records, labels, OIT acceptance and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 09¦52
09 | 53 | B09_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦53
09 | 54 | B09_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦54
09 | 55 | B09_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 09¦55
09 | 56 | B09_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B09-Q1 | Confirm final TR scope: B01 basement, 104B first level, and 206A second level? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory may miss scope | 0 | 0 | 0 | 09¦56
09 | 57 | B09_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B09-Q2 | What active services are currently fed from B01 existing equipment/security/network devices? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 09¦57
09 | 58 | B09_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B09-Q3 | What hazardous/abatement steps apply to B01, 104B and 206A work areas? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0 | 09¦58
09 | 59 | B09_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B09-Q4 | Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 09¦59
09 | 60 | B09_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B09-Q5 | Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? | GC / COR | Closed | 0 | 0 | Life safety acceptance risk | 0 | 0 | 0 | 09¦60
09 | 61 | B09_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B09-Q6 | Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 09¦61
09 | 62 | B09_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B09-Q7 | Are all rated wall/floor penetrations, sleeves and firestopping identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 09¦62
09 | 63 | B09_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B09-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 09¦63
09 | 64 | B09_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦64
09 | 65 | B09_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦65
09 | 66 | B09_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 09¦66
09 | 67 | B09_Assessment | 74 | 10. PHOTO LOG | DATA | B09-P001 | B01 | Existing Condition | Basement TR B01 existing telecom/security/network equipment, storage conditions, panels, ceiling, walls and pathways | 0 | Paul | 0 | B09-R1/B09-R2 | Closed | 0 | 09¦67
09 | 68 | B09_Assessment | 75 | 10. PHOTO LOG | DATA | B09-P002 | 104B | Existing Condition | First-level TR 104B, walls/door/ceiling/floor, security devices, IU-1-01 location and pathways | 0 | Paul | 0 | B09-R1/B09-R4 | Closed | 0 | 09¦68
09 | 69 | B09_Assessment | 76 | 10. PHOTO LOG | DATA | B09-P003 | 206A | Existing Condition | Second-level TR 206A, walls/door/ceiling/floor, adjacent Nursing Service 206, IU-2-01 location and pathways | 0 | Paul | 0 | B09-R1/B09-R4 | Closed | 0 | 09¦69
09 | 70 | B09_Assessment | 77 | 10. PHOTO LOG | DATA | B09-P004 | All | Hazardous Materials | Flooring, ceilings, pipe insulation, penetrations and abatement-related locations before disturbance | 0 | Paul | 0 | B09-R3 | Closed | 0 | 09¦70
09 | 71 | B09_Assessment | 78 | 10. PHOTO LOG | DATA | B09-P005 | All | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B09-R7 | Closed | 0 | 09¦71
09 | 72 | B09_Assessment | 79 | 10. PHOTO LOG | DATA | B09-P006 | All | HVAC | IU/CU equipment, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B09-R5 | Closed | 0 | 09¦72
09 | 73 | B09_Assessment | 80 | 10. PHOTO LOG | DATA | B09-P007 | All | Electrical | B09 TR panels, breakers, SPD, rack receptacles, access controllers, lighting and labels | 0 | Paul | 0 | B09-R6 | Closed | 0 | 09¦73
09 | 74 | B09_Assessment | 81 | 10. PHOTO LOG | DATA | B09-P008 | All | Telecom/Security | Racks, fiber, Cat6A, LIU, patch panels, labeling/testing, cameras, access control and VMS/PACS integration | 0 | Paul | 0 | B09-R8 | Closed | 0 | 09¦74
09 | 75 | B09_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 09¦75
10 | 1 | B10_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦1
10 | 2 | B10_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 10¦2
10 | 3 | B10_Assessment | 10 | 1. ROOM INVENTORY | DATA | 10 | 200A | Attic | Existing attic telecom/equipment area | Telecom Room | 2 | 1 | Verify | 10A-401 / 10E-401 / 10T-604 / 10M-701 | Primary Building 10 TR. Drawings identify attic-level Room 200A with existing wall-mounted rack/equipment, new telecom rack equipment, panels B10-TR200AA/AB, IU-1-01, CU-1-01, rack receptacles and future rack space. | 10¦3
10 | 4 | B10_Assessment | 11 | 1. ROOM INVENTORY | DATA | 10 | B24 | Basement | Existing electrical room - normal power | Electrical source / coordination room | 0 | 0 | Verify | 10E-401 / 10E-701 | Basement existing electrical room normal power referenced on electrical enlarged plan; coordinate B10-MDP/B10-L10-E feeders and load measurement. | 10¦4
10 | 5 | B10_Assessment | 12 | 1. ROOM INVENTORY | DATA | 10 | B25 | Basement | Existing electrical room - emergency power | Emergency electrical source / coordination room | 0 | 0 | Verify | 10E-401 / 10E-601 / 10E-701 | Basement existing electrical room emergency power referenced on electrical enlarged plan; coordinate ATS-B10-LSD, emergency source and TR equipment continuity. | 10¦5
10 | 6 | B10_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦6
10 | 7 | B10_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦7
10 | 8 | B10_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 10¦8
10 | 9 | B10_Assessment | 16 | 2. ROOM READINESS | DATA | 200A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Attic TR; verify room enclosure, open-to-deck/rated wall requirements, existing rack/equipment, attic access, structural/pathway clearance, future rack clearance and housekeeping. | 10¦9
10 | 10 | B10_Assessment | 17 | 2. ROOM READINESS | DATA | B24 | N/A | N/A | N/A | Verify | N/A | Verify | Verify | Verify | Electrical source room; verify panel access, breaker/feeder routes, lockout/tagout needs and working clearances. | 10¦10
10 | 11 | B10_Assessment | 18 | 2. ROOM READINESS | DATA | B25 | N/A | N/A | N/A | Verify | N/A | Verify | Verify | Verify | Emergency electrical source room; verify ATS/emergency panel access, shutdown constraints and power continuity. | 10¦11
10 | 12 | B10_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦12
10 | 13 | B10_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦13
10 | 14 | B10_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 10¦14
10 | 15 | B10_Assessment | 22 | 3. FIRE PROTECTION | DATA | 200A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping. | 10¦15
10 | 16 | B10_Assessment | 23 | 3. FIRE PROTECTION | DATA | B24 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place. | 10¦16
10 | 17 | B10_Assessment | 24 | 3. FIRE PROTECTION | DATA | B25 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment. | 10¦17
10 | 18 | B10_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦18
10 | 19 | B10_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦19
10 | 20 | B10_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 10¦20
10 | 21 | B10_Assessment | 28 | 4. HVAC / COOLING | DATA | 200A | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm. | 10¦21
10 | 22 | B10_Assessment | 29 | 4. HVAC / COOLING | DATA | B24 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work. | 10¦22
10 | 23 | B10_Assessment | 30 | 4. HVAC / COOLING | DATA | B25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted. | 10¦23
10 | 24 | B10_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦24
10 | 25 | B10_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦25
10 | 26 | B10_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 10¦26
10 | 27 | B10_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | 200A | Verify | 5 kW / rack equipment | Verify | Verify | B10-TR200AA / B10-TR200AB | Verify | Verify | Verify | Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels. | 10¦27
10 | 28 | B10_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | B24 | N/A | N/A | N/A | N/A | B10-MDP / B10-L10-E | Verify | Verify | Verify | Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing. | 10¦28
10 | 29 | B10_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | B25 | N/A | N/A | N/A | N/A | ATS-B10-LSD / emergency distribution | Verify | Verify | Verify | Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required. | 10¦29
10 | 30 | B10_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦30
10 | 31 | B10_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦31
10 | 32 | B10_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 10¦32
10 | 33 | B10_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | 200A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover. | 10¦33
10 | 34 | B10_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | B24 | N/A | N/A | N/A | Verify | N/A | N/A | N/A | Verify | Coordinate telecom power pathways through/source from basement electrical room if applicable. | 10¦34
10 | 35 | B10_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | B25 | N/A | N/A | N/A | Verify | N/A | N/A | N/A | Verify | Coordinate emergency source/backup power pathways for telecom equipment and cooling. | 10¦35
10 | 36 | B10_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦36
10 | 37 | B10_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦37
10 | 38 | B10_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 10¦38
10 | 39 | B10_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | 200A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | General scope requires PACS/CCTV for TR doors; verify door hardware, access controller, camera/VMS integration and any existing attic access/security constraints. | 10¦39
10 | 40 | B10_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | B24 | N/A | N/A | N/A | N/A | Verify | N/A | Verify | Verify | Verify security impact only if electrical source room access or devices are modified. | 10¦40
10 | 41 | B10_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | B25 | N/A | N/A | N/A | N/A | Verify | N/A | Verify | Verify | Verify emergency electrical room security impact if work requires access control changes. | 10¦41
10 | 42 | B10_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦42
10 | 43 | B10_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦43
10 | 44 | B10_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 10¦44
10 | 45 | B10_Assessment | 52 | 8. OWNER RISKS | DATA | B10-R1 | 200A | Attic Telecom Room existing conditions and access not field verified | High | Medium | 6 | Survey Room 200A, attic access route, existing rack/equipment, floor/deck conditions, clearances and utilities | GCC / Contractor | Closed | Attic work may have access and staging constraints. | 10¦45
10 | 46 | B10_Assessment | 53 | 8. OWNER RISKS | DATA | B10-R2 | 200A | Hazardous material abatement plan exists for attic level | High | Medium | 6 | Coordinate attic abatement/IH review before penetrations, ceiling/floor work, cabling or HVAC/electrical installation | GC / IH / COR | Closed | Drawing index includes 10H-102 hazardous material abatement plan - attic. | 10¦46
10 | 47 | B10_Assessment | 54 | 8. OWNER RISKS | DATA | B10-R3 | 200A | Existing wall-mounted rack/equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place and develop night-shift cutover/temporary rack plan | Telecom / OIT | Closed | Telecom drawings reference existing wall-mounted rack/equipment to be replaced/transferred. | 10¦47
10 | 48 | B10_Assessment | 55 | 8. OWNER RISKS | DATA | B10-R4 | 200A | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 capacity, power source, condensate routing, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 10¦48
10 | 49 | B10_Assessment | 56 | 8. OWNER RISKS | DATA | B10-R5 | B24/B25 | Panel source, generator/ATS path and shutdown sequencing unclear | Critical | Medium | 8 | Verify B10-MDP, B10-L10-E, ATS-B10-LSD, panel feeders, load measurement and LOTO before electrical work | Electrical / GCC | Closed | Basement normal/emergency electrical rooms are source coordination points. | 10¦49
10 | 50 | B10_Assessment | 57 | 8. OWNER RISKS | DATA | B10-R6 | 200A | Fire alarm/sprinkler/firestopping work in attic TR could affect occupied operations | Critical | Medium | 8 | Track impairments, fire watch, sprinkler/head changes, FA device work, rated penetrations and temporary firestopping | GC / FP / FA | Closed | Shutdowns limited one at a time campus-wide. | 10¦50
10 | 51 | B10_Assessment | 58 | 8. OWNER RISKS | DATA | B10-R7 | 200A | Telecom/fiber cutover could affect active hospital communications | Critical | Medium | 8 | Require cutover plan, testing, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | All telecom cabling must be tested, approved and accepted before connecting to active operations. | 10¦51
10 | 52 | B10_Assessment | 59 | 8. OWNER RISKS | DATA | B10-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, test reports, power verification, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 10¦52
10 | 53 | B10_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦53
10 | 54 | B10_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦54
10 | 55 | B10_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 10¦55
10 | 56 | B10_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B10-Q1 | Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 10¦56
10 | 57 | B10_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B10-Q2 | What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? | OIT / Contractor | Closed | 0 | 0 | Potential communications outage | 0 | 0 | 0 | 10¦57
10 | 58 | B10_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B10-Q3 | What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? | GC / IH / COR | Closed | 0 | 0 | Work delay/exposure risk | 0 | 0 | 0 | 10¦58
10 | 59 | B10_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B10-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 10¦59
10 | 60 | B10_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B10-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 10¦60
10 | 61 | B10_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B10-Q6 | Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 10¦61
10 | 62 | B10_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B10-Q7 | Are all attic wall/floor/ceiling penetrations, sleeves and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 10¦62
10 | 63 | B10_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B10-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 10¦63
10 | 64 | B10_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦64
10 | 65 | B10_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦65
10 | 66 | B10_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 10¦66
10 | 67 | B10_Assessment | 74 | 10. PHOTO LOG | DATA | B10-P001 | 200A | Existing Condition | Attic TR 200A existing rack/equipment, floor/deck, walls, access route, pathways and clearances | 0 | Paul | 0 | B10-R1/B10-R3 | Closed | 0 | 10¦67
10 | 68 | B10_Assessment | 75 | 10. PHOTO LOG | DATA | B10-P002 | 200A | Hazardous Materials | Attic abatement-related materials, flooring/penetrations, ceiling/deck and disturbance areas | 0 | Paul | 0 | B10-R2 | Closed | 0 | 10¦68
10 | 69 | B10_Assessment | 76 | 10. PHOTO LOG | DATA | B10-P003 | B24 | Electrical | Existing normal electrical room panels, B10-MDP/B10-L10-E, feeder route and working clearances | 0 | Paul | 0 | B10-R5 | Closed | 0 | 10¦69
10 | 70 | B10_Assessment | 77 | 10. PHOTO LOG | DATA | B10-P004 | B25 | Electrical | Existing emergency electrical room, ATS-B10-LSD/emergency distribution and access constraints | 0 | Paul | 0 | B10-R5 | Closed | 0 | 10¦70
10 | 71 | B10_Assessment | 78 | 10. PHOTO LOG | DATA | B10-P005 | 200A | Firestop | All attic wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B10-R6 | Closed | 0 | 10¦71
10 | 72 | B10_Assessment | 79 | 10. PHOTO LOG | DATA | B10-P006 | 200A | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B10-R4 | Closed | 0 | 10¦72
10 | 73 | B10_Assessment | 80 | 10. PHOTO LOG | DATA | B10-P007 | 200A | Telecom | Racks, UPS/PDU, fiber, Cat6A, patch panels, LIU, bonding, labels and test records | 0 | Paul | 0 | B10-R7 | Closed | 0 | 10¦73
10 | 74 | B10_Assessment | 81 | 10. PHOTO LOG | DATA | B10-P008 | 200A | Security | Card reader, electric strike, door position, CCTV/PACS, motion sensor and VMS/PACS integration | 0 | Paul | 0 | B10-R8 | Closed | 0 | 10¦74
10 | 75 | B10_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10¦75
12 | 1 | B12_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦1
12 | 2 | B12_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 12¦2
12 | 3 | B12_Assessment | 10 | 1. ROOM INVENTORY | DATA | 12 | 00 / existing fiber path | B/1/2 | Existing building fiber pathway / pull-through route | Fiber-only pull-through scope | 0 | 0 | Verify | 12G-000 / 12T-100 / 12T-101 / 12T-604 | Cover sheet states Building 12 receives fiber only. Rack elevation sheet identifies Building 12 as existing rack elevation/fiber only with no rack mounting and no new TR buildout. | 12¦3
12 | 4 | B12_Assessment | 11 | 1. ROOM INVENTORY | DATA | 12 | Existing rack/demarc - field verify | Field verify | Existing service point / serving closet | Protect-in-place / fiber transition point | 0 | 0 | Verify | 12T-604 / 12T-601 / 12T-602 / 12T-603A/B | 12T-604 identifies building level B/1/2 and mounting type NONE/FIBER ONLY. Field verification required to document where fiber enters, passes through, and terminates. | 12¦4
12 | 5 | B12_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦5
12 | 6 | B12_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦6
12 | 7 | B12_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 12¦7
12 | 8 | B12_Assessment | 15 | 2. ROOM READINESS | DATA | Fiber path B/1/2 | N/A / Verify | N/A / Verify | N/A | Verify | N/A | Verify | Verify | Verify | No new TR room indicated; focus is route readiness, penetrations, cable tray/conduit capacity, and access to existing pathway. | 12¦8
12 | 9 | B12_Assessment | 16 | 2. ROOM READINESS | DATA | Existing rack/demarc - field verify | N/A / Verify | N/A / Verify | N/A | Verify | N/A / Verify | Verify | Verify | Verify | Confirm existing equipment, demarc, or closet location; protect active services and confirm no new rack required. | 12¦9
12 | 10 | B12_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦10
12 | 11 | B12_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦11
12 | 12 | B12_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 12¦12
12 | 13 | B12_Assessment | 20 | 3. FIRE PROTECTION | DATA | Fiber path B/1/2 | N/A | N/A | N/A / Verify | N/A / Verify | N/A | Verify | Verify | Verify | No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route. | 12¦13
12 | 14 | B12_Assessment | 21 | 3. FIRE PROTECTION | DATA | Existing rack/demarc - field verify | N/A | N/A | N/A / Verify | N/A / Verify | N/A | Verify | Verify | Verify | No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work. | 12¦14
12 | 15 | B12_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦15
12 | 16 | B12_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦16
12 | 17 | B12_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 12¦17
12 | 18 | B12_Assessment | 25 | 4. HVAC / COOLING | DATA | Fiber path B/1/2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment. | 12¦18
12 | 19 | B12_Assessment | 26 | 4. HVAC / COOLING | DATA | Existing rack/demarc - field verify | Existing / N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Field verify existing environmental conditions only if existing service point/equipment is accessed. | 12¦19
12 | 20 | B12_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦20
12 | 21 | B12_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦21
12 | 22 | B12_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 12¦22
12 | 23 | B12_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | Fiber path B/1/2 | N/A | N/A | N/A | N/A | N/A | N/A | Labeling Verify | Verify | No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown. | 12¦23
12 | 24 | B12_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | Existing rack/demarc - field verify | Existing / N/A | N/A | N/A | N/A | N/A | N/A | Labeling Verify | Verify | Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling. | 12¦24
12 | 25 | B12_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦25
12 | 26 | B12_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦26
12 | 27 | B12_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 12¦27
12 | 28 | B12_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | Fiber path B/1/2 | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing. | 12¦28
12 | 29 | B12_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | Existing rack/demarc - field verify | Existing / none new | N/A / Verify | Verify | Verify | Verify | Verify | Verify | Verify | 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only. | 12¦29
12 | 30 | B12_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦30
12 | 31 | B12_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦31
12 | 32 | B12_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 12¦32
12 | 33 | B12_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | Fiber path B/1/2 | N/A | N/A | N/A | N/A | N/A / Verify | N/A | N/A | N/A / Verify | No new TR door or PACS/CCTV package shown for Building 12; verify security access only for work areas and existing equipment rooms. | 12¦33
12 | 34 | B12_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | Existing rack/demarc - field verify | N/A / Verify | N/A / Verify | N/A | N/A | N/A / Verify | N/A | N/A | N/A / Verify | Confirm access requirements to existing closet/demarc while protecting active operations. | 12¦34
12 | 35 | B12_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦35
12 | 36 | B12_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦36
12 | 37 | B12_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 12¦37
12 | 38 | B12_Assessment | 45 | 8. OWNER RISKS | DATA | B12-R1 | All | Fiber-only scope could be mistaken for full TR scope or skipped as minor work | High | Medium | 6 | Clearly tag Building 12 as fiber-only and verify required fiber path, testing, labels and acceptance deliverables | GCC / OIT / GC | Closed | Cover sheet note says this building is to receive fiber only. | 12¦38
12 | 39 | B12_Assessment | 46 | 8. OWNER RISKS | DATA | B12-R2 | Fiber path B/1/2 | Existing pull-through pathway not field verified | High | Medium | 6 | Trace basement/first/second level pathway, conduit/cable tray capacity, pull points and access before scheduled pull | Telecom Contractor | Closed | 12T-100/101 plan sheets and 12T-604 identify fiber-only B/1/2 scope. | 12¦39
12 | 40 | B12_Assessment | 47 | 8. OWNER RISKS | DATA | B12-R3 | All | Existing service continuity during fiber pull/cutover may not be defined | Critical | Medium | 8 | Coordinate with VA OIT, submit phasing/cutover plan, and maintain legacy service until new fiber is tested and accepted | OIT / Telecom | Closed | All telecom cabling must be tested, approved and accepted before active connection. | 12¦40
12 | 41 | B12_Assessment | 48 | 8. OWNER RISKS | DATA | B12-R4 | All | Pathway penetrations/firestopping may be overlooked because there is no architectural/FP package | High | Medium | 6 | Inspect all new/reused penetrations and require permanent or temporary firestopping at end of shift | GC / Firestop | Closed | General notes still require firestopping for floor/rated wall penetrations. | 12¦41
12 | 42 | B12_Assessment | 49 | 8. OWNER RISKS | DATA | B12-R5 | Existing rack/demarc - field verify | Existing termination/demarc location and ownership unclear | Medium | Medium | 4 | Field document existing rack/demarc/serving closet and confirm where new fiber terminates or passes through | GCC / OIT | Closed | 12T-604 shows room/rack as 00; actual field condition must be documented. | 12¦42
12 | 43 | B12_Assessment | 50 | 8. OWNER RISKS | DATA | B12-R6 | All | Test reports, labels and as-builts may be incomplete for fiber-only work | High | Medium | 6 | Track fiber OTDR/certification, labeling, route documentation and VA/OIT acceptance before closeout | Telecom / GCC | Closed | Fiber-only work still requires record drawings and acceptance. | 12¦43
12 | 44 | B12_Assessment | 51 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦44
12 | 45 | B12_Assessment | 52 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦45
12 | 46 | B12_Assessment | 53 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 12¦46
12 | 47 | B12_Assessment | 54 | 9. OPEN QUESTIONS | DATA | B12-Q1 | Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? | VA / OIT / Designer | Closed | 0 | 0 | Scope misunderstanding | 0 | 0 | 0 | 12¦47
12 | 48 | B12_Assessment | 55 | 9. OPEN QUESTIONS | DATA | B12-Q2 | What exact pathway does the Building 12 fiber take through basement, first and second levels? | Telecom Contractor / OIT | Closed | 0 | 0 | Fiber pull and access risk | 0 | 0 | 0 | 12¦48
12 | 49 | B12_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B12-Q3 | Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? | OIT / Contractor | Closed | 0 | 0 | Termination and ownership unclear | 0 | 0 | 0 | 12¦49
12 | 50 | B12_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B12-Q4 | Are existing conduits/cable trays available and below fill limits for the new fiber? | Telecom Contractor | Closed | 0 | 0 | Pathway capacity risk | 0 | 0 | 0 | 12¦50
12 | 51 | B12_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B12-Q5 | Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? | GC / Firestop | Closed | 0 | 0 | Life safety/firestop risk | 0 | 0 | 0 | 12¦51
12 | 52 | B12_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B12-Q6 | What is the approved cutover/testing/acceptance sequence for Building 12 fiber? | OIT / COR / Contractor | Closed | 0 | 0 | Possible outage or acceptance delay | 0 | 0 | 0 | 12¦52
12 | 53 | B12_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B12-Q7 | Which fiber test reports, labels, route documentation and as-builts are required for closeout? | Telecom / GCC | Closed | 0 | 0 | Closeout documentation gap | 0 | 0 | 0 | 12¦53
12 | 54 | B12_Assessment | 61 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦54
12 | 55 | B12_Assessment | 62 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦55
12 | 56 | B12_Assessment | 63 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 12¦56
12 | 57 | B12_Assessment | 64 | 10. PHOTO LOG | DATA | B12-P001 | Fiber path B/1/2 | Existing Condition | Existing conduit/cable tray/pathway from entry through basement/first/second levels | 0 | Paul | 0 | B12-R2 | Closed | 0 | 12¦57
12 | 58 | B12_Assessment | 65 | 10. PHOTO LOG | DATA | B12-P002 | Existing rack/demarc - field verify | Existing Condition | Existing rack, demarc, serving closet or fiber termination/pass-through point | 0 | Paul | 0 | B12-R5 | Closed | 0 | 12¦58
12 | 59 | B12_Assessment | 66 | 10. PHOTO LOG | DATA | B12-P003 | All | Firestop | All floor/wall/sleeve penetrations before pull, during work, and after permanent firestop | 0 | Paul | 0 | B12-R4 | Closed | 0 | 12¦59
12 | 60 | B12_Assessment | 67 | 10. PHOTO LOG | DATA | B12-P004 | All | Telecom | Fiber reels, pull route, pull boxes, labels, slack loops, termination points and test records | 0 | Paul | 0 | B12-R3/B12-R6 | Closed | 0 | 12¦60
12 | 61 | B12_Assessment | 68 | 10. PHOTO LOG | DATA | B12-P005 | All | Closeout | Fiber certification/OTDR screenshots, labeling, as-built route and VA/OIT acceptance evidence | 0 | Paul | 0 | B12-R6 | Closed | 0 | 12¦61
12 | 62 | B12_Assessment | 69 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12¦62
13 | 1 | B13_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦1
13 | 2 | B13_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 13¦2
13 | 3 | B13_Assessment | 10 | 1. ROOM INVENTORY | DATA | 13 | 124 | First | Telecom Room / new TR build area | Telecom Room | 2 | 1 | Verify | 13A-401 / 13E-401 / 13T-100 / 13T-701 | Primary Building 13 TR. Plans identify Telecom Room 124 at 119 SF, served by Rack ID TR01-124-1, panels B13-TR124AA/AB, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, and a future rack allowance. | 13¦3
13 | 4 | B13_Assessment | 11 | 1. ROOM INVENTORY | DATA | 13 | 222 | Second | Existing Tel Room / existing rack and patching area | Existing telecom transition point | 1 | 0 | Verify | 13T-100 / 13R-900 | Existing second-level Tel Room 222 shown with existing telco patch, plywood backboard, indoor AC unit, wall-mounted rack, patch panel, and security cabinet. Protect active services and verify what is transferred to Room 124. | 13¦4
13 | 5 | B13_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦5
13 | 6 | B13_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦6
13 | 7 | B13_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 13¦7
13 | 8 | B13_Assessment | 15 | 2. ROOM READINESS | DATA | 124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack clearances, wall backing, and pathway entry points. | 13¦8
13 | 9 | B13_Assessment | 16 | 2. ROOM READINESS | DATA | 222 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing second-floor tel room; verify existing equipment status, pathway, AC unit, backboard, and transition/abandonment scope. | 13¦9
13 | 10 | B13_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦10
13 | 11 | B13_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦11
13 | 12 | B13_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 13¦12
13 | 13 | B13_Assessment | 20 | 3. FIRE PROTECTION | DATA | 124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | 13¦13
13 | 14 | B13_Assessment | 21 | 3. FIRE PROTECTION | DATA | 222 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | 13¦14
13 | 15 | B13_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦15
13 | 16 | B13_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦16
13 | 17 | B13_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 13¦17
13 | 18 | B13_Assessment | 25 | 4. HVAC / COOLING | DATA | 124 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | 13¦18
13 | 19 | B13_Assessment | 26 | 4. HVAC / COOLING | DATA | 222 | Existing indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | 13¦19
13 | 20 | B13_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦20
13 | 21 | B13_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦21
13 | 22 | B13_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 13¦22
13 | 23 | B13_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | 124 | Verify | 5 kW / 240V rack UPS | Verify | Verify | B13-TR124AA / B13-TR124AB | Verify | Verify | Verify | Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements. | 13¦23
13 | 24 | B13_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | 222 | Existing | Existing | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | 13¦24
13 | 25 | B13_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦25
13 | 26 | B13_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦26
13 | 27 | B13_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 13¦27
13 | 28 | B13_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | 124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B. | 13¦28
13 | 29 | B13_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | 222 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124. | 13¦29
13 | 30 | B13_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦30
13 | 31 | B13_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦31
13 | 32 | B13_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 13¦32
13 | 33 | B13_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | 124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical enlarged plan shows security/access-control device callouts at Room 124 and 124-CAM-01 camera designation; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | 13¦33
13 | 34 | B13_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | 222 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | 13¦34
13 | 35 | B13_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦35
13 | 36 | B13_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦36
13 | 37 | B13_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 13¦37
13 | 38 | B13_Assessment | 45 | 8. OWNER RISKS | DATA | B13-R1 | All | Existing conditions for Room 124 and existing Tel Room 222 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B13 includes new TR plus existing second-level tel transition point. | 13¦38
13 | 39 | B13_Assessment | 46 | 8. OWNER RISKS | DATA | B13-R2 | 124 | First-level hazardous material abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | Drawing index includes 13H-101 hazardous material abatement plan - first level. | 13¦39
13 | 40 | B13_Assessment | 47 | 8. OWNER RISKS | DATA | B13-R3 | 222 | Existing Tel Room 222 equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing rack/backboard/security/patch equipment shown. | 13¦40
13 | 41 | B13_Assessment | 48 | 8. OWNER RISKS | DATA | B13-R4 | 124 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 13¦41
13 | 42 | B13_Assessment | 49 | 8. OWNER RISKS | DATA | B13-R5 | 124 | 240V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B13-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs | Electrical / GCC | Closed | Panel and circuit references are concentrated at Room 124. | 13¦42
13 | 43 | B13_Assessment | 50 | 8. OWNER RISKS | DATA | B13-R6 | 124 | Rated wall/door/firestop scope may affect life-safety acceptance | High | Medium | 6 | Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | GC / FP / FA | Closed | New TRs must be 1-hour fire/smoke rated. | 13¦43
13 | 44 | B13_Assessment | 51 | 8. OWNER RISKS | DATA | B13-R7 | All | Telecom/fiber cutover could affect active hospital communications across first and second levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | 13T-701 shows Room 124 serving large port count and Level 2 outlets. | 13¦44
13 | 45 | B13_Assessment | 52 | 8. OWNER RISKS | DATA | B13-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 13¦45
13 | 46 | B13_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦46
13 | 47 | B13_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦47
13 | 48 | B13_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 13¦48
13 | 49 | B13_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B13-Q1 | Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 13¦49
13 | 50 | B13_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B13-Q2 | What active services are currently fed from existing Tel Room 222 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 13¦50
13 | 51 | B13_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B13-Q3 | What hazardous/abatement steps apply to first-level Room 124 work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0 | 13¦51
13 | 52 | B13_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B13-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 13¦52
13 | 53 | B13_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B13-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 13¦53
13 | 54 | B13_Assessment | 61 | 9. OPEN QUESTIONS | DATA | B13-Q6 | Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 13¦54
13 | 55 | B13_Assessment | 62 | 9. OPEN QUESTIONS | DATA | B13-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 13¦55
13 | 56 | B13_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B13-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 13¦56
13 | 57 | B13_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦57
13 | 58 | B13_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦58
13 | 59 | B13_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 13¦59
13 | 60 | B13_Assessment | 67 | 10. PHOTO LOG | DATA | B13-P001 | 124 | Existing Condition | Room 124 walls, ceiling/deck, floor, door, adjacent Telehealth 124A/109, rack location, pathways and penetrations | 0 | Paul | 0 | B13-R1/B13-R6 | Closed | 0 | 13¦60
13 | 61 | B13_Assessment | 68 | 10. PHOTO LOG | DATA | B13-P002 | 222 | Existing Condition | Existing Tel Room 222 wall rack, telco patch, plywood backboard, AC unit, patch panel and security cabinet | 0 | Paul | 0 | B13-R1/B13-R3 | Closed | 0 | 13¦61
13 | 62 | B13_Assessment | 69 | 10. PHOTO LOG | DATA | B13-P003 | 124 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B13-R2 | Closed | 0 | 13¦62
13 | 63 | B13_Assessment | 70 | 10. PHOTO LOG | DATA | B13-P004 | 124 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B13-R6 | Closed | 0 | 13¦63
13 | 64 | B13_Assessment | 71 | 10. PHOTO LOG | DATA | B13-P005 | 124 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B13-R4 | Closed | 0 | 13¦64
13 | 65 | B13_Assessment | 72 | 10. PHOTO LOG | DATA | B13-P006 | 124 | Electrical | B13-TR124AA/AB panels, rack receptacles, breakers, SPD, access controller, lighting and labels | 0 | Paul | 0 | B13-R5 | Closed | 0 | 13¦65
13 | 66 | B13_Assessment | 73 | 10. PHOTO LOG | DATA | B13-P007 | 124/222 | Telecom | New racks, fiber path A/B, Cat6A, patch panels, LIU, labels/test records and existing Room 222 transfer work | 0 | Paul | 0 | B13-R7 | Closed | 0 | 13¦66
13 | 67 | B13_Assessment | 74 | 10. PHOTO LOG | DATA | B13-P008 | 124/222 | Security | 124-CAM-01, card reader, electric strike, door position, motion sensor, existing security cabinet and VMS/PACS integration | 0 | Paul | 0 | B13-R8 | Closed | 0 | 13¦67
13 | 68 | B13_Assessment | 75 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13¦68
14 | 1 | B14_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦1
14 | 2 | B14_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 14¦2
14 | 3 | B14_Assessment | 10 | 1. ROOM INVENTORY | DATA | 14 | 119 | First | Telecom Room / new TR build area | Telecom Room | 1 | 1 | Verify | 14A-401 / 14E-100 / 14T-100 / 14T-604 / 14T-701 | Primary Building 14 TR. Plans identify Telecom Room 119 at 124 SF, served by Rack ID TR01-119-1, panels B14-TR119A/B, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, 56 feet of first-level cable tray, and a future rack allowance. | 14¦3
14 | 4 | B14_Assessment | 11 | 1. ROOM INVENTORY | DATA | 14 | B.01 | Basement | Existing Tel/F Panel room / telecom equipment area | Existing telecom transition point | 1 | 0 | Verify | 14T-100 / 14T-604 / 14R-900 | Existing basement Tel/F Panel B.01 shown at 165 SF with existing wall-mounted TE, patch panels, telco patch, plywood backboards, and legacy fiber/equipment. Protect active services and verify what transfers to Room 119. | 14¦4
14 | 5 | B14_Assessment | 12 | 1. ROOM INVENTORY | DATA | 14 | B2 | Basement | Existing telecom room reference | Existing telecom transition point | 1 | 0 | Verify | 14R-900 | Photo reference sheet identifies basement existing telecom room B2. Field verify whether B2 is same/related to B.01 or separate legacy telecom space. | 14¦5
14 | 6 | B14_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦6
14 | 7 | B14_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦7
14 | 8 | B14_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 14¦8
14 | 9 | B14_Assessment | 16 | 2. ROOM READINESS | DATA | 119 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack/future rack clearances, wall backing, and pathway entry points. | 14¦9
14 | 10 | B14_Assessment | 17 | 2. ROOM READINESS | DATA | B.01 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room; verify active equipment status, pathway, backboards, wall-mounted TE, and transition/abandonment scope. | 14¦10
14 | 11 | B14_Assessment | 18 | 2. ROOM READINESS | DATA | B2 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room photo reference; verify whether active services/equipment remain and confirm relationship to B.01. | 14¦11
14 | 12 | B14_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦12
14 | 13 | B14_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦13
14 | 14 | B14_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 14¦14
14 | 15 | B14_Assessment | 22 | 3. FIRE PROTECTION | DATA | 119 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | 14¦15
14 | 16 | B14_Assessment | 23 | 3. FIRE PROTECTION | DATA | B.01 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | 14¦16
14 | 17 | B14_Assessment | 24 | 3. FIRE PROTECTION | DATA | B2 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room; verify no unsealed penetrations remain after cable transfer or reuse. | 14¦17
14 | 18 | B14_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦18
14 | 19 | B14_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦19
14 | 20 | B14_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 14¦20
14 | 21 | B14_Assessment | 28 | 4. HVAC / COOLING | DATA | 119 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 119 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | 14¦21
14 | 22 | B14_Assessment | 29 | 4. HVAC / COOLING | DATA | B.01 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Tel/F Panel room; verify existing environmental conditions during cutover and whether legacy equipment remains active. | 14¦22
14 | 23 | B14_Assessment | 30 | 4. HVAC / COOLING | DATA | B2 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom room reference; field verify cooling/ventilation and active equipment condition. | 14¦23
14 | 24 | B14_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦24
14 | 25 | B14_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦25
14 | 26 | B14_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 14¦26
14 | 27 | B14_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | 119 | Verify | 5 kW / 240V rack UPS | Verify | Verify | B14-TR119A / B14-TR119B | Verify | Verify | Verify | Electrical plan/schedules identify B14-TR119A/B, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and panel load measurement requirements. | 14¦27
14 | 28 | B14_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | B.01 | Existing | Existing | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing basement wall-mounted TE/equipment area; verify power source, active equipment, UPS/PDU status, and transition requirements before disconnect or removal. | 14¦28
14 | 29 | B14_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | B2 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing telecom room photo reference; confirm power sources and any cutover requirements. | 14¦29
14 | 30 | B14_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦30
14 | 31 | B14_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦31
14 | 32 | B14_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 14¦32
14 | 33 | B14_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | 119 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 14T-701 identifies Room 119 schedule: 44 WAO total, 29 active ports per survey, 76 total ports per schedule, and 84 total ports with 10% allowance. New Rack ID TR01-119-1 serves first and second level outlets with Fiber Path A/B. | 14¦33
14 | 34 | B14_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | B.01 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room B.01 equipment includes wall-mounted TE, Cisco switch/legacy patch panel, telco patch, plywood backboards, and legacy Fiber LIU; verify active services and transfer plan to Room 119. | 14¦34
14 | 35 | B14_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | B2 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room B2 is identified by photo reference; verify active devices, routing, and relation to B.01. | 14¦35
14 | 36 | B14_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦36
14 | 37 | B14_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦37
14 | 38 | B14_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 14¦38
14 | 39 | B14_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | 119 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 119-CAM-01 and security/access-control scope for Room 119; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | 14¦39
14 | 40 | B14_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | B.01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify whether existing security equipment remains, is relocated, or requires temporary protection during cutover. | 14¦40
14 | 41 | B14_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | B2 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify security/access conditions and whether any legacy security equipment is present. | 14¦41
14 | 42 | B14_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦42
14 | 43 | B14_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦43
14 | 44 | B14_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 14¦44
14 | 45 | B14_Assessment | 52 | 8. OWNER RISKS | DATA | B14-R1 | All | Existing conditions for Room 119 and existing basement telecom rooms B.01/B2 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B14 includes new TR plus existing basement telecom transition points. | 14¦45
14 | 46 | B14_Assessment | 53 | 8. OWNER RISKS | DATA | B14-R2 | 119 | First-level hazardous material abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | Drawing index includes 14H-101 hazardous material abatement plan - first level; page 6 notes lead-based paint abatement in room/restroom context. | 14¦46
14 | 47 | B14_Assessment | 54 | 8. OWNER RISKS | DATA | B14-R3 | B.01/B2 | Existing basement telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing wall-mounted TE, patch panels, telco patch and legacy Fiber LIU shown. | 14¦47
14 | 48 | B14_Assessment | 55 | 8. OWNER RISKS | DATA | B14-R4 | 119 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 14¦48
14 | 49 | B14_Assessment | 56 | 8. OWNER RISKS | DATA | B14-R5 | 119 | 240V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B14-TR119A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs | Electrical / GCC | Closed | Panel and circuit references are concentrated at Room 119. | 14¦49
14 | 50 | B14_Assessment | 57 | 8. OWNER RISKS | DATA | B14-R6 | 119 | Rated wall/door/firestop scope may affect life-safety acceptance | High | Medium | 6 | Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | GC / FP / FA | Closed | New TRs must be 1-hour fire/smoke rated. | 14¦50
14 | 51 | B14_Assessment | 58 | 8. OWNER RISKS | DATA | B14-R7 | All | Telecom/fiber cutover could affect active hospital communications across basement, first and second levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | 14T-701 shows Room 119 serving Level 1 and Level 2 outlets with 84 total ports including allowance. | 14¦51
14 | 52 | B14_Assessment | 59 | 8. OWNER RISKS | DATA | B14-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 14¦52
14 | 53 | B14_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦53
14 | 54 | B14_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦54
14 | 55 | B14_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 14¦55
14 | 56 | B14_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B14-Q1 | Confirm final telecom scope: new Room 119 and existing basement B.01/B2 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 14¦56
14 | 57 | B14_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B14-Q2 | What active services are currently fed from existing B.01/B2 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 14¦57
14 | 58 | B14_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B14-Q3 | What hazardous/abatement steps apply to first-level Room 119 work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0 | 14¦58
14 | 59 | B14_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B14-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 119? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 14¦59
14 | 60 | B14_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B14-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 119? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 14¦60
14 | 61 | B14_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B14-Q6 | Are B14-TR119A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 14¦61
14 | 62 | B14_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B14-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 14¦62
14 | 63 | B14_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B14-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 14¦63
14 | 64 | B14_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦64
14 | 65 | B14_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦65
14 | 66 | B14_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 14¦66
14 | 67 | B14_Assessment | 74 | 10. PHOTO LOG | DATA | B14-P001 | 119 | Existing Condition | Room 119 walls, ceiling/deck, floor, door, adjacent conference/restroom/office spaces, rack location, pathways and penetrations | 0 | Paul | 0 | B14-R1/B14-R6 | Closed | 0 | 14¦67
14 | 68 | B14_Assessment | 75 | 10. PHOTO LOG | DATA | B14-P002 | B.01 | Existing Condition | Existing basement Tel/F Panel B.01, wall-mounted TE, patch panels, telco patch, plywood backboards, legacy Fiber LIU and pathways | 0 | Paul | 0 | B14-R1/B14-R3 | Closed | 0 | 14¦68
14 | 69 | B14_Assessment | 76 | 10. PHOTO LOG | DATA | B14-P003 | B2 | Existing Condition | Existing basement telecom room B2 photo reference, equipment, pathways, power and protection-in-place needs | 0 | Paul | 0 | B14-R1/B14-R3 | Closed | 0 | 14¦69
14 | 70 | B14_Assessment | 77 | 10. PHOTO LOG | DATA | B14-P004 | 119 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B14-R2 | Closed | 0 | 14¦70
14 | 71 | B14_Assessment | 78 | 10. PHOTO LOG | DATA | B14-P005 | 119 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B14-R6 | Closed | 0 | 14¦71
14 | 72 | B14_Assessment | 79 | 10. PHOTO LOG | DATA | B14-P006 | 119 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B14-R4 | Closed | 0 | 14¦72
14 | 73 | B14_Assessment | 80 | 10. PHOTO LOG | DATA | B14-P007 | 119 | Electrical | B14-TR119A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B14-R5 | Closed | 0 | 14¦73
14 | 74 | B14_Assessment | 81 | 10. PHOTO LOG | DATA | B14-P008 | 119/B.01 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 119-CAM-01 and existing B.01/B2 transfer work | 0 | Paul | 0 | B14-R7/B14-R8 | Closed | 0 | 14¦74
14 | 75 | B14_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14¦75
15 | 1 | B15_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦1
15 | 2 | B15_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 15¦2
15 | 3 | B15_Assessment | 10 | 1. ROOM INVENTORY | DATA | 15 | 124A | First | Office/room converted to Telecom Room | Telecom Room | 1 | 1 | Verify | 15A-401 / 15E-401 / 15T-100 / 15T-604 / 15T-701 | Primary Building 15 TR. Plans identify Telecom Room 124A at 121 SF, served by Rack ID TR15-109A-01, panels B15-TR124AA/AB, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, and a future rack allowance. | 15¦3
15 | 4 | B15_Assessment | 11 | 1. ROOM INVENTORY | DATA | 15 | 222 | Second | Existing Tel Room / wall-mounted rack and support equipment | Existing telecom transition point | 1 | 0 | Verify | 15T-100 / 15T-604 / 15R-900 | Existing second-level Tel Room 222 shown at 65 SF with existing/remain indoor AC unit, security cabinet, ground bar, plywood backboard, wall-mounted rack, existing Cisco switches, legacy patch panels, and floor UPS; protect active services and verify transfer to Room 124A. | 15¦4
15 | 5 | B15_Assessment | 12 | 1. ROOM INVENTORY | DATA | 15 | B01 | Basement | Existing telecom/crossover area | Existing telecom transition point | 1 | 0 | Verify | 15T-604 / 15R-900 | Rack elevations identify existing B-01 crossover wall/wall-mount TE with legacy 24-port patch panel. Photo reference identifies basement existing telecom room B01. | 15¦5
15 | 6 | B15_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦6
15 | 7 | B15_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦7
15 | 8 | B15_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 15¦8
15 | 9 | B15_Assessment | 16 | 2. ROOM READINESS | DATA | 124A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack/future rack clearances, wall backing, and pathway entry points. | 15¦9
15 | 10 | B15_Assessment | 17 | 2. ROOM READINESS | DATA | 222 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing second-level tel room; verify active equipment status, pathway, indoor AC unit, ground bar, backboard, wall rack, UPS, and transition/abandonment scope. | 15¦10
15 | 11 | B15_Assessment | 18 | 2. ROOM READINESS | DATA | B01 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom/crossover room; verify active equipment status, pathway, legacy 24-port patch panel, power, and relationship to Room 222/124A transfer. | 15¦11
15 | 12 | B15_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦12
15 | 13 | B15_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦13
15 | 14 | B15_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 15¦14
15 | 15 | B15_Assessment | 22 | 3. FIRE PROTECTION | DATA | 124A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. | 15¦15
15 | 16 | B15_Assessment | 23 | 3. FIRE PROTECTION | DATA | 222 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | 15¦16
15 | 17 | B15_Assessment | 24 | 3. FIRE PROTECTION | DATA | B01 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom/crossover room; verify no unsealed penetrations remain after cable transfer or reuse. | 15¦17
15 | 18 | B15_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦18
15 | 19 | B15_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦19
15 | 20 | B15_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 15¦20
15 | 21 | B15_Assessment | 28 | 4. HVAC / COOLING | DATA | 124A | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 124A and CU-1-01 outdoor heat-pump/A/C unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | 15¦21
15 | 22 | B15_Assessment | 29 | 4. HVAC / COOLING | DATA | 222 | Existing/remain indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Tel Room 222 is shown with existing/remain indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | 15¦22
15 | 23 | B15_Assessment | 30 | 4. HVAC / COOLING | DATA | B01 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom/crossover space; verify environmental conditions and whether active equipment remains during cutover. | 15¦23
15 | 24 | B15_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦24
15 | 25 | B15_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦25
15 | 26 | B15_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 15¦26
15 | 27 | B15_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | 124A | Verify | 5 kW / 240V rack UPS | Verify | Verify | B15-TR124AA / B15-TR124AB | Verify | Verify | Verify | Electrical enlarged plans and schedules identify B15-TR124AA/AB, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and 30-day load measurement requirements. | 15¦27
15 | 28 | B15_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | 222 | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify power source, active equipment, APC floor UPS status, and transition requirements before disconnect or removal. | 15¦28
15 | 29 | B15_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | B01 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Existing / Verify | Verify | Verify | Verify | Existing B-01 crossover; verify power sources and cutover needs for legacy patch panel/crossover. | 15¦29
15 | 30 | B15_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦30
15 | 31 | B15_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦31
15 | 32 | B15_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 15¦32
15 | 33 | B15_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | 124A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 15T-701 identifies Room 109A schedule but field plan/electrical room callouts identify Telecom Room 124A; schedule has 62 WAO total, 76 active ports per survey, 101 total ports per schedule, and 111 total ports with 10% allowance. New Rack ID TR15-109A-01 serves basement, first and second level outlets. | 15¦33
15 | 34 | B15_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | 222 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 222 equipment includes wall/wall-mounted TE, Cisco switches, legacy 48-port patch panels, ground bar, plywood backboard, security cabinet, and floor UPS; verify active services and transfer plan to Room 124A. | 15¦34
15 | 35 | B15_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | B01 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B-01 crossover includes legacy 24-port patch panel; verify active devices, routing, and relation to Room 222 and Room 124A. | 15¦35
15 | 36 | B15_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦36
15 | 37 | B15_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦37
15 | 38 | B15_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 15¦38
15 | 39 | B15_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | 124A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 124A-CAM-1 and security/access-control scope for Room 124A; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | 15¦39
15 | 40 | B15_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | 222 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | 15¦40
15 | 41 | B15_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | B01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify security/access conditions and whether any legacy security equipment is present. | 15¦41
15 | 42 | B15_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦42
15 | 43 | B15_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦43
15 | 44 | B15_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 15¦44
15 | 45 | B15_Assessment | 52 | 8. OWNER RISKS | DATA | B15-R1 | All | Existing conditions for Room 124A and existing telecom rooms 222/B01 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B15 includes new TR plus existing second-level and basement telecom transition points. | 15¦45
15 | 46 | B15_Assessment | 53 | 8. OWNER RISKS | DATA | B15-R2 | 124A | First-level hazardous material abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | Drawing index includes 15H-101 hazardous material abatement plan - first level; page 6 notes lead-based paint abatement through entire room/door frames. | 15¦46
15 | 47 | B15_Assessment | 54 | 8. OWNER RISKS | DATA | B15-R3 | 222/B01 | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing wall-mounted rack, Cisco switches, patch panels, security cabinet, ground bar and UPS shown. | 15¦47
15 | 48 | B15_Assessment | 55 | 8. OWNER RISKS | DATA | B15-R4 | 124A | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 15¦48
15 | 49 | B15_Assessment | 56 | 8. OWNER RISKS | DATA | B15-R5 | 124A | 240V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B15-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs | Electrical / GCC | Closed | Panel and circuit references are concentrated at Room 124A. | 15¦49
15 | 50 | B15_Assessment | 57 | 8. OWNER RISKS | DATA | B15-R6 | 124A | Rated wall/door/firestop scope may affect life-safety acceptance | High | Medium | 6 | Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | GC / FP / FA | Closed | New TRs must be 1-hour fire/smoke rated. | 15¦50
15 | 51 | B15_Assessment | 58 | 8. OWNER RISKS | DATA | B15-R7 | All | Telecom/fiber cutover could affect active hospital communications across basement, first and second levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | 15T-701 shows Room 124A/109A serving 111 total ports including allowance. | 15¦51
15 | 52 | B15_Assessment | 59 | 8. OWNER RISKS | DATA | B15-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 15¦52
15 | 53 | B15_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦53
15 | 54 | B15_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦54
15 | 55 | B15_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 15¦55
15 | 56 | B15_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B15-Q1 | Confirm final telecom scope: new Room 124A and existing Rooms 222/B01 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 15¦56
15 | 57 | B15_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B15-Q2 | Why does 15T-701 reference RM 109A while plans and electrical schedules identify Telecom Room 124A? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0 | 15¦57
15 | 58 | B15_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B15-Q3 | What active services are currently fed from existing Room 222 and B01 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 15¦58
15 | 59 | B15_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B15-Q4 | What hazardous/abatement steps apply to first-level Room 124A work? | GC / IH / COR | Closed | 0 | 0 | Work delay or exposure risk | 0 | 0 | 0 | 15¦59
15 | 60 | B15_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B15-Q5 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124A? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 15¦60
15 | 61 | B15_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B15-Q6 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124A? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 15¦61
15 | 62 | B15_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B15-Q7 | Are B15-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 15¦62
15 | 63 | B15_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B15-Q8 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 15¦63
15 | 64 | B15_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦64
15 | 65 | B15_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦65
15 | 66 | B15_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 15¦66
15 | 67 | B15_Assessment | 74 | 10. PHOTO LOG | DATA | B15-P001 | 124A | Existing Condition | Room 124A walls, ceiling/deck, floor, door, adjacent Office 124/Office 109/HAC 123, rack location, pathways and penetrations | 0 | Paul | 0 | B15-R1/B15-R6 | Closed | 0 | 15¦67
15 | 68 | B15_Assessment | 75 | 10. PHOTO LOG | DATA | B15-P002 | 222 | Existing Condition | Existing Tel Room 222 wall rack, Cisco switches, legacy patch panels, indoor AC unit, security cabinet, ground bar, plywood backboard and floor UPS | 0 | Paul | 0 | B15-R1/B15-R3 | Closed | 0 | 15¦68
15 | 69 | B15_Assessment | 76 | 10. PHOTO LOG | DATA | B15-P003 | B01 | Existing Condition | Existing basement telecom/crossover B01, legacy 24-port patch panel, pathway, power and protection-in-place needs | 0 | Paul | 0 | B15-R1/B15-R3 | Closed | 0 | 15¦69
15 | 70 | B15_Assessment | 77 | 10. PHOTO LOG | DATA | B15-P004 | 124A | Hazardous Materials | First-level abatement-related materials, lead-based paint/door frames, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B15-R2 | Closed | 0 | 15¦70
15 | 71 | B15_Assessment | 78 | 10. PHOTO LOG | DATA | B15-P005 | 124A | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B15-R6 | Closed | 0 | 15¦71
15 | 72 | B15_Assessment | 79 | 10. PHOTO LOG | DATA | B15-P006 | 124A | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B15-R4 | Closed | 0 | 15¦72
15 | 73 | B15_Assessment | 80 | 10. PHOTO LOG | DATA | B15-P007 | 124A | Electrical | B15-TR124AA/AB panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B15-R5 | Closed | 0 | 15¦73
15 | 74 | B15_Assessment | 81 | 10. PHOTO LOG | DATA | B15-P008 | 124A/222/B01 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 124A-CAM-1 and existing 222/B01 transfer work | 0 | Paul | 0 | B15-R7/B15-R8 | Closed | 0 | 15¦74
15 | 75 | B15_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15¦75
16 | 1 | B16_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦1
16 | 2 | B16_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 16¦2
16 | 3 | B16_Assessment | 10 | 1. ROOM INVENTORY | DATA | 16 | 015 | Basement | Vacant / new telecom room build area | Telecom Room | 1 | 1 | Verify | 16A-400 / 16E-100 / 16T-100 / 16T-604 / 16T-701 | Primary Building 16 TR. Plans identify Telecom Room 015 at 79 SF, served by Rack ID TR01-015-A-1, panels B16-TR015A/B, 240V UPS/PDU rack power, IU-1-01/CU-1-01 cooling, 96 feet total cable tray, and future rack allowance. | 16¦3
16 | 4 | B16_Assessment | 11 | 1. ROOM INVENTORY | DATA | 16 | 014 | Basement | Existing telecom room / stair-adjacent legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 16T-100 / 16T-604 / 16R-900 | Existing basement Telecom Room 014 shown with wall-mounted rack, plywood backboard, patch panel, security cabinet, telco patch, existing floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU/wall; protect active services and verify transfer to Room 015. | 16¦4
16 | 5 | B16_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦5
16 | 6 | B16_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦6
16 | 7 | B16_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 16¦7
16 | 8 | B16_Assessment | 15 | 2. ROOM READINESS | DATA | 015 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack/future rack clearances, wall backing, and pathway entry points. | 16¦8
16 | 9 | B16_Assessment | 16 | 2. ROOM READINESS | DATA | 014 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom room; verify active equipment status, pathway, rack/UPS/backboard, security cabinet, and transition/abandonment scope. | 16¦9
16 | 10 | B16_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦10
16 | 11 | B16_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦11
16 | 12 | B16_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 16¦12
16 | 13 | B16_Assessment | 20 | 3. FIRE PROTECTION | DATA | 015 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | 16¦13
16 | 14 | B16_Assessment | 21 | 3. FIRE PROTECTION | DATA | 014 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | 16¦14
16 | 15 | B16_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦15
16 | 16 | B16_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦16
16 | 17 | B16_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 16¦17
16 | 18 | B16_Assessment | 25 | 4. HVAC / COOLING | DATA | 015 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 015 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | 16¦18
16 | 19 | B16_Assessment | 26 | 4. HVAC / COOLING | DATA | 014 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Telecom Room 014; verify existing environmental conditions during cutover and whether legacy equipment remains active. | 16¦19
16 | 20 | B16_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦20
16 | 21 | B16_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦21
16 | 22 | B16_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 16¦22
16 | 23 | B16_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | 015 | Verify | 5 kW / 240V rack UPS | Verify | Verify | B16-TR015A / B16-TR015B | Verify | Verify | Verify | Electrical plans/schedules identify B16-TR015A/B, 240V rack UPS requirements, rack receptacles, TR receptacles, lighting, access controller, CU-1-01, SPD requirements, existing panel demolition/replacement, and 30-day load measurement requirements. | 16¦23
16 | 24 | B16_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | 014 | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | 16¦24
16 | 25 | B16_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦25
16 | 26 | B16_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦26
16 | 27 | B16_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 16¦27
16 | 28 | B16_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | 015 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 16T-701 identifies Room 015-A schedule: 25 WAO total, 25 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. New Rack ID TR01-015-A-1 serves basement, first, second and attic level outlets. | 16¦28
16 | 29 | B16_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | 014 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 014 equipment includes wall/TE rack, floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU; verify active services and transfer plan to Room 015. | 16¦29
16 | 30 | B16_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦30
16 | 31 | B16_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦31
16 | 32 | B16_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 16¦32
16 | 33 | B16_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | 015 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 015-CAM-1 and security/access-control scope for Room 015; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | 16¦33
16 | 34 | B16_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | 014 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in Room 014; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | 16¦34
16 | 35 | B16_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦35
16 | 36 | B16_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦36
16 | 37 | B16_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 16¦37
16 | 38 | B16_Assessment | 45 | 8. OWNER RISKS | DATA | B16-R1 | All | Existing conditions for Room 015 and existing Telecom Room 014 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B16 includes new basement TR plus existing basement telecom transition point. | 16¦38
16 | 39 | B16_Assessment | 46 | 8. OWNER RISKS | DATA | B16-R2 | 014 | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing wall-mounted rack, Cisco switch, legacy patch panel, security cabinet and UPS shown. | 16¦39
16 | 40 | B16_Assessment | 47 | 8. OWNER RISKS | DATA | B16-R3 | 015 | Basement TR buildout may conflict with existing utilities, water heater/stair/storage conditions and pathway routing | High | Medium | 6 | Survey adjacent Water Heater 010, Vacant 011/012/013, Stair 014, pathway/ductbank routing, and constructability constraints | GC / GCC | Closed | Room 015 is basement level and adjacent to existing utilities/rooms. | 16¦40
16 | 41 | B16_Assessment | 48 | 8. OWNER RISKS | DATA | B16-R4 | 015 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 16¦41
16 | 42 | B16_Assessment | 49 | 8. OWNER RISKS | DATA | B16-R5 | 015 | 240V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B16-TR015A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs | Electrical / GCC | Closed | Panel schedule includes existing panel replacement/demolition and 30-day load measurement requirements. | 16¦42
16 | 43 | B16_Assessment | 50 | 8. OWNER RISKS | DATA | B16-R6 | 015 | Rated wall/door/firestop scope may affect life-safety acceptance | High | Medium | 6 | Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | GC / FP / FA | Closed | New TRs must be 1-hour fire/smoke rated. | 16¦43
16 | 44 | B16_Assessment | 51 | 8. OWNER RISKS | DATA | B16-R7 | All | Telecom/fiber cutover could affect active hospital communications across basement, first, second and attic levels | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | 16T-701 shows Room 015 serving 40 total ports including allowance. | 16¦44
16 | 45 | B16_Assessment | 52 | 8. OWNER RISKS | DATA | B16-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 16¦45
16 | 46 | B16_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦46
16 | 47 | B16_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦47
16 | 48 | B16_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 16¦48
16 | 49 | B16_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B16-Q1 | Confirm final telecom scope: new Room 015 and existing Room 014 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 16¦49
16 | 50 | B16_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B16-Q2 | What active services are currently fed from existing Room 014 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 16¦50
16 | 51 | B16_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B16-Q3 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 015? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 16¦51
16 | 52 | B16_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B16-Q4 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 015? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 16¦52
16 | 53 | B16_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B16-Q5 | Are B16-TR015A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 16¦53
16 | 54 | B16_Assessment | 61 | 9. OPEN QUESTIONS | DATA | B16-Q6 | Which existing panel/circuit breaker/feeder demolition and replacement affects Room 015 telecom power? | Electrical / GCC | Closed | 0 | 0 | Panel outage/cutover risk | 0 | 0 | 0 | 16¦54
16 | 55 | B16_Assessment | 62 | 9. OPEN QUESTIONS | DATA | B16-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 16¦55
16 | 56 | B16_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B16-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 16¦56
16 | 57 | B16_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦57
16 | 58 | B16_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦58
16 | 59 | B16_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 16¦59
16 | 60 | B16_Assessment | 67 | 10. PHOTO LOG | DATA | B16-P001 | 015 | Existing Condition | Room 015 walls, ceiling/deck, floor, door, adjacent Vacant 011/012/013, Stair 014, Water Heater 010, rack location, pathways and penetrations | 0 | Paul | 0 | B16-R1/B16-R3 | Closed | 0 | 16¦60
16 | 61 | B16_Assessment | 68 | 10. PHOTO LOG | DATA | B16-P002 | 014 | Existing Condition | Existing Telecom Room 014 wall rack/TE, Cisco switch, legacy 12-port patch panel, Fiber LIU, floor UPS, plywood backboard and security cabinet | 0 | Paul | 0 | B16-R1/B16-R2 | Closed | 0 | 16¦61
16 | 62 | B16_Assessment | 69 | 10. PHOTO LOG | DATA | B16-P003 | 015 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B16-R6 | Closed | 0 | 16¦62
16 | 63 | B16_Assessment | 70 | 10. PHOTO LOG | DATA | B16-P004 | 015 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B16-R4 | Closed | 0 | 16¦63
16 | 64 | B16_Assessment | 71 | 10. PHOTO LOG | DATA | B16-P005 | 015 | Electrical | B16-TR015A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B16-R5 | Closed | 0 | 16¦64
16 | 65 | B16_Assessment | 72 | 10. PHOTO LOG | DATA | B16-P006 | 015/014 | Telecom | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records and existing Room 014 transfer work | 0 | Paul | 0 | B16-R7 | Closed | 0 | 16¦65
16 | 66 | B16_Assessment | 73 | 10. PHOTO LOG | DATA | B16-P007 | 015/014 | Security | 015-CAM-1, card reader, electric strike, door position, motion sensor, existing security cabinet and VMS/PACS integration | 0 | Paul | 0 | B16-R8 | Closed | 0 | 16¦66
16 | 67 | B16_Assessment | 74 | 10. PHOTO LOG | DATA | B16-P008 | All | Cable Tray / Pathway | Basement and first-level cable tray/pathway route, supports, fill, firestopping and seismic bracing | 0 | Paul | 0 | B16-R3/B16-R7 | Closed | 0 | 16¦67
16 | 68 | B16_Assessment | 75 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16¦68
17 | 1 | B17_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦1
17 | 2 | B17_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 17¦2
17 | 3 | B17_Assessment | 10 | 1. ROOM INVENTORY | DATA | 17 | 118 | First | New telecom room build area | Telecom Room | 1 | 1 | Verify | 17_29A-401 / 17_29E-401 / 17_29T-100 / 17_29T-604 / 17_29T-701 | Primary Building 17 TR. Plans identify Telecom Room 118 at 157 SF, Rack ID TR17-118-1, panels B17-TR118A/B, 208V rack UPS/PDU equipment, IU-1-01/CU-1-01 cooling, 517 feet total cable tray, and future rack allowance. Rack elevation notes Room 118 serves Building 29. | 17¦3
17 | 4 | B17_Assessment | 11 | 1. ROOM INVENTORY | DATA | 17 | B35A | Basement | Existing telecom closet / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 17_29T-100 / 17_29T-604 / 17_29R-900 | Existing basement Telecom Closet B35A shown at 12 SF with wall-mounted TE, patch panel, security cabinet, plywood backboard, indoor AC unit, floor UPS, Cisco switches, legacy Ortronics 24/48-port patch panels and SERTEX utility service ports. Protect active services and verify transfer to Room 118. | 17¦4
17 | 5 | B17_Assessment | 12 | 1. ROOM INVENTORY | DATA | 29 | Building 29 path | First / served from B17 | Building 29 service extension | Served from B17 TR 118 | 0 | 0 | Verify | 17_29T-100 / 17_29T-604 / 17_29T-701 | Building 29 is shown served from B17, with path to B29 via 4-inch PVC and fiber extending from Building 17 to Building 29. Field verify pathway, service boundary, and active outlets included in TR17-118-1 schedule. | 17¦5
17 | 6 | B17_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦6
17 | 7 | B17_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦7
17 | 8 | B17_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 17¦8
17 | 9 | B17_Assessment | 16 | 2. ROOM READINESS | DATA | 118 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, static-control floor sealer, rack/future rack clearances, wall backing, and cable tray/pathway entry points. | 17¦9
17 | 10 | B17_Assessment | 17 | 2. ROOM READINESS | DATA | B35A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing basement telecom closet; verify active equipment status, pathway, rack/UPS/backboard, indoor AC, security cabinet, and transition/abandonment scope. | 17¦10
17 | 11 | B17_Assessment | 18 | 2. ROOM READINESS | DATA | B29 Path | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify route from Building 17 to Building 29, 4-inch PVC path, fiber handoff, ownership limits, labeling and final test documentation. | 17¦11
17 | 12 | B17_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦12
17 | 13 | B17_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦13
17 | 14 | B17_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 17¦14
17 | 15 | B17_Assessment | 22 | 3. FIRE PROTECTION | DATA | 118 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | 17¦15
17 | 16 | B17_Assessment | 23 | 3. FIRE PROTECTION | DATA | B35A | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom closet; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | 17¦16
17 | 17 | B17_Assessment | 24 | 3. FIRE PROTECTION | DATA | B29 Path | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Verify firestopping at pathway penetrations between Building 17 and Building 29 and any rated floor/wall assemblies. | 17¦17
17 | 18 | B17_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦18
17 | 19 | B17_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦19
17 | 20 | B17_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 17¦20
17 | 21 | B17_Assessment | 28 | 4. HVAC / COOLING | DATA | 118 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 118 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | 17¦21
17 | 22 | B17_Assessment | 29 | 4. HVAC / COOLING | DATA | B35A | Existing indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing B35A is shown with existing indoor AC unit; verify whether it remains active, is abandoned, or needs temporary protection during cutover. | 17¦22
17 | 23 | B17_Assessment | 30 | 4. HVAC / COOLING | DATA | B29 Path | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No dedicated cooling expected for pathway; verify any equipment cabinets or active service locations in Building 29 if applicable. | 17¦23
17 | 24 | B17_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦24
17 | 25 | B17_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦25
17 | 26 | B17_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 17¦26
17 | 27 | B17_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | 118 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B17-TR118A / B17-TR118B | Verify | Verify | Verify | Electrical plans/schedules identify B17-TR118A fed from BUS-B17-NPB1-R and B17-TR118B fed from BUS-B17-EQDP, with TR RM118 rack receptacles, 208V UPS/PDU equipment, CU-1-01, SPD requirements, and 30-day load measurement requirements. | 17¦27
17 | 28 | B17_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | B35A | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. | 17¦28
17 | 29 | B17_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | B29 Path | N/A | N/A | N/A | N/A | B17 source / verify | Verify | Verify | Verify | Verify whether any Building 29 equipment or extension path requires power, grounding, bonding, or labeling tied back to B17 TR 118. | 17¦29
17 | 30 | B17_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦30
17 | 31 | B17_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦31
17 | 32 | B17_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 17¦32
17 | 33 | B17_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | 118 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 17_29T-701 identifies Room 118 schedule: 113 WAO total, 67 active ports per survey, 154 total ports per schedule, and 169 total ports with 10% allowance. Rack ID TR17-118-1 serves basement, first, second-level outlets and Building 29 path. | 17¦33
17 | 34 | B17_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | B35A | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room B35A equipment includes SERTEX utility service ports, legacy Ortronics patch panels, Cisco switches, wall-mounted TE, Fiber/legacy equipment, security cabinet, and floor UPS; verify active services and transfer plan to Room 118. | 17¦34
17 | 35 | B17_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | B29 Path | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Building 29 is shown served from B17; verify fiber from Building 17 to Building 29, path to B29 4-inch PVC, outlet labels, test records and as-builts. | 17¦35
17 | 36 | B17_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦36
17 | 37 | B17_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦37
17 | 38 | B17_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 17¦38
17 | 39 | B17_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | 118 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 118-CAM-01 and security/access-control scope for Room 118; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | 17¦39
17 | 40 | B17_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | B35A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in B35A; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | 17¦40
17 | 41 | B17_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | B29 Path | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify Building 29 pathway and any security scope tied into B17 TR 118/VMS/PACS. | 17¦41
17 | 42 | B17_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦42
17 | 43 | B17_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦43
17 | 44 | B17_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 17¦44
17 | 45 | B17_Assessment | 52 | 8. OWNER RISKS | DATA | B17-R1 | All | Existing conditions for Room 118, B35A and Building 29 service path not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B17_29 includes new TR plus existing basement telecom transition point and B29 service path. | 17¦45
17 | 46 | B17_Assessment | 53 | 8. OWNER RISKS | DATA | B17-R2 | 118 | First-level hazardous material abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | Drawing index includes 17_29H-101 hazardous material abatement plan - first level. | 17¦46
17 | 47 | B17_Assessment | 54 | 8. OWNER RISKS | DATA | B17-R3 | B35A | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing SERTEX utility service, Cisco switches, legacy patch panels, security cabinet and UPS shown. | 17¦47
17 | 48 | B17_Assessment | 55 | 8. OWNER RISKS | DATA | B17-R4 | 118 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 17¦48
17 | 49 | B17_Assessment | 56 | 8. OWNER RISKS | DATA | B17-R5 | 118 | 208V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B17-TR118A/B schedules, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, SPD, labels, load measurement and LOTO needs | Electrical / GCC | Closed | Panel sources include normal and equipment/emergency-side distribution references. | 17¦49
17 | 50 | B17_Assessment | 57 | 8. OWNER RISKS | DATA | B17-R6 | 118/B29 Path | Cable tray and pathway scope is large and crosses multiple levels/building service boundary | High | Medium | 6 | Verify 517 ft cable tray, supports, seismic bracing, 40% fill, path to B29 4-inch PVC, penetrations and labeling before install | Telecom / GC | Closed | Cable tray schedule: basement 200 ft, first level 202 ft, second level 115 ft. | 17¦50
17 | 51 | B17_Assessment | 58 | 8. OWNER RISKS | DATA | B17-R7 | All | Telecom/fiber cutover could affect active hospital communications across B17 and B29 | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | Room 118 serves 169 total ports including allowance and B29 path. | 17¦51
17 | 52 | B17_Assessment | 59 | 8. OWNER RISKS | DATA | B17-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 17¦52
17 | 53 | B17_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦53
17 | 54 | B17_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦54
17 | 55 | B17_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 17¦55
17 | 56 | B17_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B17-Q1 | Confirm final telecom scope: new Room 118, existing B35A, and Building 29 served from B17? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0 | 17¦56
17 | 57 | B17_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B17-Q2 | What active services are currently fed from existing B35A equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 17¦57
17 | 58 | B17_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B17-Q3 | What exact Building 29 outlets/devices are served through TR17-118-1? | VA / OIT / Designer | Closed | 0 | 0 | Building 29 scope boundary unclear | 0 | 0 | 0 | 17¦58
17 | 59 | B17_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B17-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 118? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 17¦59
17 | 60 | B17_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B17-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 118? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 17¦60
17 | 61 | B17_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B17-Q6 | Are B17-TR118A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 17¦61
17 | 62 | B17_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B17-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 17¦62
17 | 63 | B17_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B17-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 17¦63
17 | 64 | B17_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦64
17 | 65 | B17_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦65
17 | 66 | B17_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 17¦66
17 | 67 | B17_Assessment | 74 | 10. PHOTO LOG | DATA | B17-P001 | 118 | Existing Condition | Room 118 walls, ceiling/deck, floor, door, adjacent Lab/Freezer/Research/Corridor areas, rack location, pathways and penetrations | 0 | Paul | 0 | B17-R1/B17-R2 | Closed | 0 | 17¦67
17 | 68 | B17_Assessment | 75 | 10. PHOTO LOG | DATA | B17-P002 | B35A | Existing Condition | Existing Telecom Closet B35A wall TE, SERTEX service ports, legacy patch panels, Cisco switches, security cabinet, plywood backboard, indoor AC and floor UPS | 0 | Paul | 0 | B17-R1/B17-R3 | Closed | 0 | 17¦68
17 | 69 | B17_Assessment | 76 | 10. PHOTO LOG | DATA | B17-P003 | B29 Path | Pathway | Path to B29 4-inch PVC, fiber route, penetrations, handoff points and labeling | 0 | Paul | 0 | B17-R6/B17-R7 | Closed | 0 | 17¦69
17 | 70 | B17_Assessment | 77 | 10. PHOTO LOG | DATA | B17-P004 | 118 | Hazardous Materials | First-level abatement-related materials, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B17-R2 | Closed | 0 | 17¦70
17 | 71 | B17_Assessment | 78 | 10. PHOTO LOG | DATA | B17-P005 | 118/B29 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop, including B29 pathway | 0 | Paul | 0 | B17-R6 | Closed | 0 | 17¦71
17 | 72 | B17_Assessment | 79 | 10. PHOTO LOG | DATA | B17-P006 | 118 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B17-R4 | Closed | 0 | 17¦72
17 | 73 | B17_Assessment | 80 | 10. PHOTO LOG | DATA | B17-P007 | 118 | Electrical | B17-TR118A/B panels, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B17-R5 | Closed | 0 | 17¦73
17 | 74 | B17_Assessment | 81 | 10. PHOTO LOG | DATA | B17-P008 | 118/B35A/B29 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 118-CAM-01 and existing B35A transfer work | 0 | Paul | 0 | B17-R7/B17-R8 | Closed | 0 | 17¦74
17 | 75 | B17_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17¦75
18 | 1 | B18_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦1
18 | 2 | B18_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 18¦2
18 | 3 | B18_Assessment | 10 | 1. ROOM INVENTORY | DATA | 18 | 110 | First | New telecom room build area | Telecom Room | 1 | 1 | Verify | 18A-401 / 18E-101 / 18T-100 / 18T-401 / 18T-604 / 18T-701 | Primary Building 18 TR. Plans identify Telecom Room 110 at 168 SF, Rack ID TR01-111A-1, panels B18-TR110A/B, 208V rack UPS/PDU equipment, IU-1-01/CU-1-01 cooling, 315 feet total cable tray, and future rack allowance. Room 110 is the new rack room even though the schedule labels RM 111A. | 18¦3
18 | 4 | B18_Assessment | 11 | 1. ROOM INVENTORY | DATA | 18 | 111B | First | Existing TE / stair-adjacent legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 18T-401 / 18T-604 / 18R-900 | Existing first-level TE 111B shown at 13 SF with wall-mounted rack, plywood backboard, patch panel, security cabinet, existing floor UPS, and 5RU fiber optic housing. Protect active services and verify transfer to Room 110. | 18¦4
18 | 5 | B18_Assessment | 12 | 1. ROOM INVENTORY | DATA | 18 | 213 | Second | Existing telecom closet / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 18T-401 / 18T-604 / 18R-900 | Existing second-level Closet 213 shown at 8 SF with wall-mounted rack, plywood backboard, patch panel, security cabinet, APC floor UPS, SERTEX utility service ports, Cisco switch and legacy Ortronics patch panels. Protect active services and verify transfer to Room 110. | 18¦5
18 | 6 | B18_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦6
18 | 7 | B18_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦7
18 | 8 | B18_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 18¦8
18 | 9 | B18_Assessment | 16 | 2. ROOM READINESS | DATA | 110 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour fire/smoke-rated enclosure, open-to-deck conditions, 45-minute door/frame, access control, static-control floor sealer, rack/future rack clearances, wall backing, and cable tray/pathway entry points. | 18¦9
18 | 10 | B18_Assessment | 17 | 2. ROOM READINESS | DATA | 111B | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing first-level TE; verify active equipment status, pathway, rack/UPS/backboard, security cabinet, fiber housing and transition/abandonment scope. | 18¦10
18 | 11 | B18_Assessment | 18 | 2. ROOM READINESS | DATA | 213 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing second-level closet; verify active equipment status, pathway, rack/UPS/backboard, security cabinet and transition/abandonment scope. | 18¦11
18 | 12 | B18_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦12
18 | 13 | B18_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦13
18 | 14 | B18_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 18¦14
18 | 15 | B18_Assessment | 22 | 3. FIRE PROTECTION | DATA | 110 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. | 18¦15
18 | 16 | B18_Assessment | 23 | 3. FIRE PROTECTION | DATA | 111B | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing TE room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | 18¦16
18 | 17 | B18_Assessment | 24 | 3. FIRE PROTECTION | DATA | 213 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing second-level closet; verify protection-in-place and firestopping after transfer or abandonment. | 18¦17
18 | 18 | B18_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦18
18 | 19 | B18_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦19
18 | 20 | B18_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 18¦20
18 | 21 | B18_Assessment | 28 | 4. HVAC / COOLING | DATA | 110 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 110 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. | 18¦21
18 | 22 | B18_Assessment | 29 | 4. HVAC / COOLING | DATA | 111B | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing TE 111B; verify existing environmental conditions during cutover and whether legacy equipment remains active. | 18¦22
18 | 23 | B18_Assessment | 30 | 4. HVAC / COOLING | DATA | 213 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Closet 213; verify existing environmental conditions during cutover and whether legacy equipment remains active. | 18¦23
18 | 24 | B18_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦24
18 | 25 | B18_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦25
18 | 26 | B18_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 18¦26
18 | 27 | B18_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | 110 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B18-TR110A / B18-TR110B | Verify | Verify | Verify | Electrical plans/schedules identify B18-TR110A/B, 208V rack UPS requirements, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and telecom panelboard schedule requirements. | 18¦27
18 | 28 | B18_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | 111B | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. | 18¦28
18 | 29 | B18_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | 213 | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area; verify active equipment, APC UPS status, source circuits, SERTEX utility service and transfer requirements before disconnect/removal. | 18¦29
18 | 30 | B18_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦30
18 | 31 | B18_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦31
18 | 32 | B18_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 18¦32
18 | 33 | B18_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | 110 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 18T-701 identifies RM 111A schedule: 86 WAO total, 61 active ports per survey, 122 ports per schedule, and 134 total ports with 10% allowance. New rack elevation is Room 110, 1 rack plus future, with UPS, Future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | 18¦33
18 | 34 | B18_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | 111B | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 111B equipment includes wall-mounted rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber optic housing; verify active services and transfer plan to Room 110. | 18¦34
18 | 35 | B18_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | 213 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 213 equipment includes SERTEX utility service ports, Cisco switch, multiple legacy Ortronics patch panels, wall/wall-mount TE and APC floor UPS; verify active services and transfer plan to Room 110. | 18¦35
18 | 36 | B18_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦36
18 | 37 | B18_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦37
18 | 38 | B18_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 18¦38
18 | 39 | B18_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | 110 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom/electrical plans show 111A-CAM-01 and security/access-control scope for the new TR area; verify room naming, CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. | 18¦39
18 | 40 | B18_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | 111B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in 111B; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | 18¦40
18 | 41 | B18_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | 213 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing security cabinet shown in 213; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | 18¦41
18 | 42 | B18_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦42
18 | 43 | B18_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦43
18 | 44 | B18_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 18¦44
18 | 45 | B18_Assessment | 52 | 8. OWNER RISKS | DATA | B18-R1 | All | Existing conditions for Room 110, Room 111B and Room 213 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B18 includes new first-level TR plus existing first and second-level telecom transition points. | 18¦45
18 | 46 | B18_Assessment | 53 | 8. OWNER RISKS | DATA | B18-R2 | 110 | First-level hazardous material / lead-based paint abatement plan exists | High | Medium | 6 | Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work | GC / IH / COR | Closed | 18H-101 notes lead-based paint abatement through entire telecom room/door frames. | 18¦46
18 | 47 | B18_Assessment | 54 | 8. OWNER RISKS | DATA | B18-R3 | 111B/213 | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path | Telecom / OIT | Closed | Existing racks, SERTEX ports, Cisco switch, patch panels, security cabinets and UPS units shown. | 18¦47
18 | 48 | B18_Assessment | 55 | 8. OWNER RISKS | DATA | B18-R4 | 110 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 18¦48
18 | 49 | B18_Assessment | 56 | 8. OWNER RISKS | DATA | B18-R5 | 110 | 208V UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify B18-TR110A/B schedules, rack receptacles, SPD, labels, source circuits and LOTO needs | Electrical / GCC | Closed | Panel references are concentrated at Room 110 with CU-1-01 and rack receptacles. | 18¦49
18 | 50 | B18_Assessment | 57 | 8. OWNER RISKS | DATA | B18-R6 | 110 | Cable tray and pathway scope crosses first and second levels | High | Medium | 6 | Verify 315 ft cable tray, supports, seismic bracing, 40% fill, penetrations, coordination with lighting/HVAC and labeling before install | Telecom / GC | Closed | Cable tray schedule: first level 174 ft, second level 141 ft. | 18¦50
18 | 51 | B18_Assessment | 58 | 8. OWNER RISKS | DATA | B18-R7 | All | Telecom/fiber cutover could affect active hospital communications and legacy cross-building service ports | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | Room 213 existing rack elevation references SERTEX utility service ports to B17, B19 and B3. | 18¦51
18 | 52 | B18_Assessment | 59 | 8. OWNER RISKS | DATA | B18-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, fire alarm/sprinkler acceptance, power verification, cabling test records, labels and as-builts | GC / Cx Manager | Closed | Required by cover/general notes. | 18¦52
18 | 53 | B18_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦53
18 | 54 | B18_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦54
18 | 55 | B18_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 18¦55
18 | 56 | B18_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B18-Q1 | Confirm final telecom scope: new Room 110 with existing 111B and 213 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0 | 18¦56
18 | 57 | B18_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B18-Q2 | Why does 18T-701 reference RM 111A while new rack/electrical plans identify Telecom Room 110? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0 | 18¦57
18 | 58 | B18_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B18-Q3 | What active services are currently fed from existing 111B and 213 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 18¦58
18 | 59 | B18_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B18-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 110? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 18¦59
18 | 60 | B18_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B18-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 110? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 18¦60
18 | 61 | B18_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B18-Q6 | Are B18-TR110A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 18¦61
18 | 62 | B18_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B18-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 18¦62
18 | 63 | B18_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B18-Q8 | Which third-party inspections and commissioning forms are required before VA acceptance? | GC / Cx Manager | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 18¦63
18 | 64 | B18_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦64
18 | 65 | B18_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦65
18 | 66 | B18_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 18¦66
18 | 67 | B18_Assessment | 74 | 10. PHOTO LOG | DATA | B18-P001 | 110 | Existing Condition | Room 110 walls, ceiling/deck, floor, door, adjacent Corridor 121/Stair 122/Office 112, rack location, pathways and penetrations | 0 | Paul | 0 | B18-R1/B18-R2 | Closed | 0 | 18¦67
18 | 68 | B18_Assessment | 75 | 10. PHOTO LOG | DATA | B18-P002 | 111B | Existing Condition | Existing TE 111B wall rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber housing | 0 | Paul | 0 | B18-R1/B18-R3 | Closed | 0 | 18¦68
18 | 69 | B18_Assessment | 76 | 10. PHOTO LOG | DATA | B18-P003 | 213 | Existing Condition | Existing Closet 213 wall rack/TE, SERTEX service ports, Cisco switch, legacy Ortronics patch panels, security cabinet, plywood backboard and APC floor UPS | 0 | Paul | 0 | B18-R1/B18-R3 | Closed | 0 | 18¦69
18 | 70 | B18_Assessment | 77 | 10. PHOTO LOG | DATA | B18-P004 | 110 | Hazardous Materials | First-level abatement/lead-paint areas, flooring, walls, ceiling/penetrations, and disturbance areas | 0 | Paul | 0 | B18-R2 | Closed | 0 | 18¦70
18 | 71 | B18_Assessment | 78 | 10. PHOTO LOG | DATA | B18-P005 | 110 | Firestop | All wall/floor/sleeve/tray penetrations before and after firestop | 0 | Paul | 0 | B18-R6 | Closed | 0 | 18¦71
18 | 72 | B18_Assessment | 79 | 10. PHOTO LOG | DATA | B18-P006 | 110 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B18-R4 | Closed | 0 | 18¦72
18 | 73 | B18_Assessment | 80 | 10. PHOTO LOG | DATA | B18-P007 | 110 | Electrical | B18-TR110A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B18-R5 | Closed | 0 | 18¦73
18 | 74 | B18_Assessment | 81 | 10. PHOTO LOG | DATA | B18-P008 | 110/111B/213 | Telecom/Security | New rack/future rack, fiber path A/B, Cat6A, patch panels, LIU, labels/test records, 111A-CAM-01 and existing 111B/213 transfer work | 0 | Paul | 0 | B18-R7/B18-R8 | Closed | 0 | 18¦74
18 | 75 | B18_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18¦75
20 | 1 | B20_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦1
20 | 2 | B20_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 20¦2
20 | 3 | B20_Assessment | 10 | 1. ROOM INVENTORY | DATA | 20 | 1B | First | Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 20T-101 / 20T-701 / 20E-101 / 20E-601 | Primary Building 20 TE. Plans identify Office 1B at 110 SF with new wall-mount telecom enclosure Rack ID TE01-1B-1, 12RU enclosure, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and 33 total ports with 10% allowance. | 20¦3
20 | 4 | B20_Assessment | 11 | 1. ROOM INVENTORY | DATA | 20 | 8A | First | Existing Tel/Data Closet / open TE cabinet | Existing telecom transition point | 2 | 0 | Verify | 20T-101 / 20T-701 / 20R-900 | Existing Tel/Data Closet 8A at 17 SF with existing open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy Ortronics 48-port patch panel, floor UPS and Fiber LIU. Protect active services and transfer to Office 1B TE. | 20¦4
20 | 5 | B20_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦5
20 | 6 | B20_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦6
20 | 7 | B20_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 20¦7
20 | 8 | B20_Assessment | 15 | 2. ROOM READINESS | DATA | 1B | Verify | Verify | N/A / Office | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in Office 1B; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, and that office use can remain operational. | 20¦8
20 | 9 | B20_Assessment | 16 | 2. ROOM READINESS | DATA | 8A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing Tel/Data Closet; verify active equipment status, existing open cabinet, indoor AC, ground bar/backboard, floor UPS, pathway and transition/abandonment scope. | 20¦9
20 | 10 | B20_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦10
20 | 11 | B20_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦11
20 | 12 | B20_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 20¦12
20 | 13 | B20_Assessment | 20 | 3. FIRE PROTECTION | DATA | 1B | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 20 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. | 20¦13
20 | 14 | B20_Assessment | 21 | 3. FIRE PROTECTION | DATA | 8A | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing closet; verify protection-in-place and firestopping after cable transfer or reuse. | 20¦14
20 | 15 | B20_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦15
20 | 16 | B20_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦16
20 | 17 | B20_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 20¦17
20 | 18 | B20_Assessment | 25 | 4. HVAC / COOLING | DATA | 1B | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Cover sheet states mechanical scope is excluded. Verify whether Office 1B ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | 20¦18
20 | 19 | B20_Assessment | 26 | 4. HVAC / COOLING | DATA | 8A | Existing indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Tel/Data Closet 8A includes indoor AC unit to remain/protect in place; verify operation during cutover and whether equipment remains after transition. | 20¦19
20 | 20 | B20_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦20
20 | 21 | B20_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦21
20 | 22 | B20_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 20¦22
20 | 23 | B20_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | 1B | Verify | APC UPS / TE enclosure | Verify | Verify | 20E-101 / 20E-601 source to verify | Verify | Verify | Verify | 20T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | 20¦23
20 | 24 | B20_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | 8A | Existing | Existing floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing 8A elevation shows UPS on ground, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | 20¦24
20 | 25 | B20_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦25
20 | 26 | B20_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦26
20 | 27 | B20_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 20¦27
20 | 28 | B20_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | 1B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 20T-701 identifies TE01-1B-1: 21 WAO total, 24 active ports per survey, 30 ports per schedule, 33 total ports with 10% allowance. Provide new wall-mount TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. | 20¦28
20 | 29 | B20_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | 8A | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Tel/Data Closet 8A contains open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy 48-port patch panel and Fiber LIU. Field verify all active services. | 20¦29
20 | 30 | B20_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦30
20 | 31 | B20_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦31
20 | 32 | B20_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 20¦32
20 | 33 | B20_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | 1B | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 20 does not appear to create a new TR door/PACS package. Verify any existing cameras/security devices in Office 1B and ensure no camera angle or VMS integration is disrupted. | 20¦33
20 | 34 | B20_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | 8A | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Keynotes indicate existing cameras are to be retained and re-used/protected in place; verify existing security equipment and cabinet impacts during cutover. | 20¦34
20 | 35 | B20_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦35
20 | 36 | B20_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦36
20 | 37 | B20_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 20¦37
20 | 38 | B20_Assessment | 45 | 8. OWNER RISKS | DATA | B20-R1 | All | Existing conditions for new Office 1B TE and existing Tel/Data Closet 8A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B20 has a compact TE scope but still depends on field conditions and existing equipment transfer. | 20¦38
20 | 39 | B20_Assessment | 46 | 8. OWNER RISKS | DATA | B20-R2 | 1B/8A | Existing equipment in 8A may remain active during transfer to new TE in 1B | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 20T-101 keynotes require transfer of existing devices and phasing plan. | 20¦39
20 | 40 | B20_Assessment | 47 | 8. OWNER RISKS | DATA | B20-R3 | 1B | Room naming and TE designation could cause PMIS mapping confusion | Medium | Medium | 4 | Track as Building 20 / Office 1B / TE01-1B-1 and link existing Room 8A as transition point | GCC / VA | Closed | Schedule is Office 1B and rack ID TE01-1B-1; existing telecom room is 8A. | 20¦40
20 | 41 | B20_Assessment | 48 | 8. OWNER RISKS | DATA | B20-R4 | 1B | No mechanical scope, but TE/UPS/network equipment may add heat load to Office 1B | High | Medium | 6 | Verify heat load, office ventilation, equipment clearances and owner acceptance before energizing enclosure | VA / Electrical / Telecom | Closed | Cover excludes mechanical/fire protection; existing HVAC may be relied on. | 20¦41
20 | 42 | B20_Assessment | 49 | 8. OWNER RISKS | DATA | B20-R5 | 1B | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs. | 20¦42
20 | 43 | B20_Assessment | 50 | 8. OWNER RISKS | DATA | B20-R6 | All | 459 feet of cable tray/pathway requires coordination despite small port count | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | Telecom / GC | Closed | 20T-701 cable tray schedule lists Level 1 estimated length of 459 ft. | 20¦43
20 | 44 | B20_Assessment | 51 | 8. OWNER RISKS | DATA | B20-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | 20T-101 requires fire caulk at sleeves and rated penetration protection. | 20¦44
20 | 45 | B20_Assessment | 52 | 8. OWNER RISKS | DATA | B20-R8 | All | Commissioning/test documentation may be overlooked due to TE-only scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification and owner signoff | GC / Cx Manager | Closed | Cover/general notes still require testing, acceptance and documentation. | 20¦45
20 | 46 | B20_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦46
20 | 47 | B20_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦47
20 | 48 | B20_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 20¦48
20 | 49 | B20_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B20-Q1 | Confirm final scope: new wall-mount TE enclosure in Office 1B and existing Tel/Data Closet 8A transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0 | 20¦49
20 | 50 | B20_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B20-Q2 | What active services are currently fed from existing 8A open TE cabinet and related equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 20¦50
20 | 51 | B20_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B20-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Office 1B? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 20¦51
20 | 52 | B20_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B20-Q4 | Is Office 1B HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0 | 20¦52
20 | 53 | B20_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B20-Q5 | Are existing cameras/security devices in Building 20 protected and retained with no VMS/PACS changes? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0 | 20¦53
20 | 54 | B20_Assessment | 61 | 9. OPEN QUESTIONS | DATA | B20-Q6 | Are all 459 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0 | 20¦54
20 | 55 | B20_Assessment | 62 | 9. OPEN QUESTIONS | DATA | B20-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0 | 20¦55
20 | 56 | B20_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B20-Q8 | Which test records and turnover documents are required for TE-only acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 20¦56
20 | 57 | B20_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦57
20 | 58 | B20_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦58
20 | 59 | B20_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 20¦59
20 | 60 | B20_Assessment | 67 | 10. PHOTO LOG | DATA | B20-P001 | 1B | Existing Condition | Office 1B wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B20-R1/B20-R3 | Closed | 0 | 20¦60
20 | 61 | B20_Assessment | 68 | 10. PHOTO LOG | DATA | B20-P002 | 8A | Existing Condition | Existing Tel/Data Closet 8A open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard and cable entries | 0 | Paul | 0 | B20-R1/B20-R2 | Closed | 0 | 20¦61
20 | 62 | B20_Assessment | 69 | 10. PHOTO LOG | DATA | B20-P003 | 8A | Existing Equipment | BIX blocks, Cisco switch, legacy Ortronics 48-port patch panel, UPS on ground and Fiber LIU on wall | 0 | Paul | 0 | B20-R2/B20-R5 | Closed | 0 | 20¦62
20 | 63 | B20_Assessment | 70 | 10. PHOTO LOG | DATA | B20-P004 | 1B/8A | Pathway | 459 ft Level 1 cable tray route, sleeves, wall penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B20-R6/B20-R7 | Closed | 0 | 20¦63
20 | 64 | B20_Assessment | 71 | 10. PHOTO LOG | DATA | B20-P005 | 1B | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and disconnect/access | 0 | Paul | 0 | B20-R5 | Closed | 0 | 20¦64
20 | 65 | B20_Assessment | 72 | 10. PHOTO LOG | DATA | B20-P006 | 1B/8A | Telecom | TE01-1B-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B20-R2/B20-R8 | Closed | 0 | 20¦65
20 | 66 | B20_Assessment | 73 | 10. PHOTO LOG | DATA | B20-P007 | All | Firestop | 4-inch speed sleeve, wall penetrations and fire caulk before/after photos | 0 | Paul | 0 | B20-R7 | Closed | 0 | 20¦66
20 | 67 | B20_Assessment | 74 | 10. PHOTO LOG | DATA | B20-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B20-R8 | Closed | 0 | 20¦67
20 | 68 | B20_Assessment | 75 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20¦68
21 | 1 | B21_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦1
21 | 2 | B21_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 21¦2
21 | 3 | B21_Assessment | 10 | 1. ROOM INVENTORY | DATA | 21 | 100A | First | M&O Foreman Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 21_19T-101 / 21_19T-604 / 21_19T-701 / 21_19E-101 | Primary Building 21/B19 TE. Plans identify M&O Foreman Office 100A at 202 SF with new 12RU telecom enclosure, shown as 19 serving 21, Room 100-A, and schedule Rack ID TR01-104-1 / RM 104. Includes APC UPS, two PDUs, network switches B20 and B19, 48-port Cat6A patch panel, Fiber LIU, and 131 total ports with 10% allowance. | 21¦3
21 | 4 | B21_Assessment | 11 | 1. ROOM INVENTORY | DATA | 21 | B1.TR | Basement | Existing telecom room / wall-mount TE | Existing telecom transition point | 1 | 0 | Verify | 21_19T-100 / 21_19T-604 | Existing Building 21 basement B1.TR shown with legacy Ortronics 24/48-port patch panels, UPS on ground, Cisco switch, multiple legacy 24-port patch panels, Fiber LIU, and APC floor UPS. Protect active services and verify transfer/cutover to new TE. | 21¦4
21 | 5 | B21_Assessment | 12 | 1. ROOM INVENTORY | DATA | 19 | B05TR | Basement / First | Existing telecom room / wall-mount TE | Existing telecom transition point serving B19/B21 | 2 | 0 | Verify | 21_19T-100 / 21_19T-604 / 21_19R-900 | Existing Building 19 B05TR shown with basement and first-level existing elevations, legacy Ortronics patch panels, Cisco switch, Fiber LIU, APC floor UPS, and photo reference for basement B05. New enclosure is marked '19 serving 21'. | 21¦5
21 | 6 | B21_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦6
21 | 7 | B21_Assessment | 14 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦7
21 | 8 | B21_Assessment | 15 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 21¦8
21 | 9 | B21_Assessment | 16 | 2. ROOM READINESS | DATA | 100A | Verify | Verify | N/A / Office | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in M&O Foreman Office 100A; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, and that office use can remain operational. | 21¦9
21 | 10 | B21_Assessment | 17 | 2. ROOM READINESS | DATA | B1.TR | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing B21 basement telecom room; verify active equipment status, pathway, UPS/backboard, Fiber LIU, and transition/abandonment scope. | 21¦10
21 | 11 | B21_Assessment | 18 | 2. ROOM READINESS | DATA | B05TR | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing B19 telecom room/equipment; verify active services, B19/B21 service boundary, path to new TE, and transition scope. | 21¦11
21 | 12 | B21_Assessment | 19 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦12
21 | 13 | B21_Assessment | 20 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦13
21 | 14 | B21_Assessment | 21 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 21¦14
21 | 15 | B21_Assessment | 22 | 3. FIRE PROTECTION | DATA | 100A | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 21_19 receives a Telecom Enclosure and fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. | 21¦15
21 | 16 | B21_Assessment | 23 | 3. FIRE PROTECTION | DATA | B1.TR | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing B21 basement TR; verify protection-in-place and firestopping after cable transfer or reuse. | 21¦16
21 | 17 | B21_Assessment | 24 | 3. FIRE PROTECTION | DATA | B05TR | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing B19 B05TR; verify protection-in-place and firestopping after cable transfer or reuse. | 21¦17
21 | 18 | B21_Assessment | 25 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦18
21 | 19 | B21_Assessment | 26 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦19
21 | 20 | B21_Assessment | 27 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 21¦20
21 | 21 | B21_Assessment | 28 | 4. HVAC / COOLING | DATA | 100A | Verify / Existing HVAC | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical sheets exist in index. Verify whether new TE heat load in Office 100A is supported by existing/new HVAC and whether any mechanical scope applies despite TE designation. | 21¦21
21 | 22 | B21_Assessment | 29 | 4. HVAC / COOLING | DATA | B1.TR | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing B21 B1.TR; verify environmental conditions during cutover and whether legacy equipment remains active. | 21¦22
21 | 23 | B21_Assessment | 30 | 4. HVAC / COOLING | DATA | B05TR | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing B19 B05TR; verify environmental conditions and whether equipment remains active during/after Building 21 transfer. | 21¦23
21 | 24 | B21_Assessment | 31 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦24
21 | 25 | B21_Assessment | 32 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦25
21 | 26 | B21_Assessment | 33 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 21¦26
21 | 27 | B21_Assessment | 34 | 5. ELECTRICAL / UPS | DATA | 100A | Verify | APC UPS / TE enclosure | Verify | Verify | 21_19E-101 / 21_19E-701 source to verify | Verify | Verify | Verify | 21_19T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switches, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | 21¦27
21 | 28 | B21_Assessment | 35 | 5. ELECTRICAL / UPS | DATA | B1.TR | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing B21 B1.TR elevation shows UPS on ground, Cisco switch, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements. | 21¦28
21 | 29 | B21_Assessment | 36 | 5. ELECTRICAL / UPS | DATA | B05TR | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing B19 B05TR elevations show APC floor UPS, legacy patch panels, Cisco switch and Fiber LIU; verify power source, active equipment and transfer/retention requirements. | 21¦29
21 | 30 | B21_Assessment | 37 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦30
21 | 31 | B21_Assessment | 38 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦31
21 | 32 | B21_Assessment | 39 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 21¦32
21 | 33 | B21_Assessment | 40 | 6. TELECOMMUNICATIONS | DATA | 100A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 21_19T-701 identifies RM 104 schedule: 90 WAO total, 67 active ports per survey, 119 ports per schedule, and 131 total ports with 10% allowance. 659 ft cable tray total: 63 ft basement and 596 ft first level. | 21¦33
21 | 34 | B21_Assessment | 41 | 6. TELECOMMUNICATIONS | DATA | B1.TR | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B21 B1.TR equipment includes multiple legacy patch panels, Cisco switch, UPS on ground, Fiber LIU and APC floor UPS; verify active services and transfer plan to new TE. | 21¦34
21 | 35 | B21_Assessment | 42 | 6. TELECOMMUNICATIONS | DATA | B05TR | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B19 B05TR equipment includes legacy Ortronics patch panels, Cisco switch, Fiber LIU and APC floor UPS; verify active services and whether B19/B21 devices are served from new enclosure. | 21¦35
21 | 36 | B21_Assessment | 43 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦36
21 | 37 | B21_Assessment | 44 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦37
21 | 38 | B21_Assessment | 45 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 21¦38
21 | 39 | B21_Assessment | 46 | 7. SECURITY / PACS / CCTV | DATA | 100A | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 21_19 appears to create a TE enclosure rather than a full TR door/PACS package. Verify any existing cameras/security devices in Room 100A and ensure no camera angle or VMS integration is disrupted. | 21¦39
21 | 40 | B21_Assessment | 47 | 7. SECURITY / PACS / CCTV | DATA | B1.TR | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify any existing security device/cabinet impacts during cutover. | 21¦40
21 | 41 | B21_Assessment | 48 | 7. SECURITY / PACS / CCTV | DATA | B05TR | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/camera protection-in-place and any impact from B19/B21 shared telecom equipment. | 21¦41
21 | 42 | B21_Assessment | 49 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦42
21 | 43 | B21_Assessment | 50 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦43
21 | 44 | B21_Assessment | 51 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 21¦44
21 | 45 | B21_Assessment | 52 | 8. OWNER RISKS | DATA | B21-R1 | All | Existing conditions for new 100A TE, B21 B1.TR and B19 B05TR not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B21 is combined with B19 and has multiple transition points. | 21¦45
21 | 46 | B21_Assessment | 53 | 8. OWNER RISKS | DATA | B21-R2 | 100A/B1.TR/B05TR | Existing equipment may remain active during transfer to new TE enclosure | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | Rack elevations show existing B21 and B19 equipment and new 19-serving-21 enclosure. | 21¦46
21 | 47 | B21_Assessment | 54 | 8. OWNER RISKS | DATA | B21-R3 | 100A | Room naming mismatch: schedule says RM 104 / TR01-104-1 while plan/enlarged view identifies Room 100A | High | Medium | 6 | Track PMIS as Building 21 / Room 100A / Schedule RM 104 / Rack ID TR01-104-1 and confirm with designer | GCC / VA / Designer | Closed | Important for PMIS mapping and field punch list. | 21¦47
21 | 48 | B21_Assessment | 55 | 8. OWNER RISKS | DATA | B21-R4 | All | B19/B21 combined package may blur scope boundary and ownership of ports | High | Medium | 6 | Separate Building 21 work, Building 19 transition work, and shared service/cross-connect items in PMIS notes | GCC / OIT | Closed | Sheet package is 21_19 and new enclosure is labeled 19 serving 21. | 21¦48
21 | 49 | B21_Assessment | 56 | 8. OWNER RISKS | DATA | B21-R5 | 100A | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and PDUs. | 21¦49
21 | 50 | B21_Assessment | 57 | 8. OWNER RISKS | DATA | B21-R6 | All | 659 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | Telecom / GC | Closed | 21_19T-701 cable tray schedule lists 63 ft basement and 596 ft first level. | 21¦50
21 | 51 | B21_Assessment | 58 | 8. OWNER RISKS | DATA | B21-R7 | All | Fire protection scope excluded, but rated penetrations and temporary firestopping still apply | High | Medium | 6 | Track 4-inch sleeves, rated penetrations, fire caulk, temporary firestopping and patching even without FP scope | GC / Firestop | Closed | Cover excludes fire protection; telecom notes require fire caulk and rated penetrations. | 21¦51
21 | 52 | B21_Assessment | 59 | 8. OWNER RISKS | DATA | B21-R8 | All | Commissioning/test documentation may be overlooked due to TE-only scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification and owner signoff | GC / Cx Manager | Closed | General notes still require testing, acceptance and documentation. | 21¦52
21 | 53 | B21_Assessment | 60 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦53
21 | 54 | B21_Assessment | 61 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦54
21 | 55 | B21_Assessment | 62 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 21¦55
21 | 56 | B21_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B21-Q1 | Confirm final scope: new TE enclosure at Room 100A/RM 104 and existing B21 B1.TR plus B19 B05TR transition? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0 | 21¦56
21 | 57 | B21_Assessment | 64 | 9. OPEN QUESTIONS | DATA | B21-Q2 | Why does 21_19T-701 list RM 104 / TR01-104-1 while enlarged plan identifies Room 100A? | VA / Designer / OIT | Closed | 0 | 0 | Room naming mismatch could affect PMIS tracking | 0 | 0 | 0 | 21¦57
21 | 58 | B21_Assessment | 65 | 9. OPEN QUESTIONS | DATA | B21-Q3 | What active services are currently fed from existing B21 B1.TR and B19 B05TR equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 21¦58
21 | 59 | B21_Assessment | 66 | 9. OPEN QUESTIONS | DATA | B21-Q4 | What exactly is meant by '19 serving 21' on the new TE enclosure elevation? | VA / OIT / Designer | Closed | 0 | 0 | Building 19/21 boundary unclear | 0 | 0 | 0 | 21¦59
21 | 60 | B21_Assessment | 67 | 9. OPEN QUESTIONS | DATA | B21-Q5 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in 100A? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 21¦60
21 | 61 | B21_Assessment | 68 | 9. OPEN QUESTIONS | DATA | B21-Q6 | Are all 659 ft of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0 | 21¦61
21 | 62 | B21_Assessment | 69 | 9. OPEN QUESTIONS | DATA | B21-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0 | 21¦62
21 | 63 | B21_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B21-Q8 | Which test records and turnover documents are required for TE-only acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 21¦63
21 | 64 | B21_Assessment | 71 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦64
21 | 65 | B21_Assessment | 72 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦65
21 | 66 | B21_Assessment | 73 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 21¦66
21 | 67 | B21_Assessment | 74 | 10. PHOTO LOG | DATA | B21-P001 | 100A | Existing Condition | M&O Foreman Office 100A wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B21-R1/B21-R3 | Closed | 0 | 21¦67
21 | 68 | B21_Assessment | 75 | 10. PHOTO LOG | DATA | B21-P002 | B1.TR | Existing Condition | Existing B21 basement B1.TR wall TE, legacy patch panels, Cisco switch, Fiber LIU, UPS on ground and cable entries | 0 | Paul | 0 | B21-R1/B21-R2 | Closed | 0 | 21¦68
21 | 69 | B21_Assessment | 76 | 10. PHOTO LOG | DATA | B21-P003 | B05TR | Existing Condition | Existing B19 B05TR basement and first-level TE/equipment, APC floor UPS, Cisco switch, patch panels, Fiber LIU and pathways | 0 | Paul | 0 | B21-R1/B21-R4 | Closed | 0 | 21¦69
21 | 70 | B21_Assessment | 77 | 10. PHOTO LOG | DATA | B21-P004 | 100A/B05TR/B1.TR | Pathway | 659 ft cable tray route, sleeves, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B21-R6/B21-R7 | Closed | 0 | 21¦70
21 | 71 | B21_Assessment | 78 | 10. PHOTO LOG | DATA | B21-P005 | 100A | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B21-R5 | Closed | 0 | 21¦71
21 | 72 | B21_Assessment | 79 | 10. PHOTO LOG | DATA | B21-P006 | 100A/B1.TR/B05TR | Telecom | TR01-104-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B21-R2/B21-R8 | Closed | 0 | 21¦72
21 | 73 | B21_Assessment | 80 | 10. PHOTO LOG | DATA | B21-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B21-R7 | Closed | 0 | 21¦73
21 | 74 | B21_Assessment | 81 | 10. PHOTO LOG | DATA | B21-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B21-R8 | Closed | 0 | 21¦74
21 | 75 | B21_Assessment | 82 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21¦75
22 | 1 | B22_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦1
22 | 2 | B22_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 22¦2
22 | 3 | B22_Assessment | 10 | 1. ROOM INVENTORY | DATA | 22 | 102 | First | Break Room / new TE location | Telecom Enclosure | 1 | 0 | Verify | 22T-101 / 22T-701 / 22E-101 / 22E-701 | Primary Building 22 TE. Plans identify Break Room 102 at 358 SF with new 12RU telecom enclosure Rack ID TR01-102-1, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and 8 total ports with 10% allowance. | 22¦3
22 | 4 | B22_Assessment | 11 | 1. ROOM INVENTORY | DATA | 22 | 103 | First | Existing wall/wall-mount TE / legacy equipment area | Existing telecom transition point | 1 | 0 | Verify | 22T-101 / 22T-701 / 22R-900 | Existing Room 103 first-level wall/wall-mount TE shown with APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall, and ports 1-24 to Building 19 ports 73-96. Protect active services and transfer to Room 102 TE. | 22¦4
22 | 5 | B22_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦5
22 | 6 | B22_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦6
22 | 7 | B22_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 22¦7
22 | 8 | B22_Assessment | 15 | 2. ROOM READINESS | DATA | 102 | Verify | Verify | N/A / Break Room | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in Break Room 102; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, and that break-room use can remain operational. | 22¦8
22 | 9 | B22_Assessment | 16 | 2. ROOM READINESS | DATA | 103 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing first-level wall/wall-mount TE; verify active equipment status, UPS, Cisco switch, SERTEX utility service, Fiber LIU, pathway, and transition/abandonment scope. | 22¦9
22 | 10 | B22_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦10
22 | 11 | B22_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦11
22 | 12 | B22_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 22¦12
22 | 13 | B22_Assessment | 20 | 3. FIRE PROTECTION | DATA | 102 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 22 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. | 22¦13
22 | 14 | B22_Assessment | 21 | 3. FIRE PROTECTION | DATA | 103 | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing TE room; verify protection-in-place and firestopping after cable transfer or reuse. | 22¦14
22 | 15 | B22_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦15
22 | 16 | B22_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦16
22 | 17 | B22_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 22¦17
22 | 18 | B22_Assessment | 25 | 4. HVAC / COOLING | DATA | 102 | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Cover sheet states mechanical scope is excluded. Verify whether Break Room 102 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | 22¦18
22 | 19 | B22_Assessment | 26 | 4. HVAC / COOLING | DATA | 103 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing Room 103 equipment area; verify existing environmental conditions during cutover and whether legacy equipment remains active. | 22¦19
22 | 20 | B22_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦20
22 | 21 | B22_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦21
22 | 22 | B22_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 22¦22
22 | 23 | B22_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | 102 | Verify | APC UPS / TE enclosure | Verify | Verify | 22E-101 / 22E-701 source to verify | Verify | Verify | Verify | 22T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | 22¦23
22 | 24 | B22_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | 103 | Existing | Existing APC UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing 103 elevation shows APC UPS, Cisco switch, SERTEX utility service, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | 22¦24
22 | 25 | B22_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦25
22 | 26 | B22_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦26
22 | 27 | B22_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 22¦27
22 | 28 | B22_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | 102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 22T-701 identifies TR01-102-1: 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total port quantities, and 8 total ports with 10% allowance. Provide new wall-mount 12RU TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. | 22¦28
22 | 29 | B22_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | 103 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing Room 103 contains APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall and ports 1-24 to Bldg 19 ports 73-96. Field verify all active services and B19 handoff. | 22¦29
22 | 30 | B22_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦30
22 | 31 | B22_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦31
22 | 32 | B22_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 22¦32
22 | 33 | B22_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | 102 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 22 does not appear to create a new full TR door/PACS package. Verify any existing cameras/security devices in Break Room 102 and ensure no camera angle or VMS integration is disrupted. | 22¦33
22 | 34 | B22_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | 103 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Verify security/access conditions and whether any legacy security equipment is present at existing TE location. | 22¦34
22 | 35 | B22_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦35
22 | 36 | B22_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦36
22 | 37 | B22_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 22¦37
22 | 38 | B22_Assessment | 45 | 8. OWNER RISKS | DATA | B22-R1 | All | Existing conditions for new Break Room 102 TE and existing Room 103 TE not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B22 has a compact TE scope but still depends on field conditions and existing equipment transfer. | 22¦38
22 | 39 | B22_Assessment | 46 | 8. OWNER RISKS | DATA | B22-R2 | 102/103 | Existing equipment in 103 may remain active during transfer to new TE in 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 22T-101 keynotes require transfer of existing devices and phasing plan. | 22¦39
22 | 40 | B22_Assessment | 47 | 8. OWNER RISKS | DATA | B22-R3 | 102 | Break Room 102 use may conflict with wall-mount TE access and clearances | Medium | Medium | 4 | Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance | GCC / VA | Closed | New TE is in Break Room 102 rather than a dedicated TR. | 22¦40
22 | 41 | B22_Assessment | 48 | 8. OWNER RISKS | DATA | B22-R4 | 102 | No mechanical scope, but TE/UPS/network equipment may add heat load to Break Room 102 | High | Medium | 6 | Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure | VA / Electrical / Telecom | Closed | Cover excludes mechanical/fire protection; existing HVAC may be relied on. | 22¦41
22 | 42 | B22_Assessment | 49 | 8. OWNER RISKS | DATA | B22-R5 | 102 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs. | 22¦42
22 | 43 | B22_Assessment | 50 | 8. OWNER RISKS | DATA | B22-R6 | All | 139 feet of cable tray/pathway requires coordination despite small port count | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | Telecom / GC | Closed | 22T-701 cable tray schedule lists first floor estimated length of 139 ft. | 22¦43
22 | 44 | B22_Assessment | 51 | 8. OWNER RISKS | DATA | B22-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | 22T-101 requires fire caulk at sleeves and rated penetration protection. | 22¦44
22 | 45 | B22_Assessment | 52 | 8. OWNER RISKS | DATA | B22-R8 | 103 / B19 | Existing SERTEX utility service and B19 port relationship may create cutover dependency | High | Medium | 6 | Verify ports 1-24 to Bldg 19 ports 73-96, service provider dependency, labels, test records and OIT approval | Telecom / OIT | Closed | Existing Room 103 elevation identifies ports to Building 19. | 22¦45
22 | 46 | B22_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦46
22 | 47 | B22_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦47
22 | 48 | B22_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 22¦48
22 | 49 | B22_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B22-Q1 | Confirm final scope: new wall-mount TE enclosure in Break Room 102 and existing Room 103 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0 | 22¦49
22 | 50 | B22_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B22-Q2 | What active services are currently fed from existing Room 103 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 22¦50
22 | 51 | B22_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B22-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 22¦51
22 | 52 | B22_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B22-Q4 | Is Break Room 102 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0 | 22¦52
22 | 53 | B22_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B22-Q5 | Are existing cameras/security devices in Building 22 protected and retained with no VMS/PACS changes? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0 | 22¦53
22 | 54 | B22_Assessment | 61 | 9. OPEN QUESTIONS | DATA | B22-Q6 | Are all 139 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0 | 22¦54
22 | 55 | B22_Assessment | 62 | 9. OPEN QUESTIONS | DATA | B22-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0 | 22¦55
22 | 56 | B22_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B22-Q8 | What is the operational impact of Room 103 ports 1-24 to Building 19 ports 73-96? | VA / OIT / Designer | Closed | 0 | 0 | B19 dependency/cutover risk | 0 | 0 | 0 | 22¦56
22 | 57 | B22_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦57
22 | 58 | B22_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦58
22 | 59 | B22_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 22¦59
22 | 60 | B22_Assessment | 67 | 10. PHOTO LOG | DATA | B22-P001 | 102 | Existing Condition | Break Room 102 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B22-R1/B22-R3 | Closed | 0 | 22¦60
22 | 61 | B22_Assessment | 68 | 10. PHOTO LOG | DATA | B22-P002 | 103 | Existing Condition | Existing Room 103 wall/wall-mount TE, APC UPS, Cisco switch, SERTEX utility service, legacy patch panel, Fiber LIU and cable entries | 0 | Paul | 0 | B22-R1/B22-R2 | Closed | 0 | 22¦61
22 | 62 | B22_Assessment | 69 | 10. PHOTO LOG | DATA | B22-P003 | 103 / B19 | Existing Equipment | Ports 1-24 to Building 19 ports 73-96, active service labeling, utility service and handoff condition | 0 | Paul | 0 | B22-R8 | Closed | 0 | 22¦62
22 | 63 | B22_Assessment | 70 | 10. PHOTO LOG | DATA | B22-P004 | 102/103 | Pathway | 139 ft first-floor cable tray route, sleeves, wall penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B22-R6/B22-R7 | Closed | 0 | 22¦63
22 | 64 | B22_Assessment | 71 | 10. PHOTO LOG | DATA | B22-P005 | 102 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B22-R5 | Closed | 0 | 22¦64
22 | 65 | B22_Assessment | 72 | 10. PHOTO LOG | DATA | B22-P006 | 102/103 | Telecom | TR01-102-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B22-R2/B22-R8 | Closed | 0 | 22¦65
22 | 66 | B22_Assessment | 73 | 10. PHOTO LOG | DATA | B22-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B22-R7 | Closed | 0 | 22¦66
22 | 67 | B22_Assessment | 74 | 10. PHOTO LOG | DATA | B22-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B22-R8 | Closed | 0 | 22¦67
22 | 68 | B22_Assessment | 75 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22¦68
33 | 1 | B33_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦1
33 | 2 | B33_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 33¦2
33 | 3 | B33_Assessment | 10 | 1. ROOM INVENTORY | DATA | 33 | B23 | Basement | EEO Manager Office / new TE location | Telecom Enclosure | 1 | 0 | Verify | 33T-100 / 33T-604 / 33T-701 / 33E-100 / 33E-701 | Primary Building 33 TE. Plans identify EEO Manager Office B23 at 175 SF with new 12RU telecom enclosure Rack ID TE01-B23-1, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, 55 WAO total, and 97 total ports with 10% allowance. | 33¦3
33 | 4 | B33_Assessment | 11 | 1. ROOM INVENTORY | DATA | 33 | B17 | Basement / First photo reference | Existing Tel Closet / open TE cabinet and legacy equipment | Existing telecom transition point | 2 | 0 | Verify | 33T-100 / 33T-604 / 33R-900 | Existing Tel Closet B17 shown at 13 SF with existing open TE cabinet, network door controller, indoor AC unit, plywood backboard, keypad, patch panel, ground bar, equipment box, Cisco switches, legacy patch panels, Fiber LIU, SERTEX utility service, and UPS on floor. Protect active services and verify transfer to Room B23 TE. | 33¦4
33 | 5 | B33_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦5
33 | 6 | B33_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦6
33 | 7 | B33_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 33¦7
33 | 8 | B33_Assessment | 15 | 2. ROOM READINESS | DATA | B23 | Verify | Verify | N/A / Office | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in EEO Manager Office B23; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, and office-use impacts. | 33¦8
33 | 9 | B33_Assessment | 16 | 2. ROOM READINESS | DATA | B17 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing Tel Closet; verify active equipment status, open TE cabinet, indoor AC, network door controller, keypad/security devices, UPS, backboard, Fiber LIU, and transition/abandonment scope. | 33¦9
33 | 10 | B33_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦10
33 | 11 | B33_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦11
33 | 12 | B33_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 33¦12
33 | 13 | B33_Assessment | 20 | 3. FIRE PROTECTION | DATA | B23 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 33 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. | 33¦13
33 | 14 | B33_Assessment | 21 | 3. FIRE PROTECTION | DATA | B17 | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing Tel Closet; verify protection-in-place and firestopping after cable transfer or reuse. | 33¦14
33 | 15 | B33_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦15
33 | 16 | B33_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦16
33 | 17 | B33_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 33¦17
33 | 18 | B33_Assessment | 25 | 4. HVAC / COOLING | DATA | B23 | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Cover sheet states mechanical scope is excluded. Verify whether Office B23 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. | 33¦18
33 | 19 | B33_Assessment | 26 | 4. HVAC / COOLING | DATA | B17 | Existing indoor AC unit | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing B17 enlarged plan identifies an existing indoor AC unit. Verify operation during cutover and determine whether active legacy equipment remains after transfer to B23. | 33¦19
33 | 20 | B33_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦20
33 | 21 | B33_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦21
33 | 22 | B33_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 33¦22
33 | 23 | B33_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | B23 | Verify | APC UPS / TE enclosure | Verify | Verify | 33E-100 / 33E-701 source to verify | Verify | Verify | Verify | 33T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. | 33¦23
33 | 24 | B33_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | B17 | Existing | Existing UPS on floor | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing B17 elevations show UPS on floor, Cisco switches, SERTEX utility service, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements before disconnect/removal. | 33¦24
33 | 25 | B33_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦25
33 | 26 | B33_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦26
33 | 27 | B33_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 33¦27
33 | 28 | B33_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | B23 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 33T-701 identifies TE01-B23-1: 55 WAO total, 34 active ports per survey, 88 total ports per schedule, and 97 total ports with 10% allowance. Basement cable tray schedule totals 102 ft. Provide 10 new Cat6A cross-connect cables from existing TE to new TE location. | 33¦28
33 | 29 | B33_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | B17 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B17 rack elevations include Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, passive Fiber LIU/wall mount, UPS on floor and cross-building port references to Bldgs 3, 80 and 82. | 33¦29
33 | 30 | B33_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦30
33 | 31 | B33_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦31
33 | 32 | B33_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 33¦32
33 | 33 | B33_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | B23 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 33 does not appear to create a new full TR door/PACS package. Verify existing cameras/security devices in B23 and ensure no camera angle or VMS integration is disrupted. | 33¦33
33 | 34 | B33_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | B17 | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify | Verify | Existing B17 enlarged plan identifies network door controller, keypad and equipment box; verify protection-in-place and whether any security equipment is relocated or recabled. | 33¦34
33 | 35 | B33_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦35
33 | 36 | B33_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦36
33 | 37 | B33_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 33¦37
33 | 38 | B33_Assessment | 45 | 8. OWNER RISKS | DATA | B33-R1 | All | Existing conditions for new B23 TE and existing B17 Tel Closet not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B33 has a compact TE scope but depends on existing equipment transfer and field conditions. | 33¦38
33 | 39 | B33_Assessment | 46 | 8. OWNER RISKS | DATA | B33-R2 | B23/B17 | Existing equipment in B17 may remain active during transfer to new TE in B23 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 33T-100 keynotes require transfer of existing devices and phasing plan. | 33¦39
33 | 40 | B33_Assessment | 47 | 8. OWNER RISKS | DATA | B33-R3 | B23 | Office B23 use may conflict with wall-mount TE access and clearances | Medium | Medium | 4 | Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance | GCC / VA | Closed | New TE is in EEO Manager Office B23 rather than a dedicated TR. | 33¦40
33 | 41 | B33_Assessment | 48 | 8. OWNER RISKS | DATA | B33-R4 | B23 | No mechanical scope, but TE/UPS/network equipment may add heat load to Office B23 | High | Medium | 6 | Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure | VA / Electrical / Telecom | Closed | Cover excludes mechanical/fire protection; existing HVAC may be relied on. | 33¦41
33 | 42 | B33_Assessment | 49 | 8. OWNER RISKS | DATA | B33-R5 | B23 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs. | 33¦42
33 | 43 | B33_Assessment | 50 | 8. OWNER RISKS | DATA | B33-R6 | All | 102 feet of basement cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | Telecom / GC | Closed | 33T-701 cable tray schedule lists basement level estimated length of 102 ft. | 33¦43
33 | 44 | B33_Assessment | 51 | 8. OWNER RISKS | DATA | B33-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | 33T-100 requires fire caulk at sleeves and rated penetration protection. | 33¦44
33 | 45 | B33_Assessment | 52 | 8. OWNER RISKS | DATA | B33-R8 | B17 / Other Bldgs | Existing B17 cross-building service relationships may create cutover dependency | High | Medium | 6 | Verify ports to Bldgs 3, 80 and 82, SERTEX utility service, labels, test records, service provider dependency and OIT approval | Telecom / OIT | Closed | Existing B17 elevation identifies ports 1-72 to Bldg 3, 73-96 to Bldg 80, 97-120 to Bldg 82, and 121-144 to Bldg 3. | 33¦45
33 | 46 | B33_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦46
33 | 47 | B33_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦47
33 | 48 | B33_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 33¦48
33 | 49 | B33_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B33-Q1 | Confirm final scope: new wall-mount TE enclosure in B23 and existing B17 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0 | 33¦49
33 | 50 | B33_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B33-Q2 | What active services are currently fed from existing B17 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 33¦50
33 | 51 | B33_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B33-Q3 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in B23? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 33¦51
33 | 52 | B33_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B33-Q4 | Is Office B23 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk after mechanical scope excluded | 0 | 0 | 0 | 33¦52
33 | 53 | B33_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B33-Q5 | Are existing cameras/security devices in Building 33 protected and retained with no VMS/PACS disruption? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0 | 33¦53
33 | 54 | B33_Assessment | 61 | 9. OPEN QUESTIONS | DATA | B33-Q6 | Are all 102 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0 | 33¦54
33 | 55 | B33_Assessment | 62 | 9. OPEN QUESTIONS | DATA | B33-Q7 | Are the 10 new Cat6A cross-connect cables from existing TE to new TE location coordinated and labeled? | Telecom / OIT | Closed | 0 | 0 | Cutover and labeling risk | 0 | 0 | 0 | 33¦55
33 | 56 | B33_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B33-Q8 | What is the operational impact of B17 ports serving Buildings 3, 80 and 82? | VA / OIT / Designer | Closed | 0 | 0 | Cross-building dependency/cutover risk | 0 | 0 | 0 | 33¦56
33 | 57 | B33_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦57
33 | 58 | B33_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦58
33 | 59 | B33_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 33¦59
33 | 60 | B33_Assessment | 67 | 10. PHOTO LOG | DATA | B33-P001 | B23 | Existing Condition | EEO Manager Office B23 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B33-R1/B33-R3 | Closed | 0 | 33¦60
33 | 61 | B33_Assessment | 68 | 10. PHOTO LOG | DATA | B33-P002 | B17 | Existing Condition | Existing Tel Closet B17 open TE cabinet, network door controller, indoor AC unit, plywood backboard, keypad, patch panel, ground bar and equipment box | 0 | Paul | 0 | B33-R1/B33-R2 | Closed | 0 | 33¦61
33 | 62 | B33_Assessment | 69 | 10. PHOTO LOG | DATA | B33-P003 | B17 | Existing Equipment | Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, Fiber LIU, UPS on floor and cross-building port labels | 0 | Paul | 0 | B33-R2/B33-R8 | Closed | 0 | 33¦62
33 | 63 | B33_Assessment | 70 | 10. PHOTO LOG | DATA | B33-P004 | B23/B17 | Pathway | 102 ft basement cable tray route, 4-inch sleeve, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B33-R6/B33-R7 | Closed | 0 | 33¦63
33 | 64 | B33_Assessment | 71 | 10. PHOTO LOG | DATA | B33-P005 | B23 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, grounding/bonding, labels and access | 0 | Paul | 0 | B33-R5 | Closed | 0 | 33¦64
33 | 65 | B33_Assessment | 72 | 10. PHOTO LOG | DATA | B33-P006 | B23/B17 | Telecom | TE01-B23-1 enclosure, cross-connect cables, Fiber LIU, patch panels, labels, test results and existing B17 equipment transfer | 0 | Paul | 0 | B33-R2/B33-R8 | Closed | 0 | 33¦65
33 | 66 | B33_Assessment | 73 | 10. PHOTO LOG | DATA | B33-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B33-R7 | Closed | 0 | 33¦66
33 | 67 | B33_Assessment | 74 | 10. PHOTO LOG | DATA | B33-P008 | B17/B23 | Security / Existing Devices | Existing cameras, network door controller, keypad and equipment box to remain/protect or be recabled | 0 | Paul | 0 | B33-R8 | Closed | 0 | 33¦67
33 | 68 | B33_Assessment | 75 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33¦68
61 | 1 | B61_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦1
61 | 2 | B61_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 61¦2
61 | 3 | B61_Assessment | 10 | 1. ROOM INVENTORY | DATA | 61 | B13H-A | Basement | Basement telecom / support area | Telecom Room | 1 | 1 | Pass | 61A-400 / 61E-401 / 61T-100 / 61T-401 / 61T-604 / 61T-701 | Basement TR identified as RM B13H-A with Rack ID TR01-B13H-A-1. Schedules identify 88 WAO total, 74 active ports, 129 scheduled ports, 142 ports with 10% allowance. Electrical panels include B61-TRB13A/B. Mechanical cooling includes IU-0-01/CU-0-01. | 61¦3
61 | 4 | B61_Assessment | 11 | 1. ROOM INVENTORY | DATA | 61 | 124 | First | First-level telecom area | Telecom Room | 1 | 1 | Pass | 61A-400 / 61E-402 / 61T-101 / 61T-401 / 61T-604 / 61T-701 | First-level TR identified as Room 124 / Rack ID TR01-124-1. Electrical panels include B61-TR124A/B. Mechanical cooling includes IU-1-01/CU-1-01. Verify room naming against electrical schedule references that also call out RM137B rack receptacles. | 61¦4
61 | 5 | B61_Assessment | 12 | 1. ROOM INVENTORY | DATA | 61 | 226 | Second | Second-level telecom area | Telecom Room | 1 | 1 | Pass | 61A-401 / 61E-402 / 61T-102 / 61T-401 / 61T-605 / 61T-702 | Second-level TR identified as Room 226 / Rack ID TR01-226-1. Schedules identify 109 WAO total, 126 active ports, 156 scheduled ports, 172 ports with 10% allowance. Electrical panels include B61-TR226A/B. Mechanical cooling includes IU-2-01/CU-2-01. | 61¦5
61 | 6 | B61_Assessment | 13 | 1. ROOM INVENTORY | DATA | 61 | 137 / 137A | First | Existing server/demarc/telecom equipment rooms | Existing demarc / server transition point | 11 | 0 | Pass | 61T-402 / 61T-606 / 61T-607 / 61R-900 | Existing Room 137/137A rack inventory and demarc/server equipment include existing 4-post racks, PACS/equipment racks, APC UPS/PDU equipment, Fujitsu FLM equipment, wall-mounted patch panels, and local elevations. Protect active services and verify what remains, transfers, or is modified. | 61¦6
61 | 7 | B61_Assessment | 14 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦7
61 | 8 | B61_Assessment | 15 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦8
61 | 9 | B61_Assessment | 16 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 61¦9
61 | 10 | B61_Assessment | 17 | 2. ROOM READINESS | DATA | B13H-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify rated walls/open-to-deck conditions, door/security, floor finish, ladder rack/cable tray, future rack clearance, wall backing, and pathway entries. | 61¦10
61 | 11 | B61_Assessment | 18 | 2. ROOM READINESS | DATA | 124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify rated construction, door hardware, ceiling/deck, rack/future rack clearances, wall backing, and riser/pathway entries. | 61¦11
61 | 12 | B61_Assessment | 19 | 2. ROOM READINESS | DATA | 226 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR; verify rated construction, door hardware, ceiling/deck, rack/future rack clearances, wall backing, and riser/pathway entries. | 61¦12
61 | 13 | B61_Assessment | 20 | 2. ROOM READINESS | DATA | 137 / 137A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing demarc/server rooms; verify existing rack inventory, operational continuity, active circuits, access control, airflow and protection-in-place. | 61¦13
61 | 14 | B61_Assessment | 21 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦14
61 | 15 | B61_Assessment | 22 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦15
61 | 16 | B61_Assessment | 23 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 61¦16
61 | 17 | B61_Assessment | 24 | 3. FIRE PROTECTION | DATA | B13H-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. | 61¦17
61 | 18 | B61_Assessment | 25 | 3. FIRE PROTECTION | DATA | 124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. | 61¦18
61 | 19 | B61_Assessment | 26 | 3. FIRE PROTECTION | DATA | 226 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. | 61¦19
61 | 20 | B61_Assessment | 27 | 3. FIRE PROTECTION | DATA | 137 / 137A | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | 61¦20
61 | 21 | B61_Assessment | 28 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦21
61 | 22 | B61_Assessment | 29 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦22
61 | 23 | B61_Assessment | 30 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 61¦23
61 | 24 | B61_Assessment | 31 | 4. HVAC / COOLING | DATA | B13H-A | IU-0-01 / CU-0-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. | 61¦24
61 | 25 | B61_Assessment | 32 | 4. HVAC / COOLING | DATA | 124 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. | 61¦25
61 | 26 | B61_Assessment | 33 | 4. HVAC / COOLING | DATA | 226 | IU-2-01 / CU-2-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. | 61¦26
61 | 27 | B61_Assessment | 34 | 4. HVAC / COOLING | DATA | 137 / 137A | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | 61¦27
61 | 28 | B61_Assessment | 35 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦28
61 | 29 | B61_Assessment | 36 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦29
61 | 30 | B61_Assessment | 37 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 61¦30
61 | 31 | B61_Assessment | 38 | 5. ELECTRICAL / UPS | DATA | B13H-A | Verify | 5 kW / 208V rack UPS | Verify | Verify | B61-TRB13A / B61-TRB13B | Verify | Verify | Verify | Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. | 61¦31
61 | 32 | B61_Assessment | 39 | 5. ELECTRICAL / UPS | DATA | 124 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B61-TR124A / B61-TR124B | Verify | Verify | Verify | Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. | 61¦32
61 | 33 | B61_Assessment | 40 | 5. ELECTRICAL / UPS | DATA | 226 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B61-TR226A / B61-TR226B | Verify | Verify | Verify | Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. | 61¦33
61 | 34 | B61_Assessment | 41 | 5. ELECTRICAL / UPS | DATA | 137 / 137A | Existing / Verify | Existing APC UPS/PDU | Existing / Verify | Verify | B61-TR137AA / B61-TR137AB / existing | Verify | Verify | Verify | Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | 61¦34
61 | 35 | B61_Assessment | 42 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦35
61 | 36 | B61_Assessment | 43 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦36
61 | 37 | B61_Assessment | 44 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 61¦37
61 | 38 | B61_Assessment | 45 | 6. TELECOMMUNICATIONS | DATA | B13H-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. | 61¦38
61 | 39 | B61_Assessment | 46 | 6. TELECOMMUNICATIONS | DATA | 124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. | 61¦39
61 | 40 | B61_Assessment | 47 | 6. TELECOMMUNICATIONS | DATA | 226 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. | 61¦40
61 | 41 | B61_Assessment | 48 | 6. TELECOMMUNICATIONS | DATA | 137 / 137A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service. | 61¦41
61 | 42 | B61_Assessment | 49 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦42
61 | 43 | B61_Assessment | 50 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦43
61 | 44 | B61_Assessment | 51 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 61¦44
61 | 45 | B61_Assessment | 52 | 7. SECURITY / PACS / CCTV | DATA | B13H-A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. | 61¦45
61 | 46 | B61_Assessment | 53 | 7. SECURITY / PACS / CCTV | DATA | 124 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify TR door hardware and access control, CCTV camera, network door controller and integration. | 61¦46
61 | 47 | B61_Assessment | 54 | 7. SECURITY / PACS / CCTV | DATA | 226 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. | 61¦47
61 | 48 | B61_Assessment | 55 | 7. SECURITY / PACS / CCTV | DATA | 137 / 137A | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | 61¦48
61 | 49 | B61_Assessment | 56 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦49
61 | 50 | B61_Assessment | 57 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦50
61 | 51 | B61_Assessment | 58 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 61¦51
61 | 52 | B61_Assessment | 59 | 8. OWNER RISKS | DATA | B61-R1 | All | Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified | High | Medium | 6 | Perform existing conditions survey with photos and active-service inventory before mobilization | GCC / Contractor | Closed | Large multi-room scope with active demarc/server equipment. | 61¦52
61 | 53 | B61_Assessment | 60 | 8. OWNER RISKS | DATA | B61-R2 | B13H-A / 124 / 226 | Hazardous material abatement plans exist for first and second levels | High | Medium | 6 | Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation | GC / IH / COR | Closed | Drawing index includes 61H-101 and 61H-102 hazardous material abatement plans. | 61¦53
61 | 54 | B61_Assessment | 61 | 8. OWNER RISKS | DATA | B61-R3 | 137 / 137A | Existing server/demarc equipment may remain active during cutover | Critical | Medium | 8 | Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path | OIT / Telecom | Closed | Existing APC/Fujitsu/rack/patch equipment shown in Room 137 inventory/rack elevations. | 61¦54
61 | 55 | B61_Assessment | 62 | 8. OWNER RISKS | DATA | B61-R4 | All TRs | Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR/server readiness. | 61¦55
61 | 56 | B61_Assessment | 63 | 8. OWNER RISKS | DATA | B61-R5 | All TRs | Panel source, UPS/PDU and rack receptacle coordination could delay energization | Critical | Medium | 8 | Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements | Electrical / GCC | Closed | Multiple telecom panelboards and PD panels shown. | 61¦56
61 | 57 | B61_Assessment | 64 | 8. OWNER RISKS | DATA | B61-R6 | All | Large cable tray scope creates coordination and firestop risk | High | Medium | 6 | Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 890 ft, first 499 ft, second 578 ft. | 61¦57
61 | 58 | B61_Assessment | 65 | 8. OWNER RISKS | DATA | B61-R7 | All | Telecom/fiber cutover could affect active hospital communications and server/demarc services | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | WAO counts and active ports are substantial across B13H-A, 124 and 226. | 61¦58
61 | 59 | B61_Assessment | 66 | 8. OWNER RISKS | DATA | B61-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope building with multiple divisions. | 61¦59
61 | 60 | B61_Assessment | 67 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦60
61 | 61 | B61_Assessment | 68 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦61
61 | 62 | B61_Assessment | 69 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 61¦62
61 | 63 | B61_Assessment | 70 | 9. OPEN QUESTIONS | DATA | B61-Q1 | Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 61¦63
61 | 64 | B61_Assessment | 71 | 9. OPEN QUESTIONS | DATA | B61-Q2 | What active services and circuits are currently housed in Room 137/137A? | OIT / Contractor | Closed | 0 | 0 | Potential outage/cutover risk | 0 | 0 | 0 | 61¦64
61 | 65 | B61_Assessment | 72 | 9. OPEN QUESTIONS | DATA | B61-Q3 | Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? | Electrical / Designer | Closed | 0 | 0 | Electrical PMIS mapping risk | 0 | 0 | 0 | 61¦65
61 | 66 | B61_Assessment | 73 | 9. OPEN QUESTIONS | DATA | B61-Q4 | Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 61¦66
61 | 67 | B61_Assessment | 74 | 9. OPEN QUESTIONS | DATA | B61-Q5 | Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 61¦67
61 | 68 | B61_Assessment | 75 | 9. OPEN QUESTIONS | DATA | B61-Q6 | Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 61¦68
61 | 69 | B61_Assessment | 76 | 9. OPEN QUESTIONS | DATA | B61-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and temporary firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 61¦69
61 | 70 | B61_Assessment | 77 | 9. OPEN QUESTIONS | DATA | B61-Q8 | Which third-party inspections, commissioning forms and OIT acceptance records are required before turnover? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 61¦70
61 | 71 | B61_Assessment | 78 | 9. OPEN QUESTIONS | BLANK | B61-Q9 | How did this sheetget made? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 61¦71
61 | 72 | B61_Assessment | 79 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦72
61 | 73 | B61_Assessment | 80 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 61¦73
61 | 74 | B61_Assessment | 81 | 10. PHOTO LOG | DATA | B61-P001 | B13H-A | Existing Condition | Basement TR B13H-A walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B61-R1/B61-R2 | Closed | 0 | 61¦74
61 | 75 | B61_Assessment | 82 | 10. PHOTO LOG | DATA | B61-P002 | 124 | Existing Condition | First-level TR 124 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B61-R1/B61-R4 | Closed | 0 | 61¦75
61 | 76 | B61_Assessment | 83 | 10. PHOTO LOG | DATA | B61-P003 | 226 | Existing Condition | Second-level TR 226 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, cable tray and riser penetrations | 0 | Paul | 0 | B61-R1/B61-R4 | Closed | 0 | 61¦76
61 | 77 | B61_Assessment | 84 | 10. PHOTO LOG | DATA | B61-P004 | 137 / 137A | Existing Equipment | Existing server/demarc racks, APC UPS/PDU, Fujitsu equipment, patch panels, PACS/equipment racks and cable entries | 0 | Paul | 0 | B61-R3/B61-R7 | Closed | 0 | 61¦77
61 | 78 | B61_Assessment | 85 | 10. PHOTO LOG | DATA | B61-P005 | All TRs | HVAC | IU/CU-0-01, IU/CU-1-01, IU/CU-2-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B61-R4 | Closed | 0 | 61¦78
61 | 79 | B61_Assessment | 86 | 10. PHOTO LOG | DATA | B61-P006 | All TRs | Electrical | B61 telecom panels, PD panels, rack receptacles, UPS/PDU, breakers, SPDs, labels and grounding/bonding | 0 | Paul | 0 | B61-R5 | Closed | 0 | 61¦79
61 | 80 | B61_Assessment | 87 | 10. PHOTO LOG | DATA | B61-P007 | All | Cable Tray / Firestop | Basement/first/second cable tray route, supports, seismic bracing, penetrations and before/after firestopping | 0 | Paul | 0 | B61-R6 | Closed | 0 | 61¦80
61 | 81 | B61_Assessment | 88 | 10. PHOTO LOG | DATA | B61-P008 | All | Telecom / Security | Racks, Fiber LIU, Cat6A, patch panels, labels/test records, CCTV, PACS and existing equipment transfer work | 0 | Paul | 0 | B61-R7/B61-R8 | Closed | 0 | 61¦81
61 | 82 | B61_Assessment | 89 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61¦82
62 | 1 | B62_TR_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦1
62 | 2 | B62_TR_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 62¦2
62 | 3 | B62_TR_Assessment | 10 | 1. ROOM INVENTORY | DATA | 62 | B24A | Basement | Restroom / Storage | TR | 1 | 1 | Verify | B62 IFC | 0 | 62¦3
62 | 4 | B62_TR_Assessment | 11 | 1. ROOM INVENTORY | DATA | 62 | 125 | First | Medication Room | TR | 1 | 1 | Verify | B62 IFC | 0 | 62¦4
62 | 5 | B62_TR_Assessment | 12 | 1. ROOM INVENTORY | DATA | 62 | 225 | Second | Office | TR | 1 | 1 | Verify | B62 IFC | 0 | 62¦5
62 | 6 | B62_TR_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦6
62 | 7 | B62_TR_Assessment | 14 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦7
62 | 8 | B62_TR_Assessment | 15 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦8
62 | 9 | B62_TR_Assessment | 16 | 2. ROOM READINESS | HEADER | Room | Walls | Ceiling | Floor | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 62¦9
62 | 10 | B62_TR_Assessment | 17 | 2. ROOM READINESS | DATA | B24A | Verify | Verify | Verify | Verify | Verify | Verify | Pass | Verify | 0 | 62¦10
62 | 11 | B62_TR_Assessment | 18 | 2. ROOM READINESS | DATA | 125 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦11
62 | 12 | B62_TR_Assessment | 19 | 2. ROOM READINESS | DATA | 225 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦12
62 | 13 | B62_TR_Assessment | 20 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦13
62 | 14 | B62_TR_Assessment | 21 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦14
62 | 15 | B62_TR_Assessment | 22 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦15
62 | 16 | B62_TR_Assessment | 23 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 62¦16
62 | 17 | B62_TR_Assessment | 24 | 3. FIRE PROTECTION | DATA | B24A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦17
62 | 18 | B62_TR_Assessment | 25 | 3. FIRE PROTECTION | DATA | 125 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦18
62 | 19 | B62_TR_Assessment | 26 | 3. FIRE PROTECTION | DATA | 225 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦19
62 | 20 | B62_TR_Assessment | 27 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦20
62 | 21 | B62_TR_Assessment | 28 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦21
62 | 22 | B62_TR_Assessment | 29 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦22
62 | 23 | B62_TR_Assessment | 30 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls Tested | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 62¦23
62 | 24 | B62_TR_Assessment | 31 | 4. HVAC / COOLING | DATA | B24A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦24
62 | 25 | B62_TR_Assessment | 32 | 4. HVAC / COOLING | DATA | 125 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦25
62 | 26 | B62_TR_Assessment | 33 | 4. HVAC / COOLING | DATA | 225 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦26
62 | 27 | B62_TR_Assessment | 34 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦27
62 | 28 | B62_TR_Assessment | 35 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦28
62 | 29 | B62_TR_Assessment | 36 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦29
62 | 30 | B62_TR_Assessment | 37 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 62¦30
62 | 31 | B62_TR_Assessment | 38 | 5. ELECTRICAL / UPS | DATA | B24A | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦31
62 | 32 | B62_TR_Assessment | 39 | 5. ELECTRICAL / UPS | DATA | 125 | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦32
62 | 33 | B62_TR_Assessment | 40 | 5. ELECTRICAL / UPS | DATA | 225 | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦33
62 | 34 | B62_TR_Assessment | 41 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦34
62 | 35 | B62_TR_Assessment | 42 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦35
62 | 36 | B62_TR_Assessment | 43 | 6. TELECOM | SECTION | 6. TELECOM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦36
62 | 37 | B62_TR_Assessment | 44 | 6. TELECOM | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 62¦37
62 | 38 | B62_TR_Assessment | 45 | 6. TELECOM | DATA | B24A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦38
62 | 39 | B62_TR_Assessment | 46 | 6. TELECOM | DATA | 125 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦39
62 | 40 | B62_TR_Assessment | 47 | 6. TELECOM | DATA | 225 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 62¦40
62 | 41 | B62_TR_Assessment | 48 | 6. TELECOM | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦41
62 | 42 | B62_TR_Assessment | 49 | 6. TELECOM | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦42
62 | 43 | B62_TR_Assessment | 50 | 7. OWNER RISKS | SECTION | 7. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦43
62 | 44 | B62_TR_Assessment | 51 | 7. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 62¦44
62 | 45 | B62_TR_Assessment | 52 | 7. OWNER RISKS | DATA | B62-R1 | All | Cooling redundancy / emergency power not verified | High | Medium | 6 | Confirm power path for cooling, controls, condensate pump | GCC / VA | Closed | 0 | 62¦45
62 | 46 | B62_TR_Assessment | 53 | 7. OWNER RISKS | DATA | B62-R2 | All | Firestopping condition unknown | High | Medium | 6 | Survey penetrations and temporary/permanent firestop plan | GCC | Closed | 0 | 62¦46
62 | 47 | B62_TR_Assessment | 54 | 7. OWNER RISKS | DATA | B62-R3 | All | Existing room conditions undocumented | Medium | High | 6 | Create photo record before construction begins | GCC | Closed | 0 | 62¦47
62 | 48 | B62_TR_Assessment | 55 | 7. OWNER RISKS | DATA | B62-R4 | All | Condensate leak risk near IT equipment | High | Medium | 6 | Verify condensate routing and alarms | GCC / Contractor | Closed | 0 | 62¦48
62 | 49 | B62_TR_Assessment | 56 | 7. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦49
62 | 50 | B62_TR_Assessment | 57 | 7. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦50
62 | 51 | B62_TR_Assessment | 58 | 8. OPEN QUESTIONS | SECTION | 8. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦51
62 | 52 | B62_TR_Assessment | 59 | 8. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 62¦52
62 | 53 | B62_TR_Assessment | 60 | 8. OPEN QUESTIONS | DATA | B62-Q1 | Are cooling units emergency powered? | VA / Designer | Closed | 0 | 0 | Cannot confirm continuity of operations | 0 | 0 | 0 | 62¦53
62 | 54 | B62_TR_Assessment | 61 | 8. OPEN QUESTIONS | DATA | B62-Q2 | Are future rack loads included in HVAC sizing? | Designer | Closed | 0 | 0 | Cooling may be undersized after expansion | 0 | 0 | 0 | 62¦54
62 | 55 | B62_TR_Assessment | 62 | 8. OPEN QUESTIONS | DATA | B62-Q3 | Is extinguisher location identified within 75 feet? | Contractor / COR | Closed | 0 | 0 | Life safety / acceptance risk | 0 | 0 | 0 | 62¦55
62 | 56 | B62_TR_Assessment | 63 | 8. OPEN QUESTIONS | DATA | B62-Q4 | Are all penetrations fully documented and firestopped? | Contractor / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 62¦56
62 | 57 | B62_TR_Assessment | 64 | 8. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦57
62 | 58 | B62_TR_Assessment | 65 | 8. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦58
62 | 59 | B62_TR_Assessment | 66 | 9. PHOTO LOG | SECTION | 9. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦59
62 | 60 | B62_TR_Assessment | 67 | 9. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 62¦60
62 | 61 | B62_TR_Assessment | 68 | 9. PHOTO LOG | DATA | B62-P001 | B24A | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0 | 62¦61
62 | 62 | B62_TR_Assessment | 69 | 9. PHOTO LOG | DATA | B62-P002 | 125 | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0 | 62¦62
62 | 63 | B62_TR_Assessment | 70 | 9. PHOTO LOG | DATA | B62-P003 | 225 | Existing Condition | Existing room condition | 0 | Paul | 0 | 0 | Closed | 0 | 62¦63
62 | 64 | B62_TR_Assessment | 71 | 9. PHOTO LOG | DATA | B62-P004 | All | Firestop | Penetration/firestopping photo | 0 | Paul | 0 | B62-R2 | Closed | 0 | 62¦64
62 | 65 | B62_TR_Assessment | 72 | 9. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦65
62 | 66 | B62_TR_Assessment | 73 | 9. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦66
62 | 67 | B62_TR_Assessment | 74 | 10. OWNER READINESS SCORE | SECTION | 10. OWNER READINESS SCORE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦67
62 | 68 | B62_TR_Assessment | 75 | 10. OWNER READINESS SCORE | HEADER | Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes | 62¦68
62 | 69 | B62_TR_Assessment | 76 | 10. OWNER READINESS SCORE | DATA | B24A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0 | 62¦69
62 | 70 | B62_TR_Assessment | 77 | 10. OWNER READINESS SCORE | DATA | 125 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0 | 62¦70
62 | 71 | B62_TR_Assessment | 78 | 10. OWNER READINESS SCORE | DATA | 225 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0 | 62¦71
62 | 72 | B62_TR_Assessment | 79 | 10. OWNER READINESS SCORE | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦72
62 | 73 | B62_TR_Assessment | 80 | 10. OWNER READINESS SCORE | BLANK | 12. PAYMENT VERIFICATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62¦73
70 | 1 | B70_TR_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦1
70 | 2 | B70_TR_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 70¦2
70 | 3 | B70_TR_Assessment | 10 | 1. ROOM INVENTORY | DATA | 70 | B27 | Basement | Telecom Room / existing service area | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room B27; rack elevation references B-27 with 1 rack + future. | 70¦3
70 | 4 | B70_TR_Assessment | 11 | 1. ROOM INVENTORY | DATA | 70 | 125A | First | Telecom Room / existing or renovated space | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room 125A; rack elevation references 125-A with 1 rack + future. | 70¦4
70 | 5 | B70_TR_Assessment | 12 | 1. ROOM INVENTORY | DATA | 70 | 262A | Second | Telecom Room / existing or renovated space | TR | 1 | 1 | Verify | 70A/70T/70M/70FX | Shown as Telecom Room 262A; rack elevation references 262-A with 1 rack + future. | 70¦5
70 | 6 | B70_TR_Assessment | 13 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦6
70 | 7 | B70_TR_Assessment | 14 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦7
70 | 8 | B70_TR_Assessment | 15 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦8
70 | 9 | B70_TR_Assessment | 16 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 70¦9
70 | 10 | B70_TR_Assessment | 17 | 2. ROOM READINESS | DATA | B27 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦10
70 | 11 | B70_TR_Assessment | 18 | 2. ROOM READINESS | DATA | 125A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦11
70 | 12 | B70_TR_Assessment | 19 | 2. ROOM READINESS | DATA | 262A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦12
70 | 13 | B70_TR_Assessment | 20 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦13
70 | 14 | B70_TR_Assessment | 21 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦14
70 | 15 | B70_TR_Assessment | 22 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦15
70 | 16 | B70_TR_Assessment | 23 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 70¦16
70 | 17 | B70_TR_Assessment | 24 | 3. FIRE PROTECTION | DATA | B27 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦17
70 | 18 | B70_TR_Assessment | 25 | 3. FIRE PROTECTION | DATA | 125A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦18
70 | 19 | B70_TR_Assessment | 26 | 3. FIRE PROTECTION | DATA | 262A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦19
70 | 20 | B70_TR_Assessment | 27 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦20
70 | 21 | B70_TR_Assessment | 28 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦21
70 | 22 | B70_TR_Assessment | 29 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦22
70 | 23 | B70_TR_Assessment | 30 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 70¦23
70 | 24 | B70_TR_Assessment | 31 | 4. HVAC / COOLING | DATA | B27 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦24
70 | 25 | B70_TR_Assessment | 32 | 4. HVAC / COOLING | DATA | 125A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦25
70 | 26 | B70_TR_Assessment | 33 | 4. HVAC / COOLING | DATA | 262A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦26
70 | 27 | B70_TR_Assessment | 34 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦27
70 | 28 | B70_TR_Assessment | 35 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦28
70 | 29 | B70_TR_Assessment | 36 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦29
70 | 30 | B70_TR_Assessment | 37 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 70¦30
70 | 31 | B70_TR_Assessment | 38 | 5. ELECTRICAL / UPS | DATA | B27 | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦31
70 | 32 | B70_TR_Assessment | 39 | 5. ELECTRICAL / UPS | DATA | 125A | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦32
70 | 33 | B70_TR_Assessment | 40 | 5. ELECTRICAL / UPS | DATA | 262A | Verify | 5 kW | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦33
70 | 34 | B70_TR_Assessment | 41 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦34
70 | 35 | B70_TR_Assessment | 42 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦35
70 | 36 | B70_TR_Assessment | 43 | 6. TELECOM | SECTION | 6. TELECOM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦36
70 | 37 | B70_TR_Assessment | 44 | 6. TELECOM | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 70¦37
70 | 38 | B70_TR_Assessment | 45 | 6. TELECOM | DATA | B27 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦38
70 | 39 | B70_TR_Assessment | 46 | 6. TELECOM | DATA | 125A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦39
70 | 40 | B70_TR_Assessment | 47 | 6. TELECOM | DATA | 262A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 0 | 70¦40
70 | 41 | B70_TR_Assessment | 48 | 6. TELECOM | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦41
70 | 42 | B70_TR_Assessment | 49 | 6. TELECOM | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦42
70 | 43 | B70_TR_Assessment | 50 | 7. OWNER RISKS | SECTION | 7. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦43
70 | 44 | B70_TR_Assessment | 51 | 7. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 70¦44
70 | 45 | B70_TR_Assessment | 52 | 7. OWNER RISKS | DATA | B70-R1 | All | Cooling emergency power / continuity not verified | High | Medium | 6 | Confirm power path for cooling, controls, BACnet adapter, and condensate pump | GCC / VA | Closed | 0 | 70¦45
70 | 46 | B70_TR_Assessment | 53 | 7. OWNER RISKS | DATA | B70-R2 | All | 1-hour rated/smoke-rated TR envelope and penetrations not field verified | High | Medium | 6 | Survey walls, doors, sleeves, trays, firestop, and head-of-wall conditions | GCC | Closed | 0 | 70¦46
70 | 47 | B70_TR_Assessment | 54 | 7. OWNER RISKS | DATA | B70-R3 | B27 | Existing basement service conditions may constrain routing and access | Medium | High | 6 | Document existing utilities, clearances, and phasing around active systems | GCC | Closed | 0 | 70¦47
70 | 48 | B70_TR_Assessment | 55 | 7. OWNER RISKS | DATA | B70-R4 | All | Existing TR/service equipment transfer could affect active operations | High | Medium | 6 | Require phasing plan and maintain analog/low-voltage systems operational | GCC / Contractor | Closed | 0 | 70¦48
70 | 49 | B70_TR_Assessment | 56 | 7. OWNER RISKS | DATA | B70-R5 | All | Condensate leak risk near IT equipment | High | Medium | 6 | Verify condensate routing, insulation, pump power, and alarms | GCC / Contractor | Closed | 0 | 70¦49
70 | 50 | B70_TR_Assessment | 57 | 7. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦50
70 | 51 | B70_TR_Assessment | 58 | 7. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦51
70 | 52 | B70_TR_Assessment | 59 | 8. OPEN QUESTIONS | SECTION | 8. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦52
70 | 53 | B70_TR_Assessment | 60 | 8. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 70¦53
70 | 54 | B70_TR_Assessment | 61 | 8. OPEN QUESTIONS | DATA | B70-Q1 | Are cooling units and controls on emergency/backup power? | VA / Designer | Closed | 0 | 0 | Cannot confirm continuity of operations | 0 | 0 | 0 | 70¦54
70 | 55 | B70_TR_Assessment | 62 | 8. OPEN QUESTIONS | DATA | B70-Q2 | Are future rack loads included in HVAC sizing for B27, 125A, and 262A? | Designer | Closed | 0 | 0 | Cooling may be undersized after expansion | 0 | 0 | 0 | 70¦55
70 | 56 | B70_TR_Assessment | 63 | 8. OPEN QUESTIONS | DATA | B70-Q3 | Are extinguisher cabinet locations identified within 75 feet of each TR? | Contractor / COR | Closed | 0 | 0 | Acceptance / life safety risk | 0 | 0 | 0 | 70¦56
70 | 57 | B70_TR_Assessment | 64 | 8. OPEN QUESTIONS | DATA | B70-Q4 | Are all wall/floor penetrations and speed sleeves shown and firestopped? | Contractor / Designer | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 70¦57
70 | 58 | B70_TR_Assessment | 65 | 8. OPEN QUESTIONS | DATA | B70-Q5 | What phasing is required to keep existing low-voltage/analog systems operational? | Contractor / OIT | Closed | 0 | 0 | Potential communications interruption | 0 | 0 | 0 | 70¦58
70 | 59 | B70_TR_Assessment | 66 | 8. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦59
70 | 60 | B70_TR_Assessment | 67 | 8. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦60
70 | 61 | B70_TR_Assessment | 68 | 9. PHOTO LOG | SECTION | 9. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦61
70 | 62 | B70_TR_Assessment | 69 | 9. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 70¦62
70 | 63 | B70_TR_Assessment | 70 | 9. PHOTO LOG | DATA | B70-P001 | B27 | Existing Condition | Existing basement TR / utility condition | 0 | Paul | 0 | B70-R3 | Closed | 0 | 70¦63
70 | 64 | B70_TR_Assessment | 71 | 9. PHOTO LOG | DATA | B70-P002 | 125A | Existing Condition | Existing first-floor TR condition | 0 | Paul | 0 | 0 | Closed | 0 | 70¦64
70 | 65 | B70_TR_Assessment | 72 | 9. PHOTO LOG | DATA | B70-P003 | 262A | Existing Condition | Existing second-floor TR condition | 0 | Paul | 0 | 0 | Closed | 0 | 70¦65
70 | 66 | B70_TR_Assessment | 73 | 9. PHOTO LOG | DATA | B70-P004 | All | Firestop | Penetration/firestopping photo | 0 | Paul | 0 | B70-R2 | Closed | 0 | 70¦66
70 | 67 | B70_TR_Assessment | 74 | 9. PHOTO LOG | DATA | B70-P005 | All | HVAC | Cooling unit/condensate photo | 0 | Paul | 0 | B70-R1/B70-R5 | Closed | 0 | 70¦67
70 | 68 | B70_TR_Assessment | 75 | 9. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦68
70 | 69 | B70_TR_Assessment | 76 | 9. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦69
70 | 70 | B70_TR_Assessment | 77 | 10. OWNER READINESS SCORE | SECTION | 10. OWNER READINESS SCORE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦70
70 | 71 | B70_TR_Assessment | 78 | 10. OWNER READINESS SCORE | HEADER | Room | Room Readiness | Fire | HVAC | Electrical | Telecom | Documentation | Total Score | Readiness | Notes | 70¦71
70 | 72 | B70_TR_Assessment | 79 | 10. OWNER READINESS SCORE | DATA | B27 | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0 | 70¦72
70 | 73 | B70_TR_Assessment | 80 | 10. OWNER READINESS SCORE | DATA | 125A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0 | 70¦73
70 | 74 | B70_TR_Assessment | 81 | 10. OWNER READINESS SCORE | DATA | 262A | 50% | 50% | 50% | 50% | 50% | Verify | 50% | Partial / Yellow | 0 | 70¦74
70 | 75 | B70_TR_Assessment | 82 | 10. OWNER READINESS SCORE | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦75
70 | 76 | B70_TR_Assessment | 83 | 10. OWNER READINESS SCORE | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦76
70 | 77 | B70_TR_Assessment | 84 | 10. OWNER READINESS SCORE | DATA | SOURCE / DRAWING REVIEW NOTES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦77
70 | 78 | B70_TR_Assessment | 85 | 10. OWNER READINESS SCORE | DATA | Source package | 518-22-700.Bedford.EHRM.IFC.B70.20260316.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦78
70 | 79 | B70_TR_Assessment | 86 | 10. OWNER READINESS SCORE | DATA | TR locations identified | B27 basement, 125A first floor, 262A second floor based on architectural, fire protection, mechanical, and telecom drawing references. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦79
70 | 80 | B70_TR_Assessment | 87 | 10. OWNER READINESS SCORE | DATA | Fire protection basis | Building 70 is fully sprinklered. TRs require sprinkler modifications, fire alarm devices, extinguisher coverage within 75 feet, and firestopping at penetrations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦80
70 | 81 | B70_TR_Assessment | 88 | 10. OWNER READINESS SCORE | DATA | HVAC basis | New indoor units, condensate routing, thermostat, and BACnet adapter are noted for TR spaces; emergency power and operational continuity should be field verified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦81
70 | 82 | B70_TR_Assessment | 89 | 10. OWNER READINESS SCORE | DATA | Telecom basis | TR rack elevations show 1 rack plus future rack at B-27, 125-A, and 262-A with UPS/PDU/cable management/grounding requirements. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦82
70 | 83 | B70_TR_Assessment | 90 | 10. OWNER READINESS SCORE | BLANK | 0 | 12. PAYMENT VERIFICATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦83
70 | 84 | B70_TR_Assessment | 91 | 10. OWNER READINESS SCORE | DATA | Based on the Building 70 IFC review, the telecom scope is very similar to Building 62, but Building 70 appears to have three TRs (B27, 125A, and 262A) instead of a single room. The project introduces new racks, UPS equipment, dedicated cooling, fire alarm modifications, sprinkler modifications, grounding, cable management, and access control while maintaining hospital operations. | Telecom Room Build | Not Started | 0 | 0 | 🟡 | 0 | 0 | 0 | 0 | 70¦84
70 | 85 | B70_TR_Assessment | 92 | 10. OWNER READINESS SCORE | BLANK | 0 | Cooling Installation | Not Started | 1 | 0 | 🟢 | -1 | 0 | 0 | 0 | 70¦85
70 | 86 | B70_TR_Assessment | 93 | 10. OWNER READINESS SCORE | DATA | Building 70 – Telecom Room Infrastructure Scope | UPS Installation | Not Started | 1 | 0 | 🟢 | -1 | 0 | 0 | 0 | 70¦86
70 | 87 | B70_TR_Assessment | 94 | 10. OWNER READINESS SCORE | BLANK | 0 | Fiber Installation | Not Started | 1 | 0 | 🟢 | -1 | 0 | 0 | 0 | 70¦87
70 | 88 | B70_TR_Assessment | 95 | 10. OWNER READINESS SCORE | DATA | Existing Conditions Survey | Firestopping | Not Started | 1 | 0 | 🟢 | -1 | 0 | 0 | 0 | 70¦88
70 | 89 | B70_TR_Assessment | 96 | 10. OWNER READINESS SCORE | BLANK | 0 | Payment Confidence | 0 | 0.8 | 0 | Success: Recommended payment aligns with observed progress and evidence is documented. | 0 | 0 | 0 | 0 | 70¦89
70 | 90 | B70_TR_Assessment | 97 | 10. OWNER READINESS SCORE | DATA | Verify existing conditions of TR-B27, TR-125A, and TR-262A. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦90
70 | 91 | B70_TR_Assessment | 98 | 10. OWNER READINESS SCORE | DATA | Document existing racks, power, HVAC, fire protection, grounding, and pathway systems. | 13. OIT ACTIVATION READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦91
70 | 92 | B70_TR_Assessment | 99 | 10. OWNER READINESS SCORE | DATA | Photograph all existing conditions. | Requirement | Status | Verified | Complete | Score | Risk / Comments | Evidence Ref. | 0 | 0 | 70¦92
70 | 93 | B70_TR_Assessment | 100 | 10. OWNER READINESS SCORE | DATA | Verify existing active services and identify systems requiring uninterrupted operation. | Telecom Room Complete | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 70¦93
70 | 94 | B70_TR_Assessment | 101 | 10. OWNER READINESS SCORE | DATA | Verify room dimensions and equipment clearances. | Rack Installed | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 70¦94
70 | 95 | B70_TR_Assessment | 102 | 10. OWNER READINESS SCORE | BLANK | 0 | Fiber Tested | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 70¦95
70 | 96 | B70_TR_Assessment | 103 | 10. OWNER READINESS SCORE | DATA | Architectural | UPS Operational | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 70¦96
70 | 97 | B70_TR_Assessment | 104 | 10. OWNER READINESS SCORE | BLANK | 0 | Network Equipment Received | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 70¦97
70 | 98 | B70_TR_Assessment | 105 | 10. OWNER READINESS SCORE | DATA | Prepare rooms for new telecom infrastructure. | National OIT Approval | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 70¦98
70 | 99 | B70_TR_Assessment | 106 | 10. OWNER READINESS SCORE | DATA | Patch and repair walls, ceilings, and penetrations as required. | Local OIT Ready | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 70¦99
70 | 100 | B70_TR_Assessment | 107 | 10. OWNER READINESS SCORE | DATA | Maintain or restore all fire-rated assemblies. | Activation Scheduled | Not Started | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 70¦100
70 | 101 | B70_TR_Assessment | 108 | 10. OWNER READINESS SCORE | DATA | Verify door hardware, access control, and room security. | OIT Readiness | 0 |  | 0 | Success: Required OIT activation prerequisites are complete or formally coordinated. | 0 | 0 | 0 | 0 | 70¦101
70 | 102 | B70_TR_Assessment | 109 | 10. OWNER READINESS SCORE | DATA | Label rooms and equipment per VA standards. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦102
70 | 103 | B70_TR_Assessment | 110 | 10. OWNER READINESS SCORE | BLANK | 0 | 14. SUBMITTAL / MATERIAL VERIFICATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦103
70 | 104 | B70_TR_Assessment | 111 | 10. OWNER READINESS SCORE | DATA | Fire Protection | Spec / Item | Status | Approved | Installed | Match | QA Result | Comments / Evidence | 0 | 0 | 70¦104
70 | 105 | B70_TR_Assessment | 112 | 10. OWNER READINESS SCORE | BLANK | 0 | Telecom Equipment | Not Started | No | No | No | Pending | 0 | 0 | 0 | 70¦105
70 | 106 | B70_TR_Assessment | 113 | 10. OWNER READINESS SCORE | DATA | Verify sprinkler coverage within each TR. | Cable Tray | Not Started | No | No | No | Pending | 0 | 0 | 0 | 70¦106
70 | 107 | B70_TR_Assessment | 114 | 10. OWNER READINESS SCORE | DATA | Reconfigure sprinkler piping and heads where required. | Firestop System | Not Started | No | No | No | Pending | 0 | 0 | 0 | 70¦107
70 | 108 | B70_TR_Assessment | 115 | 10. OWNER READINESS SCORE | DATA | Verify no obstructions to sprinkler discharge. | HVAC Equipment | Not Started | No | No | No | Pending | 0 | 0 | 0 | 70¦108
70 | 109 | B70_TR_Assessment | 116 | 10. OWNER READINESS SCORE | DATA | Provide fire extinguisher cabinet and clean-agent or CO₂ extinguisher within 75 feet of each TR. | Electrical Equipment | Not Started | No | No | No | Pending | 0 | 0 | 0 | 70¦109
70 | 110 | B70_TR_Assessment | 117 | 10. OWNER READINESS SCORE | DATA | Firestop all penetrations through rated assemblies. | Inspection Compliance | 0 | 0 | 0 | Success: Installed materials match approved submittals and deficiencies are documented. | 0 | 0 | 0 | 0 | 70¦110
70 | 111 | B70_TR_Assessment | 118 | 10. OWNER READINESS SCORE | DATA | Verify compliance with NFPA 13 and VA Fire Protection Design Manual requirements. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦111
70 | 112 | B70_TR_Assessment | 119 | 10. OWNER READINESS SCORE | BLANK | 0 | 15. PRODUCTIVITY OBSERVATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦112
70 | 113 | B70_TR_Assessment | 120 | 10. OWNER READINESS SCORE | DATA | Fire Alarm | Trade | Status | Planned | Actual | Crew | Productivity | Work Observed / Delay Cause | 0 | 0 | 70¦113
70 | 114 | B70_TR_Assessment | 121 | 10. OWNER READINESS SCORE | BLANK | 0 | Electrical | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0 | 70¦114
70 | 115 | B70_TR_Assessment | 122 | 10. OWNER READINESS SCORE | DATA | Verify smoke detection coverage. | Telecom | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0 | 70¦115
70 | 116 | B70_TR_Assessment | 123 | 10. OWNER READINESS SCORE | DATA | Verify horn/strobe coverage. | Mechanical | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0 | 70¦116
70 | 117 | B70_TR_Assessment | 124 | 10. OWNER READINESS SCORE | DATA | Coordinate relocation or addition of devices as required. | Firestop | Not Started | 0 | 0 | 0 |  | 0 | 0 | 0 | 70¦117
70 | 118 | B70_TR_Assessment | 125 | 10. OWNER READINESS SCORE | DATA | Verify monitoring and reporting through existing fire alarm systems. | Contractor Performance | 0 | 0 | 0 | Success: Actual production is on or above baseline, or delay cause is documented. | 0 | 0 | 0 | 0 | 70¦118
70 | 119 | B70_TR_Assessment | 126 | 10. OWNER READINESS SCORE | DATA | Test and document final operation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦119
70 | 120 | B70_TR_Assessment | 127 | 10. OWNER READINESS SCORE | BLANK | 0 | 16. OWNER ACCEPTANCE READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦120
70 | 121 | B70_TR_Assessment | 128 | 10. OWNER READINESS SCORE | DATA | Mechanical / HVAC | Requirement | Status | Required | Complete | Score | Comments | Evidence Ref. | 0 | 0 | 70¦121
70 | 122 | B70_TR_Assessment | 129 | 10. OWNER READINESS SCORE | BLANK | 0 | Construction Complete | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0 | 70¦122
70 | 123 | B70_TR_Assessment | 130 | 10. OWNER READINESS SCORE | DATA | Verify dedicated cooling units serving each telecom room. | QA/QC Complete | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0 | 70¦123
70 | 124 | B70_TR_Assessment | 131 | 10. OWNER READINESS SCORE | DATA | Verify thermostat installation. | Deficiencies Closed | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0 | 70¦124
70 | 125 | B70_TR_Assessment | 132 | 10. OWNER READINESS SCORE | DATA | Verify BACnet integration and controls. | OIT Ready | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0 | 70¦125
70 | 126 | B70_TR_Assessment | 133 | 10. OWNER READINESS SCORE | DATA | Verify condensate routing and drainage. | Documentation Complete | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0 | 70¦126
70 | 127 | B70_TR_Assessment | 134 | 10. OWNER READINESS SCORE | DATA | Verify emergency power requirements for cooling equipment. | Recommended for Acceptance | Not Started | Yes | No | 0 | 0 | 0 | 0 | 0 | 70¦127
70 | 128 | B70_TR_Assessment | 135 | 10. OWNER READINESS SCORE | DATA | Verify continuous cooling capability during hospital operations. | Acceptance Readiness | 0 | 0 | 0 | Success: Building is ready for turnover when all required gates are complete. | 0 | 0 | 0 | 0 | 70¦128
70 | 129 | B70_TR_Assessment | 136 | 10. OWNER READINESS SCORE | DATA | Perform startup and commissioning. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦129
70 | 130 | B70_TR_Assessment | 137 | 10. OWNER READINESS SCORE | BLANK | 0 | 16. SOURCE / DRAWING REVIEW NOTES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦130
70 | 131 | B70_TR_Assessment | 138 | 10. OWNER READINESS SCORE | DATA | Electrical | Source Package | 518-22-700.Bedford.EHRM.IFC.B61.20260316.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦131
70 | 132 | B70_TR_Assessment | 139 | 10. OWNER READINESS SCORE | BLANK | 0 | Drawing Index | 70-sheet Building 61 IFC package includes general, hazardous abatement, architectural, interiors, fire protection, plumbing, mechanical, electrical, telecommunications, schedules/rack elevations, server/demarc rack elevations and photo references. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦132
70 | 133 | B70_TR_Assessment | 140 | 10. OWNER READINESS SCORE | DATA | Verify new electrical distribution serving telecom equipment. | Architectural / Hazardous Basis | Drawing index includes 61H-101 first-level and 61H-102 second-level hazardous material abatement plans plus architectural enlarged views 61A-400/401 for basement, first and second levels. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦133
70 | 134 | B70_TR_Assessment | 141 | 10. OWNER READINESS SCORE | DATA | Verify dedicated panel assignments. | Mechanical Basis | 61M sheets identify dedicated split-system cooling for telecom rooms using IU-0-01/IU-1-01/IU-2-01 and CU-0-01/CU-1-01/CU-2-01, with BACnet adapter mounted adjacent to unit in telecom room; verify emergency power, condensate and alarms. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦134
70 | 135 | B70_TR_Assessment | 142 | 10. OWNER READINESS SCORE | DATA | Verify UPS installation and ratings. | Electrical Basis | 61E-401/402/601/701/702/703 identify B61 telecom panelboards and PD panels including B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, rack receptacles, SPDs, UPS/PDU and cooling equipment circuits. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦135
70 | 136 | B70_TR_Assessment | 143 | 10. OWNER READINESS SCORE | DATA | Verify rack power distribution units. | Telecom Basis | 61T-701/702 identify B13H-A: 88 WAO, 74 active, 129 scheduled, 142 with allowance; 226: 109 WAO, 126 active, 156 scheduled, 172 with allowance. Cable tray schedule totals 1,966 ft: basement 890 ft, first 499 ft, second 578 ft. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦136
70 | 137 | B70_TR_Assessment | 144 | 10. OWNER READINESS SCORE | DATA | Verify emergency power source. | Server / Demarc Basis | 61T-402/606/607 and 61R-900 reference Room 137/137A existing telecom/server/demarc racks, APC UPS/PDU, Fujitsu equipment, wall-mounted patch panels and active systems requiring protection-in-place and cutover coordination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦137
70 | 138 | B70_TR_Assessment | 145 | 10. OWNER READINESS SCORE | DATA | Verify grounding and bonding requirements. | Operational Basis | Cover/general notes require existing ports replaced, conduit reuse where possible, 10% data-port allowance, coordination drawings, third-party inspections, commissioning/recommissioning, VA acceptance before active connections, and shutdowns limited one at a time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦138
70 | 139 | B70_TR_Assessment | 146 | 10. OWNER READINESS SCORE | DATA | Verify circuit identification and labeling. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦139
70 | 140 | B70_TR_Assessment | 147 | 10. OWNER READINESS SCORE | BLANK | 0 | PILOT ACCEPTANCE GATE — COPY / PASTE BLOCK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦140
70 | 141 | B70_TR_Assessment | 148 | 10. OWNER READINESS SCORE | DATA | Telecommunications | Purpose | Use this as the objective completion gate for pilot turnover. A building/pilot stays YELLOW until all eight gates are complete. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦141
70 | 142 | B70_TR_Assessment | 149 | 10. OWNER READINESS SCORE | BLANK | 0 | How to use | Copy A5:H18 into the applicable Building Assessment sheet. Status cells are intended to be Yes / No / N/A, with evidence links in the Evidence column. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦142
70 | 143 | B70_TR_Assessment | 150 | 10. OWNER READINESS SCORE | DATA | Install and/or verify new equipment racks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦143
70 | 144 | B70_TR_Assessment | 151 | 10. OWNER READINESS SCORE | DATA | Install vertical and horizontal cable management. | Requirement | Status | Evidence / Link | Date | Owner | QC Notes | Gate Met? | Dashboard Signal | 0 | 70¦144
70 | 145 | B70_TR_Assessment | 152 | 10. OWNER READINESS SCORE | DATA | Install grounding busbars. | Approved Submittals | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0 | 70¦145
70 | 146 | B70_TR_Assessment | 153 | 10. OWNER READINESS SCORE | DATA | Install fiber termination shelves. | ICRA / PCRA | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0 | 70¦146
70 | 147 | B70_TR_Assessment | 154 | 10. OWNER READINESS SCORE | DATA | Install patch panels. | QA/QC Reports | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0 | 70¦147
70 | 148 | B70_TR_Assessment | 155 | 10. OWNER READINESS SCORE | DATA | Verify Cat6A and fiber terminations. | Firestopping | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0 | 70¦148
70 | 149 | B70_TR_Assessment | 156 | 10. OWNER READINESS SCORE | DATA | Verify cable labeling. | Cable Tests | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0 | 70¦149
70 | 150 | B70_TR_Assessment | 157 | 10. OWNER READINESS SCORE | DATA | Test and certify all copper and fiber cabling. | OIT Acceptance | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0 | 70¦150
70 | 151 | B70_TR_Assessment | 158 | 10. OWNER READINESS SCORE | DATA | Verify compliance with OIT standards. | Photos | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0 | 70¦151
70 | 152 | B70_TR_Assessment | 159 | 10. OWNER READINESS SCORE | BLANK | 0 | Zero Critical Punch Items | No | 0 | 0 | 0 | 0 | 🟡 | 0 | 0 | 70¦152
70 | 153 | B70_TR_Assessment | 160 | 10. OWNER READINESS SCORE | DATA | Security | Requirement | What it Means | 0 | 0 | Verification | 0 | 0 | 0 | 0 | 70¦153
70 | 154 | B70_TR_Assessment | 161 | 10. OWNER READINESS SCORE | BLANK | 0 | Approved Submittals | Every material and piece of equipment installed in the pilot area has been reviewed and approved through the submittal process. Nothing unapproved was installed. | 0 | 0 | Verify approved submittals exist for all installed systems and that field installations match the approved documents. | 0 | 0 | 0 | 0 | 70¦154
70 | 155 | B70_TR_Assessment | 162 | 10. OWNER READINESS SCORE | DATA | Verify PACS access control for all TR doors. | ICRA / PCRA | The required Infection Control Risk Assessment and Pre-Construction Risk Assessment were approved, implemented, and maintained throughout construction. | 0 | 0 | Confirm approved plans, barrier inspections, negative air documentation (if applicable), housekeeping, and final removal procedures. | 0 | 0 | 0 | 0 | 70¦155
70 | 156 | B70_TR_Assessment | 163 | 10. OWNER READINESS SCORE | DATA | Verify card reader operation. | QA/QC Reports | Contractor quality inspections have been completed and documented. | 0 | 0 | Review QC reports, inspection checklists, deficiency logs, corrective actions, and daily QC documentation. | 0 | 0 | 0 | 0 | 70¦156
70 | 157 | B70_TR_Assessment | 164 | 10. OWNER READINESS SCORE | DATA | Verify door position monitoring. | Firestopping | Every penetration through rated walls, floors, and ceilings has been properly firestopped with approved systems. | 0 | 0 | Inspect penetrations, verify UL systems, labels, installation quality, and documentation/photos. | 0 | 0 | 0 | 0 | 70¦157
70 | 158 | B70_TR_Assessment | 165 | 10. OWNER READINESS SCORE | DATA | Verify camera coverage where required. | Cable Tests | All network, fiber, and communication cabling has passed required testing. | 0 | 0 | Verify copper certification reports, fiber OTDR/power meter results, labeling, and test documentation. | 0 | 0 | 0 | 0 | 70¦158
70 | 159 | B70_TR_Assessment | 166 | 10. OWNER READINESS SCORE | DATA | Verify integration with existing VA security systems. | OIT Acceptance | VA Office of Information & Technology has inspected and accepted the installed IT infrastructure. | 0 | 0 | Obtain written acceptance or signoff from OIT confirming systems are operational and acceptable. | 0 | 0 | 0 | 0 | 70¦159
70 | 160 | B70_TR_Assessment | 167 | 10. OWNER READINESS SCORE | BLANK | 0 | Photos | Construction has been photographically documented. | 0 | 0 | Ensure pre-construction, rough-in, above-ceiling, concealed work, and final condition photographs are complete and organized. | 0 | 0 | 0 | 0 | 70¦160
70 | 161 | B70_TR_Assessment | 168 | 10. OWNER READINESS SCORE | DATA | Operational Risk Review | Zero Critical Punch Items | No life safety, code, operational, or mission-critical deficiencies remain. Minor cosmetic items may remain only if allowed by contract. | 0 | 0 | Walk the space and confirm all critical deficiencies have been corrected prior to turnover. | 0 | 0 | 0 | 0 | 70¦161
70 | 162 | B70_TR_Assessment | 169 | 10. OWNER READINESS SCORE | BLANK | 0 | Acceptance Gate Result | 🟡 NOT COMPLETE — ACCEPTANCE GATES OPEN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦162
70 | 163 | B70_TR_Assessment | 170 | 10. OWNER READINESS SCORE | DATA | Identify systems requiring uninterrupted operation. | Open Gate Count | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦163
70 | 164 | B70_TR_Assessment | 171 | 10. OWNER READINESS SCORE | DATA | Develop cutover strategy. | Gate Completion | 0 / 8 Complete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦164
70 | 165 | B70_TR_Assessment | 172 | 10. OWNER READINESS SCORE | DATA | Review outage requirements with VA OIT. | Command Center Rule | Tile remains YELLOW until B15 returns "🟢 PILOT COMPLETE / ACCEPTANCE READY"; then tile may turn GREEN. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦165
70 | 166 | B70_TR_Assessment | 173 | 10. OWNER READINESS SCORE | DATA | Review shutdown requirements with facilities staff. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦166
70 | 167 | B70_TR_Assessment | 174 | 10. OWNER READINESS SCORE | DATA | Verify no active services are removed before migration. | Suggested Building Tile Logic | Example only: =IF(COUNTIF(<building_gate_status_range>,"No")=0,"GREEN","YELLOW") | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦167
70 | 168 | B70_TR_Assessment | 175 | 10. OWNER READINESS SCORE | BLANK | 0 | 17. OWNER DECISION SUMMARY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦168
70 | 169 | B70_TR_Assessment | 176 | 10. OWNER READINESS SCORE | DATA | Commissioning & Acceptance | Recommended Payment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦169
70 | 170 | B70_TR_Assessment | 177 | 10. OWNER READINESS SCORE | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦170
70 | 171 | B70_TR_Assessment | 178 | 10. OWNER READINESS SCORE | DATA | HVAC commissioning. | ☐ Full | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦171
70 | 172 | B70_TR_Assessment | 179 | 10. OWNER READINESS SCORE | DATA | Electrical commissioning. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦172
70 | 173 | B70_TR_Assessment | 180 | 10. OWNER READINESS SCORE | DATA | Telecom testing and certification. | ☐ Partial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦173
70 | 174 | B70_TR_Assessment | 181 | 10. OWNER READINESS SCORE | DATA | Fire alarm testing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦174
70 | 175 | B70_TR_Assessment | 182 | 10. OWNER READINESS SCORE | DATA | Fire protection testing. | ☐ Withhold | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦175
70 | 176 | B70_TR_Assessment | 183 | 10. OWNER READINESS SCORE | DATA | Security testing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦176
70 | 177 | B70_TR_Assessment | 184 | 10. OWNER READINESS SCORE | DATA | Final owner acceptance walkthrough. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦177
70 | 178 | B70_TR_Assessment | 185 | 10. OWNER READINESS SCORE | DATA | Turnover documentation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦178
70 | 179 | B70_TR_Assessment | 186 | 10. OWNER READINESS SCORE | BLANK | 0 | 18. Construction Status | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦179
70 | 180 | B70_TR_Assessment | 187 | 10. OWNER READINESS SCORE | DATA | Owner Risks Identified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦180
70 | 181 | B70_TR_Assessment | 188 | 10. OWNER READINESS SCORE | BLANK | 0 | ☐ On Schedule | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦181
70 | 182 | B70_TR_Assessment | 189 | 10. OWNER READINESS SCORE | DATA | High Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦182
70 | 183 | B70_TR_Assessment | 190 | 10. OWNER READINESS SCORE | BLANK | 0 | ☐ Behind Schedule | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70¦183
78 | 1 | B78_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦1
78 | 2 | B78_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 78¦2
78 | 3 | B78_Assessment | 10 | 1. ROOM INVENTORY | DATA | 78/78A | B30 | Basement | Basement telecom area / existing rack transfer | Telecom Room | 2 | 1 | Verify | 78_78AA-400 / 78_78AE-401 / 78_78AT-100 / 78_78AT-604 / 78_78AT-701 | Basement primary TR. Schedule identifies RM B30 with 210 WAO total, 23 active ports, 311 scheduled ports, 342 total ports with 10% allowance. Rack IDs include TR01-B30-1 and TR01-B30-2. | 78¦3
78 | 4 | B78_Assessment | 11 | 1. ROOM INVENTORY | DATA | 78/78A | B35 | Basement | Basement telecom area / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AT-100 / 78_78AT-605 / 78_78AT-702 | Basement TR/closet. Schedule identifies RM B35 with 53 WAO total, 23 active ports, 64 scheduled ports, 70 total ports with 10% allowance. Verify relationship to existing basement telecom room 15E photo reference. | 78¦4
78 | 5 | B78_Assessment | 12 | 1. ROOM INVENTORY | DATA | 78/78A | 1232 | First | First-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-401 / 78_78AE-402 / 78_78AT-101 / 78_78AT-606 / 78_78AT-702/703 | First-level TR. Schedule identifies RM 1232 with 301 WAO total, 388 active ports, 404 scheduled ports, 444 total ports with 10% allowance. Existing photo references show first-level existing telecom room 1234; verify room-name mapping. | 78¦5
78 | 6 | B78_Assessment | 13 | 1. ROOM INVENTORY | DATA | 78/78A | 227A | Second | Second-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-401 / 78_78AE-402 / 78_78AT-102 / 78_78AT-606 / 78_78AT-703/704 | Second-level TR. Schedule identifies RM 227A with 256 WAO total, 153 active ports, 348 scheduled ports, 383 total ports with 10% allowance. Existing photo references show second-level existing telecom room 1234; verify field room ID. | 78¦6
78 | 7 | B78_Assessment | 14 | 1. ROOM INVENTORY | DATA | 78/78A | 342 | Third | Third-level telecom room / existing rack transfer | Telecom Room | 2 | 1 | Verify | 78_78AA-402 / 78_78AE-403 / 78_78AT-103 / 78_78AT-607 / 78_78AT-704 | Third-level TR. Schedule identifies RM 342 with 158 WAO total, 163 active ports, 289 scheduled ports, 318 total ports with 10% allowance. Rack IDs include TR01-342-1 and TR01-342-2. | 78¦7
78 | 8 | B78_Assessment | 15 | 1. ROOM INVENTORY | DATA | 78/78A | 401 | Fourth | Fourth-level telecom room / existing rack transfer | Telecom Room | 1 | 1 | Verify | 78_78AA-402 / 78_78AE-404 / 78_78AT-104 / 78_78AT-607 / 78_78AT-705 | Fourth-level TR. Schedule identifies RM 401 with 89 WAO total, 65 active ports, 123 scheduled ports, 135 total ports with 10% allowance. | 78¦8
78 | 9 | B78_Assessment | 16 | 1. ROOM INVENTORY | DATA | 78/78A | 15E / 1234 / 353 / 308A / 408A | Existing levels | Existing telecom rooms / photo references | Existing telecom transition points | 5 | 0 | Verify | 78_78AR-900 / 901 / 902 / 903 | Photo references identify existing telecom rooms: basement 15E, first-level 1234, second-level 1234, third-level 353, fourth-level 308A and 408A. Protect active equipment and verify transfer/abandonment scope. | 78¦9
78 | 10 | B78_Assessment | 17 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦10
78 | 11 | B78_Assessment | 18 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦11
78 | 12 | B78_Assessment | 19 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 78¦12
78 | 13 | B78_Assessment | 20 | 2. ROOM READINESS | DATA | B30 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR; verify rated enclosure/open-to-deck conditions, door/PACS, future rack space, wall backing, ladder rack, and basement pathway entry points. | 78¦13
78 | 14 | B78_Assessment | 21 | 2. ROOM READINESS | DATA | B35 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Basement TR/closet; verify existing conditions, rack transfer, floor/wall conditions, clearance, pathway and firestop scope. | 78¦14
78 | 15 | B78_Assessment | 22 | 2. ROOM READINESS | DATA | 1232 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify rated construction, door hardware/access, ceiling/deck, rack/future rack clearance, wall backing and pathway entries. | 78¦15
78 | 16 | B78_Assessment | 23 | 2. ROOM READINESS | DATA | 227A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Second-level TR; verify rated construction, door hardware/access, rack/future rack clearance and vertical riser/firestop conditions. | 78¦16
78 | 17 | B78_Assessment | 24 | 2. ROOM READINESS | DATA | 342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Third-level TR; verify rack/future rack clearances, access control, firestopping and pathway routes. | 78¦17
78 | 18 | B78_Assessment | 25 | 2. ROOM READINESS | DATA | 401 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fourth-level TR; verify rack/future rack clearances, access control, firestopping and pathway routes. | 78¦18
78 | 19 | B78_Assessment | 26 | 2. ROOM READINESS | DATA | Existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom rooms must be field verified for active equipment, protection-in-place and final abandonment/transfer condition. | 78¦19
78 | 20 | B78_Assessment | 27 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦20
78 | 21 | B78_Assessment | 28 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦21
78 | 22 | B78_Assessment | 29 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 78¦22
78 | 23 | B78_Assessment | 30 | 3. FIRE PROTECTION | DATA | B30 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, and rated penetrations. | 78¦23
78 | 24 | B78_Assessment | 31 | 3. FIRE PROTECTION | DATA | B35 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify FP/FA modifications, FEC location, temporary firestopping and final UL systems. | 78¦24
78 | 25 | B78_Assessment | 32 | 3. FIRE PROTECTION | DATA | 1232 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify first-level TR sprinkler/FA work, FEC location and cable tray penetrations. | 78¦25
78 | 26 | B78_Assessment | 33 | 3. FIRE PROTECTION | DATA | 227A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR sprinkler/FA work, FEC location, vertical riser penetrations and firestopping. | 78¦26
78 | 27 | B78_Assessment | 34 | 3. FIRE PROTECTION | DATA | 342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify third-level TR fire protection/fire alarm coordination and firestop work. | 78¦27
78 | 28 | B78_Assessment | 35 | 3. FIRE PROTECTION | DATA | 401 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify fourth-level TR fire protection/fire alarm coordination and firestop work. | 78¦28
78 | 29 | B78_Assessment | 36 | 3. FIRE PROTECTION | DATA | Existing rooms | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Verify existing rooms remain protected during cutover and no unsealed penetrations remain. | 78¦29
78 | 30 | B78_Assessment | 37 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦30
78 | 31 | B78_Assessment | 38 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦31
78 | 32 | B78_Assessment | 39 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 78¦32
78 | 33 | B78_Assessment | 40 | 4. HVAC / COOLING | DATA | B30 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical sheets included for basement. Verify dedicated cooling equipment, capacity, condensate, emergency source, controls/BACnet and high-temperature alarm. | 78¦33
78 | 34 | B78_Assessment | 41 | 4. HVAC / COOLING | DATA | B35 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify dedicated cooling and relationship to B30/B35 telecom buildout. | 78¦34
78 | 35 | B78_Assessment | 42 | 4. HVAC / COOLING | DATA | 1232 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify first-level TR cooling, controls, emergency power and alarm tie-in. | 78¦35
78 | 36 | B78_Assessment | 43 | 4. HVAC / COOLING | DATA | 227A | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR cooling, condensate route and 24/7 operation. | 78¦36
78 | 37 | B78_Assessment | 44 | 4. HVAC / COOLING | DATA | 342 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify third-level TR cooling and control/alarm integration. | 78¦37
78 | 38 | B78_Assessment | 45 | 4. HVAC / COOLING | DATA | 401 | Dedicated TR cooling shown / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify fourth-level TR cooling and control/alarm integration. | 78¦38
78 | 39 | B78_Assessment | 46 | 4. HVAC / COOLING | DATA | Existing rooms | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom rooms likely have legacy cooling dependencies. Verify active equipment temperature and any protect-in-place cooling requirements. | 78¦39
78 | 40 | B78_Assessment | 47 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦40
78 | 41 | B78_Assessment | 48 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦41
78 | 42 | B78_Assessment | 49 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 78¦42
78 | 43 | B78_Assessment | 50 | 5. ELECTRICAL / UPS | DATA | B30 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TRB30 panels / verify | Verify | Verify | Verify | Rack elevations identify new rack UPS/PDU and future rack. Verify panelboard/source, SPD, rack receptacles, PDU feeds, labels, load measurement and LOTO. | 78¦43
78 | 44 | B78_Assessment | 51 | 5. ELECTRICAL / UPS | DATA | B35 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TRB35 panels / verify | Verify | Verify | Verify | Verify rack UPS/PDU source, spare/future rack provisions and grounding/bonding. | 78¦44
78 | 45 | B78_Assessment | 52 | 5. ELECTRICAL / UPS | DATA | 1232 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TR1232 panels / verify | Verify | Verify | Verify | Verify first-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. | 78¦45
78 | 46 | B78_Assessment | 53 | 5. ELECTRICAL / UPS | DATA | 227A | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TR227A panels / verify | Verify | Verify | Verify | Verify second-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. | 78¦46
78 | 47 | B78_Assessment | 54 | 5. ELECTRICAL / UPS | DATA | 342 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TR342 panels / verify | Verify | Verify | Verify | Verify third-level rack receptacles for two racks, UPS/PDU, panel sources and labels. | 78¦47
78 | 48 | B78_Assessment | 55 | 5. ELECTRICAL / UPS | DATA | 401 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B78-TR401 panels / verify | Verify | Verify | Verify | Verify fourth-level rack receptacles, UPS/PDU, panel sources and labels. | 78¦48
78 | 49 | B78_Assessment | 56 | 5. ELECTRICAL / UPS | DATA | Existing rooms | Existing / Verify | Existing UPS / PDU | Existing / Verify | Verify | Existing / verify | Verify | Verify | Verify | Existing rack elevations show wall-mounted racks/2-post racks, existing UPS/PDU and demarc/fiber equipment. Confirm active power and transfer needs. | 78¦49
78 | 50 | B78_Assessment | 57 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦50
78 | 51 | B78_Assessment | 58 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦51
78 | 52 | B78_Assessment | 59 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 78¦52
78 | 53 | B78_Assessment | 60 | 6. TELECOMMUNICATIONS | DATA | B30 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-701: 210 WAO total, 23 active ports, 311 scheduled ports, 342 with allowance; rack IDs TR01-B30-1/-2. Basement cable tray total 1,702 ft. | 78¦53
78 | 54 | B78_Assessment | 61 | 6. TELECOMMUNICATIONS | DATA | B35 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-702: 53 WAO total, 23 active ports, 64 scheduled ports, 70 with allowance. Confirm rack ID/room relation and active services. | 78¦54
78 | 55 | B78_Assessment | 62 | 6. TELECOMMUNICATIONS | DATA | 1232 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-702/703: 301 WAO total, 388 active ports, 404 scheduled ports, 444 with allowance. Large active port count; high cutover risk. | 78¦55
78 | 56 | B78_Assessment | 63 | 6. TELECOMMUNICATIONS | DATA | 227A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-703/704: 256 WAO total, 153 active ports, 348 scheduled ports, 383 with allowance. Verify second-level test records and riser labels. | 78¦56
78 | 57 | B78_Assessment | 64 | 6. TELECOMMUNICATIONS | DATA | 342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-704: 158 WAO total, 163 active ports, 289 scheduled ports, 318 with allowance. Rack IDs TR01-342-1/-2. | 78¦57
78 | 58 | B78_Assessment | 65 | 6. TELECOMMUNICATIONS | DATA | 401 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 78_78AT-705: 89 WAO total, 65 active ports, 123 scheduled ports, 135 with allowance. | 78¦58
78 | 59 | B78_Assessment | 66 | 6. TELECOMMUNICATIONS | DATA | Existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Photo references identify existing telecom rooms 15E, 1234, 353, 308A and 408A; verify all active services and transfer plan. | 78¦59
78 | 60 | B78_Assessment | 67 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦60
78 | 61 | B78_Assessment | 68 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦61
78 | 62 | B78_Assessment | 69 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 78¦62
78 | 63 | B78_Assessment | 70 | 7. SECURITY / PACS / CCTV | DATA | B30 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | TR scope includes wall-mounted CCTV cameras and PACS for TR doors. Verify CR/RX/DC/ES/MD, controller and VMS integration. | 78¦63
78 | 64 | B78_Assessment | 71 | 7. SECURITY / PACS / CCTV | DATA | B35 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify PACS/CCTV integration and door hardware coordination. | 78¦64
78 | 65 | B78_Assessment | 72 | 7. SECURITY / PACS / CCTV | DATA | 1232 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify first-level TR PACS/CCTV and VMS integration. | 78¦65
78 | 66 | B78_Assessment | 73 | 7. SECURITY / PACS / CCTV | DATA | 227A | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify second-level TR PACS/CCTV and VMS integration. | 78¦66
78 | 67 | B78_Assessment | 74 | 7. SECURITY / PACS / CCTV | DATA | 342 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify third-level TR PACS/CCTV and VMS integration. | 78¦67
78 | 68 | B78_Assessment | 75 | 7. SECURITY / PACS / CCTV | DATA | 401 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify fourth-level TR PACS/CCTV and VMS integration. | 78¦68
78 | 69 | B78_Assessment | 76 | 7. SECURITY / PACS / CCTV | DATA | Existing rooms | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify existing PACS/security devices are protected-in-place or recabled without VMS/PACS disruption. | 78¦69
78 | 70 | B78_Assessment | 77 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦70
78 | 71 | B78_Assessment | 78 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦71
78 | 72 | B78_Assessment | 79 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 78¦72
78 | 73 | B78_Assessment | 80 | 8. OWNER RISKS | DATA | B78-R1 | All | Existing conditions and active equipment across six TRs and existing telecom rooms not field verified | High | Medium | 6 | Perform detailed room-by-room existing condition survey with photos and active-service inventory | GCC / Contractor | Closed | B78/78A has six major TR areas and several existing transition rooms. | 78¦73
78 | 74 | B78_Assessment | 81 | 8. OWNER RISKS | DATA | B78-R2 | Basement / Third | Hazardous material abatement plans exist for basement and third level | High | Medium | 6 | Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or MEP installation | GC / IH / COR | Closed | Drawing index includes 78_78AH-100 and 78_78AH-103. | 78¦74
78 | 75 | B78_Assessment | 82 | 8. OWNER RISKS | DATA | B78-R3 | Existing rooms | Existing telecom equipment may remain active during cutover | Critical | Medium | 8 | Document active services, OIT windows, rack inventory, temporary utilities and rollback plan | Telecom / OIT | Closed | Photo references include 15E, 1234, 353, 308A, 408A. | 78¦75
78 | 76 | B78_Assessment | 83 | 8. OWNER RISKS | DATA | B78-R4 | All TRs | Dedicated cooling sequence, emergency power, condensate and alarms not verified | Critical | Medium | 8 | Confirm HVAC equipment serving each TR, emergency source, condensate, controls/BACnet and high-temp alarms | Mechanical / Electrical | Closed | Mechanical sheets are included for basement through fourth level. | 78¦76
78 | 77 | B78_Assessment | 84 | 8. OWNER RISKS | DATA | B78-R5 | All TRs | Panel source, UPS/PDU and rack receptacle coordination could delay energization | Critical | Medium | 8 | Verify telecom panelboards, breakers, rack receptacles, UPS/PDU sources, SPDs, labels and LOTO requirements | Electrical / GCC | Closed | Electrical plans/schedules are extensive; confirm all panel IDs in field. | 78¦77
78 | 78 | B78_Assessment | 85 | 8. OWNER RISKS | DATA | B78-R6 | All | Large cable tray scope creates coordination and firestop risk | High | Medium | 6 | Verify 4,849 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | Telecom / GC | Closed | Cable tray schedule: basement 1,702 ft, first 959 ft, second 804 ft, third 695 ft, fourth 689 ft. | 78¦78
78 | 79 | B78_Assessment | 86 | 8. OWNER RISKS | DATA | B78-R7 | All | Telecom/fiber cutover could affect active hospital communications across B78 and B78A | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | Total scheduled ports exceed 1,300 across the primary schedules. | 78¦79
78 | 80 | B78_Assessment | 87 | 8. OWNER RISKS | DATA | B78-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope 102-sheet IFC package with multiple divisions. | 78¦80
78 | 81 | B78_Assessment | 88 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦81
78 | 82 | B78_Assessment | 89 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦82
78 | 83 | B78_Assessment | 90 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 78¦83
78 | 84 | B78_Assessment | 91 | 9. OPEN QUESTIONS | DATA | B78-Q1 | Confirm final telecom room list and PMIS mapping: B30, B35, 1232, 227A, 342, 401 plus existing rooms 15E/1234/353/308A/408A? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 78¦84
78 | 85 | B78_Assessment | 92 | 9. OPEN QUESTIONS | DATA | B78-Q2 | What active services currently remain in each existing telecom room/photo reference location? | OIT / Contractor | Closed | 0 | 0 | Potential outage/cutover risk | 0 | 0 | 0 | 78¦85
78 | 86 | B78_Assessment | 93 | 9. OPEN QUESTIONS | DATA | B78-Q3 | Are Room 1232 and existing Room 1234 separate rooms or naming/mapping references for the same telecom space? | VA / Designer / OIT | Closed | 0 | 0 | PMIS mapping risk | 0 | 0 | 0 | 78¦86
78 | 87 | B78_Assessment | 94 | 9. OPEN QUESTIONS | DATA | B78-Q4 | Which dedicated cooling units serve each TR and are they on emergency/backup power? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 78¦87
78 | 88 | B78_Assessment | 95 | 9. OPEN QUESTIONS | DATA | B78-Q5 | Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 78¦88
78 | 89 | B78_Assessment | 96 | 9. OPEN QUESTIONS | DATA | B78-Q6 | Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 78¦89
78 | 90 | B78_Assessment | 97 | 9. OPEN QUESTIONS | DATA | B78-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and temporary firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 78¦90
78 | 91 | B78_Assessment | 98 | 9. OPEN QUESTIONS | DATA | B78-Q8 | Which third-party inspections, commissioning forms and OIT acceptance records are required before turnover? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 78¦91
78 | 92 | B78_Assessment | 99 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦92
78 | 93 | B78_Assessment | 100 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦93
78 | 94 | B78_Assessment | 101 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 78¦94
78 | 95 | B78_Assessment | 102 | 10. PHOTO LOG | DATA | B78-P001 | B30 | Existing Condition | Basement RM B30 walls, ceiling/deck, floor, door, racks/future rack, power, HVAC, cable tray and penetrations | 0 | Paul | 0 | B78-R1/B78-R6 | Closed | 0 | 78¦95
78 | 96 | B78_Assessment | 103 | 10. PHOTO LOG | DATA | B78-P002 | B35 | Existing Condition | Basement RM B35 and relationship to existing telecom room 15E; rack/equipment, pathway, power, HVAC and penetrations | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0 | 78¦96
78 | 97 | B78_Assessment | 104 | 10. PHOTO LOG | DATA | B78-P003 | 1232 / 1234 | Existing Condition | First-level RM 1232/new TR and existing telecom room 1234 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0 | 78¦97
78 | 98 | B78_Assessment | 105 | 10. PHOTO LOG | DATA | B78-P004 | 227A / 1234 | Existing Condition | Second-level RM 227A/new TR and existing telecom room 1234 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0 | 78¦98
78 | 99 | B78_Assessment | 106 | 10. PHOTO LOG | DATA | B78-P005 | 342 / 353 | Existing Condition | Third-level RM 342/new TR and existing telecom room 353 photo reference, active equipment, cable paths and rack transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0 | 78¦99
78 | 100 | B78_Assessment | 107 | 10. PHOTO LOG | DATA | B78-P006 | 401 / 308A / 408A | Existing Condition | Fourth-level RM 401 and existing telecom rooms 308A/408A photo references, active equipment, cable paths and transfer scope | 0 | Paul | 0 | B78-R1/B78-R3 | Closed | 0 | 78¦100
78 | 101 | B78_Assessment | 108 | 10. PHOTO LOG | DATA | B78-P007 | All | Cable Tray / Firestop | Basement through fourth-level cable tray routes, supports, seismic bracing, penetrations and before/after firestopping | 0 | Paul | 0 | B78-R6 | Closed | 0 | 78¦101
78 | 102 | B78_Assessment | 109 | 10. PHOTO LOG | DATA | B78-P008 | All | Telecom / Security / HVAC | Racks, Fiber LIU, Cat6A, patch panels, UPS/PDU, labels/test records, CCTV, PACS, HVAC units and existing transfer work | 0 | Paul | 0 | B78-R4/B78-R7/B78-R8 | Closed | 0 | 78¦102
78 | 103 | B78_Assessment | 110 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78¦103
80 | 1 | B80_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦1
80 | 2 | B80_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 80¦2
80 | 3 | B80_Assessment | 10 | 1. ROOM INVENTORY | DATA | 80 | 102 | First | Telecom Room / new TR build area | Telecom Room | 1 | 1 | Verify | 80A-401 / 80E-101 / 80E-401 / 80T-101 / 80T-604 / 80T-701 | Primary Building 80 TR. Plans identify Telecom Room 102 at 140 SF, new Rack ID TR01-102-1 plus future rack, panels B80-TR102A/B, 5kW 208V UPS/PDU rack power, IU-1-01/CU-1-01 dedicated cooling, camera 102-CAM-1, and 215 total ports with 10% allowance. | 80¦3
80 | 4 | B80_Assessment | 11 | 1. ROOM INVENTORY | DATA | 80 | 127A / 126 | First | Existing Tel Closet / existing telecom room photo reference | Existing telecom transition point | 1 | 0 | Verify | 80T-101 / 80T-604 / 80R-900 | Existing Tel Closet 127A shown at 9 SF with existing plywood backboard, ground bar, patch panel, equipment box and two-post TR. Rack elevation/photo reference identify existing room 126/127-A with existing wall/wall-mount TE, Cisco switches, legacy optical Fiber LIU, multiple legacy Ortronics patch panels, Cat5e patch panel and APC floor UPS. Verify room-number mapping and active services. | 80¦4
80 | 5 | B80_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦5
80 | 6 | B80_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦6
80 | 7 | B80_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 80¦7
80 | 8 | B80_Assessment | 15 | 2. ROOM READINESS | DATA | 102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | First-level TR; verify 1-hour/smoke-rated enclosure, open-to-deck conditions, door hardware/access control, floor sealer, rack/future rack clearances, wall backing, cable tray and fiber path A/B entry points. | 80¦8
80 | 9 | B80_Assessment | 16 | 2. ROOM READINESS | DATA | 127A / 126 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing telecom closet/room; verify active equipment status, two-post rack/wall rack, backboard, UPS, patch panels, Fiber LIU, and transition/abandonment scope. | 80¦9
80 | 10 | B80_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦10
80 | 11 | B80_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦11
80 | 12 | B80_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 80¦12
80 | 13 | B80_Assessment | 20 | 3. FIRE PROTECTION | DATA | 102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, and temporary firestopping during cable pulls. | 80¦13
80 | 14 | B80_Assessment | 21 | 3. FIRE PROTECTION | DATA | 127A / 126 | Existing / Verify | N/A | Verify Existing | Verify Existing | Verify | Verify | Verify | Verify | Existing telecom closet/room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | 80¦14
80 | 15 | B80_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦15
80 | 16 | B80_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦16
80 | 17 | B80_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 80¦17
80 | 18 | B80_Assessment | 25 | 4. HVAC / COOLING | DATA | 102 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical/electrical drawings show IU-1-01 in Telecom Room 102 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet interface, thermostat/control point, condensate pump/path, disconnects, and high-temperature alarm. | 80¦18
80 | 19 | B80_Assessment | 26 | 4. HVAC / COOLING | DATA | 127A / 126 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom room/closet may remain active during cutover. Verify existing environmental condition and whether any active equipment remains after migration to Room 102. | 80¦19
80 | 20 | B80_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦20
80 | 21 | B80_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦21
80 | 22 | B80_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 80¦22
80 | 23 | B80_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | 102 | Verify | 5 kW / 208V rack UPS | Verify | Verify | B80-TR102A / B80-TR102B | Verify | Verify | Verify | Electrical plans/schedules identify B80-TR102A fed from BUS-B80-MDP and B80-TR102B fed from BUS-B80-E1, with rack receptacles, normal/emergency circuits, CU-1-01, SPD requirements and 30-day load measurement requirements. | 80¦23
80 | 24 | B80_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | 127A / 126 | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | 80¦24
80 | 25 | B80_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦25
80 | 26 | B80_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦26
80 | 27 | B80_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 80¦27
80 | 28 | B80_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | 102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 80T-701 identifies RM102 with 117 WAO total, 98 active ports per survey, 195 total ports per schedule, and 215 total ports with 10% allowance. Rack IDs include TR01-102-1 and TR01-102-2; rack elevation shows 1 new rack plus future rack with switches, Cat6A patch panels, Cat5e patch panel, Fiber LIU, UPS and PDU. | 80¦28
80 | 29 | B80_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | 127A / 126 | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing rack elevation shows Cisco switches, legacy optical Fiber LIU on wall, multiple legacy Ortronics 24/48-port patch panels, legacy Cat5e 24-port patch panel, and APC floor UPS. Contractor must transfer existing devices to new rack and protect active services. | 80¦29
80 | 30 | B80_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦30
80 | 31 | B80_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦31
80 | 32 | B80_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 80¦32
80 | 33 | B80_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | 102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical/telecom plans show access-control scope and camera 102-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, electric strike, camera/VMS integration, and door hardware coordination. | 80¦33
80 | 34 | B80_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | 127A / 126 | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify Existing | Verify | Verify | Verify existing security/PACS equipment conditions and whether any existing camera/security device is protected, recabled, or removed during cutover. | 80¦34
80 | 35 | B80_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦35
80 | 36 | B80_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦36
80 | 37 | B80_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 80¦37
80 | 38 | B80_Assessment | 45 | 8. OWNER RISKS | DATA | B80-R1 | All | Existing conditions for Room 102 and existing 127A/126 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B80 includes new TR plus existing telecom transition point. | 80¦38
80 | 39 | B80_Assessment | 46 | 8. OWNER RISKS | DATA | B80-R2 | 127A / 126 | Existing telecom equipment may remain active during transfer to Room 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing and rollback plan | Telecom / OIT | Closed | Existing rack elevation shows Cisco switches, legacy patch panels, Fiber LIU and APC floor UPS. | 80¦39
80 | 40 | B80_Assessment | 47 | 8. OWNER RISKS | DATA | B80-R3 | 102 / 127A | Room-number mismatch between Tel Closet 127A and photo/rack reference Room 126/127-A | High | Medium | 6 | Track both IDs in PMIS and confirm field room signage/owner mapping before punch list and turnover | GCC / VA / Designer | Closed | 80T-101 calls Tel Closet 127A; 80R-900 photo reference calls existing telecom room 126; 80T-604 lists room 126/127-A. | 80¦40
80 | 41 | B80_Assessment | 48 | 8. OWNER RISKS | DATA | B80-R4 | 102 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling is central to TR readiness. | 80¦41
80 | 42 | B80_Assessment | 49 | 8. OWNER RISKS | DATA | B80-R5 | 102 | B80-TR102A/B UPS/PDU and panel source coordination could delay energization | High | Medium | 6 | Verify panel sources BUS-B80-MDP and BUS-B80-E1, breakers, receptacles, SPD, labels, load measurement and LOTO needs | Electrical / GCC | Closed | B80-TR102A/B panel schedules and one-line show normal/emergency source split. | 80¦42
80 | 43 | B80_Assessment | 50 | 8. OWNER RISKS | DATA | B80-R6 | All | 811 feet of cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | 80T-701 cable tray schedule: basement 122 ft, first level 688 ft, grand total 811 ft. | 80¦43
80 | 44 | B80_Assessment | 51 | 8. OWNER RISKS | DATA | B80-R7 | All | Telecom/fiber cutover could affect active hospital communications on first-level operations | Critical | Medium | 8 | Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | Telecom / OIT | Closed | RM102 supports 215 total ports including allowance and existing rack transfer. | 80¦44
80 | 45 | B80_Assessment | 52 | 8. OWNER RISKS | DATA | B80-R8 | All | Commissioning/third-party inspection reports may not be complete at turnover | High | Medium | 6 | Track commissioning, inspections, FA/FP acceptance, power verification, cabling tests, labels and as-builts | GC / Cx Manager | Closed | Full-scope 52-sheet IFC package with mechanical, electrical, FP and telecom work. | 80¦45
80 | 46 | B80_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦46
80 | 47 | B80_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦47
80 | 48 | B80_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 80¦48
80 | 49 | B80_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B80-Q1 | Confirm final telecom scope: new Room 102 with existing 127A/126 transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory could miss scope | 0 | 0 | 0 | 80¦49
80 | 50 | B80_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B80-Q2 | What active services are currently fed from existing Room 127A/126 equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 80¦50
80 | 51 | B80_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B80-Q3 | Are Room 127A and Room 126 the same telecom room, or separate locations? | VA / Designer / OIT | Closed | 0 | 0 | PMIS mapping and turnover risk | 0 | 0 | 0 | 80¦51
80 | 52 | B80_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B80-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 80¦52
80 | 53 | B80_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B80-Q5 | Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 102? | GC / COR | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | 80¦53
80 | 54 | B80_Assessment | 61 | 9. OPEN QUESTIONS | DATA | B80-Q6 | Are B80-TR102A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 80¦54
80 | 55 | B80_Assessment | 62 | 9. OPEN QUESTIONS | DATA | B80-Q7 | Are all rated wall/floor penetrations, sleeves, cable tray entries and firestopping details identified? | GC / Firestop | Closed | 0 | 0 | Fire/smoke spread risk | 0 | 0 | 0 | 80¦55
80 | 56 | B80_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B80-Q8 | Which third-party inspections and commissioning forms are required before VA/OIT acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 80¦56
80 | 57 | B80_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦57
80 | 58 | B80_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦58
80 | 59 | B80_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 80¦59
80 | 60 | B80_Assessment | 67 | 10. PHOTO LOG | DATA | B80-P001 | 102 | Existing Condition | Room 102 walls, ceiling/deck, floor, door, rack/future rack, power, HVAC, fiber path A/B, cable tray and penetrations | 0 | Paul | 0 | B80-R1/B80-R4 | Closed | 0 | 80¦60
80 | 61 | B80_Assessment | 68 | 10. PHOTO LOG | DATA | B80-P002 | 127A / 126 | Existing Condition | Existing Tel Closet/telecom room with plywood backboard, ground bar, patch panel, equipment box, two-post rack/wall TE and cable entries | 0 | Paul | 0 | B80-R1/B80-R2 | Closed | 0 | 80¦61
80 | 62 | B80_Assessment | 69 | 10. PHOTO LOG | DATA | B80-P003 | 127A / 126 | Existing Equipment | Cisco switches, legacy Fiber LIU, Ortronics patch panels, Cat5e patch panel, APC floor UPS and active service labels | 0 | Paul | 0 | B80-R2/B80-R3 | Closed | 0 | 80¦62
80 | 63 | B80_Assessment | 70 | 10. PHOTO LOG | DATA | B80-P004 | 102 | HVAC | IU-1-01/CU-1-01, condensate, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B80-R4 | Closed | 0 | 80¦63
80 | 64 | B80_Assessment | 71 | 10. PHOTO LOG | DATA | B80-P005 | 102 | Electrical | B80-TR102A/B panels, rack receptacles, breakers, SPD, access controller, lighting, CU-1-01 and labels | 0 | Paul | 0 | B80-R5 | Closed | 0 | 80¦64
80 | 65 | B80_Assessment | 72 | 10. PHOTO LOG | DATA | B80-P006 | All | Cable Tray / Firestop | Basement and first-level cable tray route, supports, seismic bracing, 40% fill, penetrations and before/after firestopping | 0 | Paul | 0 | B80-R6 | Closed | 0 | 80¦65
80 | 66 | B80_Assessment | 73 | 10. PHOTO LOG | DATA | B80-P007 | 102 / 127A | Telecom | New rack/future rack, Fiber LIU, Cat6A, patch panels, labels/test records and existing rack transfer work | 0 | Paul | 0 | B80-R7 | Closed | 0 | 80¦66
80 | 67 | B80_Assessment | 74 | 10. PHOTO LOG | DATA | B80-P008 | 102 | Security | 102-CAM-1, card reader, electric strike, door position, motion sensor, existing security devices and VMS/PACS integration | 0 | Paul | 0 | B80-R8 | Closed | 0 | 80¦67
80 | 68 | B80_Assessment | 75 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80¦68
82 | 1 | B82_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦1
82 | 2 | B82_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | 82¦2
82 | 3 | B82_Assessment | 10 | 1. ROOM INVENTORY | DATA | 82 | 102 | First | Telecom Room / new TE location | Telecom Enclosure | 1 | 0 | Verify | 82A-401 / 82M-101 / 82E-101 / 82T-101 / 82T-604 / 82T-701 | Primary Building 82 TE. Plans identify Telecom Room 102 at 86 SF with new 12RU telecom enclosure, Rack ID TR01-102-01, APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, IU-1-01/CU-1-01 cooling, and 40 total ports with 10% allowance. | 82¦3
82 | 4 | B82_Assessment | 11 | 1. ROOM INVENTORY | DATA | 82 | B01-A | First | Existing telecom room / wall rack and patch panels | Existing telecom transition point | 1 | 0 | Verify | 82T-101 / 82T-604 / 82R-900 | Existing first-level telecom room B01-A shown with existing wall rack, Cisco switches, cable management, Ortronics 24-port patch panels, APC floor UPS, and photo reference. Protect active services and verify transfer to Room 102 TE. | 82¦4
82 | 5 | B82_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦5
82 | 6 | B82_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦6
82 | 7 | B82_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | 82¦7
82 | 8 | B82_Assessment | 15 | 2. ROOM READINESS | DATA | 102 | Verify | Verify | N/A / TE Room | Verify | Verify Existing | Verify | Verify | Verify | New TE enclosure location in Telecom Room 102; verify wall backing, mounting height, access clearance, power, fiber/copper path, 4-inch speed sleeve, fire/smoke wall rating, ceiling/deck conditions and that 86 SF is adequate for equipment maintenance. | 82¦8
82 | 9 | B82_Assessment | 16 | 2. ROOM READINESS | DATA | B01-A | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify Existing | Verify | Verify | Verify | Existing telecom room; verify active equipment status, wall rack, UPS, patch panels, cable management, pathway, and transition/abandonment scope. | 82¦9
82 | 10 | B82_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦10
82 | 11 | B82_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦11
82 | 12 | B82_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | 82¦12
82 | 13 | B82_Assessment | 20 | 3. FIRE PROTECTION | DATA | 102 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states Building 82 receives a Telecom Enclosure and fire protection scope is excluded. Still verify rated penetrations, 4-inch sleeve, wall/floor openings, temporary firestopping, and life-safety device impacts. | 82¦13
82 | 14 | B82_Assessment | 21 | 3. FIRE PROTECTION | DATA | B01-A | Existing / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Existing telecom room; verify protection-in-place and firestopping after cable transfer or reuse. | 82¦14
82 | 15 | B82_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦15
82 | 16 | B82_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦16
82 | 17 | B82_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | 82¦17
82 | 18 | B82_Assessment | 25 | 4. HVAC / COOLING | DATA | 102 | IU-1-01 / CU-1-01 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Mechanical and electrical drawings show IU-1-01 in/near Telecom Room 102 and CU-1-01 outdoor unit. Mechanical notes call for BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency/standby source, condensate pump/path, disconnects, controls, and high-temp alarm. | 82¦18
82 | 19 | B82_Assessment | 26 | 4. HVAC / COOLING | DATA | B01-A | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Existing telecom room may remain active during cutover. Verify existing environmental conditions and whether active equipment remains after transfer to Room 102. | 82¦19
82 | 20 | B82_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦20
82 | 21 | B82_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦21
82 | 22 | B82_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | 82¦22
82 | 23 | B82_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | 102 | Verify | APC UPS / 12RU enclosure | Verify | Verify | B82-MDP / B82-P-EMER source to verify | Verify | Verify | Verify | Electrical plans/schedules identify TE receptacle, CU-1-01, B82-MDP and B82-P-EMER sources, with SPD devices integral to new telecom panelboards. Verify receptacle type, grounding/bonding, emergency source, labels, and circuit loading. | 82¦23
82 | 24 | B82_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | B01-A | Existing | Existing APC floor UPS | Existing | Verify | Existing / Verify | Verify | Verify | Verify | Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | 82¦24
82 | 25 | B82_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦25
82 | 26 | B82_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦26
82 | 27 | B82_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | 82¦27
82 | 28 | B82_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | 102 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | 82T-701 identifies RM102 with 26 WAO total, 31 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. Rack ID TR01-102-01. Cable tray schedule totals 278 ft on first level. New enclosure includes APC UPS, two PDUs, network switch, Cat6A patch panel and Fiber LIU. | 82¦28
82 | 29 | B82_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | B01-A | Existing | Existing | Existing | Verify | Verify | Verify | Verify | Verify | Existing B01-A elevations identify Cisco switches, cable management, two Ortronics 24-port patch panels with 11 and 6 used, existing patch panels and APC floor UPS. Field verify active services and transfer plan to new TE. | 82¦29
82 | 30 | B82_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦30
82 | 31 | B82_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦31
82 | 32 | B82_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | 82¦32
82 | 33 | B82_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | 102 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Building 82 appears to create a TE enclosure rather than a full TR door/PACS package. Verify existing cameras/security devices in Room 102 and ensure no camera angle or VMS integration is disrupted. | 82¦33
82 | 34 | B82_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | B01-A | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify Existing | Verify Existing | Verify | Verify | Keynotes indicate existing cameras are to be retained and re-used. Verify security/access conditions and whether any legacy security equipment is present at existing telecom room. | 82¦34
82 | 35 | B82_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦35
82 | 36 | B82_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦36
82 | 37 | B82_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | 82¦37
82 | 38 | B82_Assessment | 45 | 8. OWNER RISKS | DATA | B82-R1 | All | Existing conditions for new Room 102 TE and existing B01-A not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | B82 has a compact TE scope but still depends on field conditions and existing equipment transfer. | 82¦38
82 | 39 | B82_Assessment | 46 | 8. OWNER RISKS | DATA | B82-R2 | 102 / B01-A | Existing equipment in B01-A may remain active during transfer to new TE in 102 | Critical | Medium | 8 | Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities | Telecom / OIT | Closed | 82T-101 keynotes require phasing plan and transfer of existing devices to new rack/enclosure. | 82¦39
82 | 40 | B82_Assessment | 47 | 8. OWNER RISKS | DATA | B82-R3 | 102 | Cover sheet says TE, but mechanical cooling is included for Room 102 | High | Medium | 6 | Confirm scope interpretation with VA/AE and ensure cooling is commissioned if it serves active TE equipment | GCC / VA / Designer | Closed | Unlike some TE buildings, B82 includes IU-1-01/CU-1-01 mechanical/electrical scope. | 82¦40
82 | 41 | B82_Assessment | 48 | 8. OWNER RISKS | DATA | B82-R4 | 102 | Dedicated cooling emergency power, condensate, BACnet and alarms not verified | Critical | Medium | 8 | Confirm IU-1-01/CU-1-01 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm | Mechanical / Electrical | Closed | Cooling appears included and must be verified before acceptance. | 82¦41
82 | 42 | B82_Assessment | 49 | 8. OWNER RISKS | DATA | B82-R5 | 102 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding, SPD and labels | Electrical / Telecom | Closed | New TE enclosure includes APC UPS and two PDUs. | 82¦42
82 | 43 | B82_Assessment | 50 | 8. OWNER RISKS | DATA | B82-R6 | All | 278 feet of first-level cable tray/pathway requires coordination and firestop tracking | High | Medium | 6 | Verify route, supports, seismic bracing, 40% fill, penetrations, light/HVAC conflicts and firestop assemblies | Telecom / GC | Closed | 82T-701 cable tray schedule lists first level estimated length of 278 ft. | 82¦43
82 | 44 | B82_Assessment | 51 | 8. OWNER RISKS | DATA | B82-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch speed sleeve, rated penetrations, fire caulk, temporary firestopping and patching even without FP sheet scope | GC / Firestop | Closed | Cover excludes fire protection; telecom notes require fire caulk and rated penetrations. | 82¦44
82 | 45 | B82_Assessment | 52 | 8. OWNER RISKS | DATA | B82-R8 | All | Commissioning/test documentation may be overlooked due to TE-only scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification, HVAC startup/controls and owner signoff | GC / Cx Manager | Closed | General notes still require testing, acceptance and documentation. | 82¦45
82 | 46 | B82_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦46
82 | 47 | B82_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦47
82 | 48 | B82_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | 82¦48
82 | 49 | B82_Assessment | 56 | 9. OPEN QUESTIONS | DATA | B82-Q1 | Confirm final scope: new 12RU wall-mount TE enclosure in Room 102 and existing B01-A transition only? | VA / OIT / Designer | Closed | 0 | 0 | Room inventory or PMIS mapping could miss scope | 0 | 0 | 0 | 82¦49
82 | 50 | B82_Assessment | 57 | 9. OPEN QUESTIONS | DATA | B82-Q2 | What active services are currently fed from existing B01-A equipment? | OIT / Contractor | Closed | 0 | 0 | Potential communications/security outage | 0 | 0 | 0 | 82¦50
82 | 51 | B82_Assessment | 58 | 9. OPEN QUESTIONS | DATA | B82-Q3 | Is Room 102 officially a TE-only scope or a conditioned telecom room with mechanical support? | VA / AE / COR | Closed | 0 | 0 | Scope and commissioning responsibility unclear | 0 | 0 | 0 | 82¦51
82 | 52 | B82_Assessment | 59 | 9. OPEN QUESTIONS | DATA | B82-Q4 | Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? | Mechanical / Electrical / VA | Closed | 0 | 0 | Cooling continuity unclear | 0 | 0 | 0 | 82¦52
82 | 53 | B82_Assessment | 60 | 9. OPEN QUESTIONS | DATA | B82-Q5 | What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | 82¦53
82 | 54 | B82_Assessment | 61 | 9. OPEN QUESTIONS | DATA | B82-Q6 | Are all 278 feet of cable tray route, sleeves, supports and firestopping details field verified? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0 | 82¦54
82 | 55 | B82_Assessment | 62 | 9. OPEN QUESTIONS | DATA | B82-Q7 | Are existing cameras/security devices protected and retained with no VMS/PACS disruption? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0 | 82¦55
82 | 56 | B82_Assessment | 63 | 9. OPEN QUESTIONS | DATA | B82-Q8 | Which test records, HVAC startup records and turnover documents are required for TE acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | 82¦56
82 | 57 | B82_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦57
82 | 58 | B82_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦58
82 | 59 | B82_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | 82¦59
82 | 60 | B82_Assessment | 67 | 10. PHOTO LOG | DATA | B82-P001 | 102 | Existing Condition | Room 102 wall location, wall backing, clearances, ceiling, power source, cable path, fiber path A/B and new TE enclosure location | 0 | Paul | 0 | B82-R1/B82-R3 | Closed | 0 | 82¦60
82 | 61 | B82_Assessment | 68 | 10. PHOTO LOG | DATA | B82-P002 | B01-A | Existing Condition | Existing first-level telecom room B01-A wall rack, Cisco switches, cable management, Ortronics patch panels, APC floor UPS and cable entries | 0 | Paul | 0 | B82-R1/B82-R2 | Closed | 0 | 82¦61
82 | 62 | B82_Assessment | 69 | 10. PHOTO LOG | DATA | B82-P003 | 102 / B01-A | Pathway | 278 ft first-level cable tray route, 4-inch sleeve, wall/floor penetrations, support points, light/HVAC conflicts and 40% fill concerns | 0 | Paul | 0 | B82-R6/B82-R7 | Closed | 0 | 82¦62
82 | 63 | B82_Assessment | 70 | 10. PHOTO LOG | DATA | B82-P004 | 102 | HVAC | IU-1-01/CU-1-01, condensate pump/path, thermostat, BACnet adapter, disconnects, high-temp alarm and power source | 0 | Paul | 0 | B82-R4 | Closed | 0 | 82¦63
82 | 64 | B82_Assessment | 71 | 10. PHOTO LOG | DATA | B82-P005 | 102 | Electrical | New TE enclosure UPS/PDU receptacles, circuit source, B82-MDP/B82-P-EMER connections, grounding/bonding, SPD, labels and access | 0 | Paul | 0 | B82-R5 | Closed | 0 | 82¦64
82 | 65 | B82_Assessment | 72 | 10. PHOTO LOG | DATA | B82-P006 | 102 / B01-A | Telecom | TR01-102-01 enclosure, cross-connect/cutover cabling, Fiber LIU, patch panels, labels, test results and existing equipment transfer | 0 | Paul | 0 | B82-R2/B82-R8 | Closed | 0 | 82¦65
82 | 66 | B82_Assessment | 73 | 10. PHOTO LOG | DATA | B82-P007 | All | Firestop | 4-inch speed sleeve, wall/floor penetrations and fire caulk before/after photos | 0 | Paul | 0 | B82-R7 | Closed | 0 | 82¦66
82 | 67 | B82_Assessment | 74 | 10. PHOTO LOG | DATA | B82-P008 | All | Security / Existing Devices | Existing cameras/security devices to remain, protection-in-place and final operating condition | 0 | Paul | 0 | B82-R8 | Closed | 0 | 82¦67
82 | 68 | B82_Assessment | 75 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82¦68
BCH | 1 | BCH_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦1
BCH | 2 | BCH_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | BCH¦2
BCH | 3 | BCH_Assessment | 10 | 1. ROOM INVENTORY | DATA | BCH | 107 | First | Existing Crescent House room area / telecom work area | Telecom Enclosure / Telecom Room | 1 | 0 | Verify | BCHGA-401 / BCHE-101 / BCHT-101 / BCHT-604 | Primary BCH telecom location. Architectural/electrical/telecom plans reference first-level Room 107. BCHT-101 enlarged plan identifies RM 107 new telecom work. BCHT-604 shows BCH Crescent House Room 107 as new telecom room / no existing elevations. | BCH¦3
BCH | 4 | BCH_Assessment | 11 | 1. ROOM INVENTORY | DATA | BCH | 00 / 107 | First | Rack/elevation reference location | Telecom Enclosure | 1 | 0 | Verify | BCHT-604 | Rack elevation shows 12RU telecom enclosure with APC UPS, two PDUs, network switch, 48-port Cat6A patch panel, Fiber LIU, and first-level mounting. Also includes separate BCH Crescent House Room 107 / new telecom room elevation; field confirm correct configuration. | BCH¦4
BCH | 5 | BCH_Assessment | 12 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦5
BCH | 6 | BCH_Assessment | 13 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦6
BCH | 7 | BCH_Assessment | 14 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | BCH¦7
BCH | 8 | BCH_Assessment | 15 | 2. ROOM READINESS | DATA | 107 | Verify | Verify | N/A / TE Scope | Verify | Verify Existing | Verify | Verify | Verify | Verify wall backing, mounting height, access clearance, cable tray/sleeve entry, rated wall/firestop requirements, floor/ceiling conditions, ICRA barriers, and whether Room 107 functions as a TE-only space or a telecom room. | BCH¦8
BCH | 9 | BCH_Assessment | 16 | 2. ROOM READINESS | DATA | 00 / 107 | Verify | Verify | N/A / TE Scope | Verify | Verify Existing | Verify | Verify | Verify | Rack elevation conflict requires field/AE confirmation before PMIS closeout. Confirm whether the 12RU wall enclosure or 45RU telecom room rack configuration is the governing installation. | BCH¦9
BCH | 10 | BCH_Assessment | 17 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦10
BCH | 11 | BCH_Assessment | 18 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦11
BCH | 12 | BCH_Assessment | 19 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | BCH¦12
BCH | 13 | BCH_Assessment | 20 | 3. FIRE PROTECTION | DATA | 107 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | Cover sheet states BCH receives a Telecom Enclosure and mechanical/fire protection scope has been excluded. Still verify existing life-safety protection, rated penetrations, 4-inch sleeve fire caulk, temporary firestopping and abandoned penetration patching. | BCH¦13
BCH | 14 | BCH_Assessment | 21 | 3. FIRE PROTECTION | DATA | 00 / 107 | Excluded / Verify | N/A | Verify Existing | Verify Existing | N/A / Verify | Verify | Verify | Verify | TE-only scope does not appear to require new FEC/fire sprinkler work, but all wall/floor/ceiling penetrations must be sealed and rated assemblies maintained. | BCH¦14
BCH | 15 | BCH_Assessment | 22 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦15
BCH | 16 | BCH_Assessment | 23 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦16
BCH | 17 | BCH_Assessment | 24 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | BCH¦17
BCH | 18 | BCH_Assessment | 25 | 4. HVAC / COOLING | DATA | 107 | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Cover sheet explicitly excludes mechanical scope. Verify existing room ambient conditions are acceptable for TE equipment and that no active network equipment will overheat. | BCH¦18
BCH | 19 | BCH_Assessment | 26 | 4. HVAC / COOLING | DATA | 00 / 107 | Excluded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | If the final scope is a 45RU new telecom room rather than a small TE, HVAC exclusion should be confirmed with VA/AE because telecom-room heat load may differ from TE assumptions. | BCH¦19
BCH | 20 | BCH_Assessment | 27 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦20
BCH | 21 | BCH_Assessment | 28 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦21
BCH | 22 | BCH_Assessment | 29 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | BCH¦22
BCH | 23 | BCH_Assessment | 30 | 5. ELECTRICAL / UPS | DATA | 107 | Verify | APC UPS / TE enclosure | Verify | Verify | BCHE-101 / BCHE-601 source to verify | Verify | Verify | Verify | Electrical plan includes first-level electrical work and notes for new wall-mount telecom enclosure, grounding/bonding and camera. Verify circuit source, receptacle type, UPS/PDU load, emergency source if required, grounding/bonding and labels. | BCH¦23
BCH | 24 | BCH_Assessment | 31 | 5. ELECTRICAL / UPS | DATA | 00 / 107 | Verify | APC UPS / 12RU enclosure or 5kW rack UPS if room rack governs | Verify | Verify | Verify | Verify | Verify | Verify | BCHT-604 shows 12RU TE equipment with APC UPS and PDUs and also a BCH 45RU new telecom room elevation. Confirm exact UPS/PDU/rack power requirement before acceptance. | BCH¦24
BCH | 25 | BCH_Assessment | 32 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦25
BCH | 26 | BCH_Assessment | 33 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦26
BCH | 27 | BCH_Assessment | 34 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | BCH¦27
BCH | 28 | BCH_Assessment | 35 | 6. TELECOMMUNICATIONS | DATA | 107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | BCHT-101 identifies telecom plan first level and enlarged Room 107. BCHT-604 identifies new telecom room/no existing elevations. There is no BCHT-701 schedule in the drawing index, so WAO/cable-tray totals must be field verified from plans and contractor coordination drawings. | BCH¦28
BCH | 29 | BCH_Assessment | 36 | 6. TELECOMMUNICATIONS | DATA | 00 / 107 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | BCHT-604 identifies a 12RU TE elevation: APC UPS, two PDUs, network switch, 48-port Cat6A patch panel and Fiber LIU. Also shows BCH Crescent House Room 107 new telecom room elevation. Confirm governing rack/enclosure and labeling. | BCH¦29
BCH | 30 | BCH_Assessment | 37 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦30
BCH | 31 | BCH_Assessment | 38 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦31
BCH | 32 | BCH_Assessment | 39 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | BCH¦32
BCH | 33 | BCH_Assessment | 40 | 7. SECURITY / PACS / CCTV | DATA | 107 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify | Verify | Verify | Verify | Telecom/electrical notes reference new IP-addressable camera with wall mount at 8'-6" A.F.F. and VMS integration. Verify whether PACS applies; TE buildings typically do not create full TR door/PACS scope. | BCH¦33
BCH | 34 | BCH_Assessment | 41 | 7. SECURITY / PACS / CCTV | DATA | 00 / 107 | N/A / Verify | N/A / Verify | N/A / Verify | N/A / Verify | Verify | Verify | Verify | Verify | Verify existing camera/security conditions, protection-in-place, and any recabling or VMS integration required. | BCH¦34
BCH | 35 | BCH_Assessment | 42 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦35
BCH | 36 | BCH_Assessment | 43 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦36
BCH | 37 | BCH_Assessment | 44 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | BCH¦37
BCH | 38 | BCH_Assessment | 45 | 8. OWNER RISKS | DATA | BCH-R1 | All | Existing conditions for Crescent House Room 107 not field verified | High | Medium | 6 | Perform existing conditions survey with photos before mobilization | GCC / Contractor | Closed | BCH is off-site at 15 Veterans Way, Lowell and requires careful field verification. | BCH¦38
BCH | 39 | BCH_Assessment | 46 | 8. OWNER RISKS | DATA | BCH-R2 | 107 | Mechanical and fire protection are excluded despite telecom/electronics installation | High | Medium | 6 | Verify existing environmental and life-safety conditions support TE equipment; confirm no dedicated HVAC/FP requirement applies | GCC / VA / AE | Closed | Cover sheet explicitly excludes mechanical and fire protection. | BCH¦39
BCH | 40 | BCH_Assessment | 47 | 8. OWNER RISKS | DATA | BCH-R3 | 107 / 00 | Rack/elevation conflict: TE 12RU enclosure versus BCH Room 107 new telecom room elevation | High | Medium | 6 | Submit RFI/confirm with AE which elevation governs and map room/equipment in PMIS | Telecom / Designer | Closed | BCHT-604 includes both TE enclosure and BCH 45RU new telecom room/no existing elevations. | BCH¦40
BCH | 41 | BCH_Assessment | 48 | 8. OWNER RISKS | DATA | BCH-R4 | 107 | Active services and existing devices may require phasing/temporary service | Critical | Medium | 8 | Document active services, maintain existing service, use phasing plan, temporary utilities and OIT cutover windows | Telecom / OIT | Closed | General telecom notes require transfer/phasing and avoiding shutdowns. | BCH¦41
BCH | 42 | BCH_Assessment | 49 | 8. OWNER RISKS | DATA | BCH-R5 | 107 | UPS/PDU/receptacle source and grounding/bonding not verified | High | Medium | 6 | Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels | Electrical / Telecom | Closed | Electrical sheets included but no full mechanical/FP package. | BCH¦42
BCH | 43 | BCH_Assessment | 50 | 8. OWNER RISKS | DATA | BCH-R6 | All | Cable tray, sleeve and pathway quantities not scheduled in a BCHT-701 sheet | High | Medium | 6 | Require coordination drawings showing route, supports, fill, penetrations, sleeves and cable counts | Telecom / GC | Closed | Drawing index does not list BCHT-701 telecom schedules. | BCH¦43
BCH | 44 | BCH_Assessment | 51 | 8. OWNER RISKS | DATA | BCH-R7 | All | Firestopping/rated sleeve work could be missed because FP scope is excluded | High | Medium | 6 | Track 4-inch sleeves, rated penetrations, fire caulk, temporary firestopping and patching even without FP scope | GC / Firestop | Closed | Telecom plan notes still require fire caulk and rated penetration protection. | BCH¦44
BCH | 45 | BCH_Assessment | 52 | 8. OWNER RISKS | DATA | BCH-R8 | All | Turnover documentation may be incomplete due to TE-only/off-site scope | High | Medium | 6 | Track cable test records, labels, as-builts, laminated schedules, OIT acceptance, UPS/PDU verification and owner signoff | GC / Cx Manager | Closed | Commissioning/testing requirements still apply to impacted systems. | BCH¦45
BCH | 46 | BCH_Assessment | 53 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦46
BCH | 47 | BCH_Assessment | 54 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦47
BCH | 48 | BCH_Assessment | 55 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | BCH¦48
BCH | 49 | BCH_Assessment | 56 | 9. OPEN QUESTIONS | DATA | BCH-Q1 | Confirm final BCH scope: Room 107 TE enclosure only, or a new telecom room/rack buildout? | VA / AE / OIT | Closed | 0 | 0 | PMIS scope and acceptance criteria unclear | 0 | 0 | 0 | BCH¦49
BCH | 50 | BCH_Assessment | 57 | 9. OPEN QUESTIONS | DATA | BCH-Q2 | Why does BCHT-604 show a T78 12RU TE enclosure and a separate BCH Crescent House Room 107 new telecom room elevation? | VA / Designer | Closed | 0 | 0 | Rack/equipment mapping conflict | 0 | 0 | 0 | BCH¦50
BCH | 51 | BCH_Assessment | 58 | 9. OPEN QUESTIONS | DATA | BCH-Q3 | What active services currently serve Crescent House and where are existing terminations located? | OIT / Contractor | Closed | 0 | 0 | Cutover/outage risk | 0 | 0 | 0 | BCH¦51
BCH | 52 | BCH_Assessment | 59 | 9. OPEN QUESTIONS | DATA | BCH-Q4 | What is the approved power source, receptacle type and circuit capacity for the new UPS/PDU? | Electrical / Designer | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | BCH¦52
BCH | 53 | BCH_Assessment | 60 | 9. OPEN QUESTIONS | DATA | BCH-Q5 | Is existing HVAC/ambient condition acceptable for TE/network equipment since mechanical scope is excluded? | VA / OIT / Facilities | Closed | 0 | 0 | Heat/load risk | 0 | 0 | 0 | BCH¦53
BCH | 54 | BCH_Assessment | 61 | 9. OPEN QUESTIONS | DATA | BCH-Q6 | Are cable tray route, sleeve locations, supports and firestopping details shown/field verified without a BCHT-701 schedule? | Telecom / GC / Firestop | Closed | 0 | 0 | Install delay or firestop gap | 0 | 0 | 0 | BCH¦54
BCH | 55 | BCH_Assessment | 62 | 9. OPEN QUESTIONS | DATA | BCH-Q7 | Are camera/security devices required, protected and integrated into VMS for Room 107? | Security / OIT | Closed | 0 | 0 | Security continuity unclear | 0 | 0 | 0 | BCH¦55
BCH | 56 | BCH_Assessment | 63 | 9. OPEN QUESTIONS | DATA | BCH-Q8 | Which test records and turnover documents are required for BCH TE/off-site acceptance? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | BCH¦56
BCH | 57 | BCH_Assessment | 64 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦57
BCH | 58 | BCH_Assessment | 65 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦58
BCH | 59 | BCH_Assessment | 66 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | BCH¦59
BCH | 60 | BCH_Assessment | 67 | 10. PHOTO LOG | DATA | BCH-P001 | 107 | Existing Condition | Room 107 walls, ceiling, floor, wall backing, clearances, existing devices, power source, cable path, and proposed TE/rack location | 0 | Paul | 0 | BCH-R1/BCH-R3 | Closed | 0 | BCH¦60
BCH | 61 | BCH_Assessment | 68 | 10. PHOTO LOG | DATA | BCH-P002 | 107 | Electrical | Panel/source, receptacles, UPS/PDU location, grounding/bonding bar, labels and access clearance | 0 | Paul | 0 | BCH-R5 | Closed | 0 | BCH¦61
BCH | 62 | BCH_Assessment | 69 | 10. PHOTO LOG | DATA | BCH-P003 | 107 | Telecom | 12RU enclosure or rack location, Fiber LIU, patch panel, network switch, Cat6A terminations, labels and test records | 0 | Paul | 0 | BCH-R3/BCH-R8 | Closed | 0 | BCH¦62
BCH | 63 | BCH_Assessment | 70 | 10. PHOTO LOG | DATA | BCH-P004 | 107 | Pathway | Cable tray route, 4-inch sleeves, wall/floor penetrations, support points and 40% fill concerns | 0 | Paul | 0 | BCH-R6/BCH-R7 | Closed | 0 | BCH¦63
BCH | 64 | BCH_Assessment | 71 | 10. PHOTO LOG | DATA | BCH-P005 | 107 | Firestop | Rated penetrations, fire caulk and temporary/final firestopping before/after photos | 0 | Paul | 0 | BCH-R7 | Closed | 0 | BCH¦64
BCH | 65 | BCH_Assessment | 72 | 10. PHOTO LOG | DATA | BCH-P006 | 107 | HVAC / Existing Environment | Existing room cooling/ventilation and ambient condition for TE equipment | 0 | Paul | 0 | BCH-R2/BCH-R5 | Closed | 0 | BCH¦65
BCH | 66 | BCH_Assessment | 73 | 10. PHOTO LOG | DATA | BCH-P007 | 107 | Security / CCTV | Camera location, existing/security devices, VMS integration, access conditions and protection-in-place | 0 | Paul | 0 | BCH-R8 | Closed | 0 | BCH¦66
BCH | 67 | BCH_Assessment | 74 | 10. PHOTO LOG | DATA | BCH-P008 | All | Off-site Coordination | Site access, staging, ICRA/dust control, work area barriers and temporary service conditions | 0 | Paul | 0 | BCH-R1/BCH-R4 | Closed | 0 | BCH¦67
BCH | 68 | BCH_Assessment | 75 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BCH¦68
MCR | 1 | MCR_Assessment | 8 | 1. ROOM INVENTORY | SECTION | 1. ROOM INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦1
MCR | 2 | MCR_Assessment | 9 | 1. ROOM INVENTORY | HEADER | Building | Room | Floor | Existing Use | New Use | Rack Count | Future Rack | Status | Drawing Ref | Notes | MCR¦2
MCR | 3 | MCR_Assessment | 10 | 1. ROOM INVENTORY | DATA | MCR | 107 / MCR | Ground | New Main Computer Room / MCR building | Main Computer Room | 12 | 0 | Verify | MCRA-101 / MCRT-100 / MCRT-101 / MCRT-401 / MCRT-607-609 / MCRT-701 | Primary new MCR space. Telecom plans show MDA-A1/A2/A3, MDA-B1/B2/B3, HDA-A, HDA-B, UPS-A and UPS-B. Rack elevations identify MDA A/B racks, HDA A/B server cabinets, existing server cabinet transfer references, 10 WAO total and 359 ft cable tray. | MCR¦3
MCR | 4 | MCR_Assessment | 11 | 1. ROOM INVENTORY | DATA | MCR | 031 / Fiber Entrance Room 1 | Ground | Fiber entrance / telecom pathway space | Fiber Entrance / support room | 1 | 0 | Verify | MCRT-401 / MCRT-701 | MCRT-701 schedule is titled Data Device and Circuit Schedule - Fiber Entrance Room 1 and identifies Rack ID TR01-031-1, four data outlets 31-A/B/C/D and security camera/data devices 07-CAM-03/04/07/08/11. | MCR¦4
MCR | 5 | MCR_Assessment | 12 | 1. ROOM INVENTORY | DATA | MCR | MDA-A1/A2/A3 | Ground | New MDA row A | Main Distribution Area A | 3 | 0 | Verify | MCRT-607 | New MDA A racks: MDA-A-1, MDA-A-2, MDA-A-3. MDA A-2 includes 1RU LIU for hybrid FOC to HDA and 48x Cat6A to HDA. MDA A-1/A-3 reserved for LAN elements/leaf/access or spine/aggregation. | MCR¦5
MCR | 6 | MCR_Assessment | 13 | 1. ROOM INVENTORY | DATA | MCR | MDA-B1/B2/B3 | Ground | New MDA row B | Main Distribution Area B | 3 | 0 | Verify | MCRT-607 | New MDA B racks: MDA-B-1, MDA-B-2, MDA-B-3. MDA B-2 includes 1RU LIU for hybrid FOC to HDA and 48x Cat6A to HDA. Supports redundant B-side backbone/distribution. | MCR¦6
MCR | 7 | MCR_Assessment | 14 | 1. ROOM INVENTORY | DATA | MCR | HDA-A | Ground | New HDA A row | Horizontal Distribution Area A | 1 | 0 | Verify | MCRT-608 | HDA A-1 new server cabinet front/rear elevation, 48-port Cat6A patch panels, HD fiber LIUs, HD Cat6A patch panel to MDA-A2, and backbone side A/B LIU. Also includes existing B61 server cabinet transfer references. | MCR¦7
MCR | 8 | MCR_Assessment | 15 | 1. ROOM INVENTORY | DATA | MCR | HDA-B | Ground | New HDA B row | Horizontal Distribution Area B | 1 | 0 | Verify | MCRT-609 | HDA B-1 new server cabinet front/rear elevation, 48-port Cat6A patch panels, HD fiber LIUs, HD Cat6A patch panel to MDA-B2, and duplicate existing B61 server cabinet transfer references. | MCR¦8
MCR | 9 | MCR_Assessment | 16 | 1. ROOM INVENTORY | DATA | MCR | Existing 107 / 137 Server MCR | Existing / transition | Existing MCR/server/core equipment | Existing equipment transition point | 20 | 0 | Verify | MCRT-604 / MCRT-605 / MCRT-606 / MCRT-608 / MCRT-609 | Existing MCR elevations include Rows 1-3 and existing server cabinet B61 equipment, Cisco core, WAN aggregation, NetScout, Canoga Perkins, Cisco switches, legacy Ortronics patch panels, LIUs, APC/Chatsworth/HP PDUs and UPS equipment. Protect and phase transfer. | MCR¦9
MCR | 10 | MCR_Assessment | 17 | 1. ROOM INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦10
MCR | 11 | MCR_Assessment | 18 | 2. ROOM READINESS | SECTION | 2. ROOM READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦11
MCR | 12 | MCR_Assessment | 19 | 2. ROOM READINESS | HEADER | Room | Walls / 1-hr Rating | Ceiling | Floor / SDC | Penetrations | Access Control | Clearances | Housekeeping | Overall | Comments | MCR¦12
MCR | 13 | MCR_Assessment | 20 | 2. ROOM READINESS | DATA | 107 / MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | New MCR building requires final architectural envelope, rated walls/doors, roof/ceiling, floor finish, equipment clearances, row spacing, lighting coordination, grounding/bonding, and path separation. | MCR¦13
MCR | 14 | MCR_Assessment | 21 | 2. ROOM READINESS | DATA | 031 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Fiber Entrance Room 1 schedule requires confirmation of room naming, wall/backbox locations, penetration/firestop detail, rack/cabinet location and service provider interface. | MCR¦14
MCR | 15 | MCR_Assessment | 22 | 2. ROOM READINESS | DATA | MDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MDA racks must be installed with mandatory blank panels, bonding, overhead tray, fiber/copper routing and A/B side path separation. | MCR¦15
MCR | 16 | MCR_Assessment | 23 | 2. ROOM READINESS | DATA | HDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | HDA server cabinets require front/rear access, blanking panels, cooling airflow coordination, patch panel/LIU arrangement and clearance for future expansion. | MCR¦16
MCR | 17 | MCR_Assessment | 24 | 2. ROOM READINESS | DATA | Existing 107/137 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing equipment rooms/racks must remain operational until cutover. Verify active equipment inventory, PDUs, UPS sources, cable labels, and safe transfer pathway. | MCR¦17
MCR | 18 | MCR_Assessment | 25 | 2. ROOM READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦18
MCR | 19 | MCR_Assessment | 26 | 3. FIRE PROTECTION | SECTION | 3. FIRE PROTECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦19
MCR | 20 | MCR_Assessment | 27 | 3. FIRE PROTECTION | HEADER | Room | Sprinkler | Cage | Detector | Horn/Strobe | Extinguisher <75 ft | Firestop | Temp Firestop | Overall | Risk / Notes | MCR¦20
MCR | 21 | MCR_Assessment | 28 | 3. FIRE PROTECTION | DATA | 107 / MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCR has full fire protection scope including wet pipe and clean-agent fire suppression system. Verify preaction/clean-agent design, agent release interface, fire alarm matrix, detection, abort/release stations, room integrity and acceptance testing. | MCR¦21
MCR | 22 | MCR_Assessment | 29 | 3. FIRE PROTECTION | DATA | 031 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Verify fiber entrance room protection, rated penetrations, firestopping, detector/strobe coverage and no gaps after cable tray installation. | MCR¦22
MCR | 23 | MCR_Assessment | 30 | 3. FIRE PROTECTION | DATA | MDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify sprinkler/clean-agent coverage around MDA equipment, fire alarm devices, rack clearance and final firestop assemblies. | MCR¦23
MCR | 24 | MCR_Assessment | 31 | 3. FIRE PROTECTION | DATA | HDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify clean-agent coverage, detector placement, alarm interfaces, and open cabinet airflow protection. | MCR¦24
MCR | 25 | MCR_Assessment | 32 | 3. FIRE PROTECTION | DATA | Existing 107/137 | Verify | N/A | Verify | Verify | Verify | Verify | Verify | Verify | Existing systems must remain protected during temporary fiber, umbilical cord and core relocation work. Verify no impairment without approved fire watch/impairment plan. | MCR¦25
MCR | 26 | MCR_Assessment | 33 | 3. FIRE PROTECTION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦26
MCR | 27 | MCR_Assessment | 34 | 4. HVAC / COOLING | SECTION | 4. HVAC / COOLING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦27
MCR | 28 | MCR_Assessment | 35 | 4. HVAC / COOLING | HEADER | Room | Dedicated Unit | Capacity Verified | Emergency Power | Controls / BACnet | Condensate Routed | High Temp Alarm | 24/7 Operation | Overall | Risk / Notes | MCR¦28
MCR | 29 | MCR_Assessment | 36 | 4. HVAC / COOLING | DATA | 107 / MCR | CRAC units / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Telecom notes call for indoor computer room air conditioner (CRAC) units tied to building management system. Mechanical sheets included; verify redundant capacity, setpoints, humidity, condensate, controls, alarms and emergency power. | MCR¦29
MCR | 30 | MCR_Assessment | 37 | 4. HVAC / COOLING | DATA | UPS-A / UPS-B | Dedicated cooling / verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | UPS rooms/equipment require thermal load validation, ventilation, emergency power and alarm integration. Verify battery/UPS environmental requirements. | MCR¦30
MCR | 31 | MCR_Assessment | 38 | 4. HVAC / COOLING | DATA | MDA-A/B | CRAC-served MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify airflow/cold aisle/hot aisle assumptions, blanking panels, floor/ceiling distribution and temperature monitoring. | MCR¦31
MCR | 32 | MCR_Assessment | 39 | 4. HVAC / COOLING | DATA | HDA-A/B | CRAC-served MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Server cabinets and patch fields require stable 24/7 cooling and monitoring. Confirm no local hot spots at dense LIU/patch panel zones. | MCR¦32
MCR | 33 | MCR_Assessment | 40 | 4. HVAC / COOLING | DATA | Existing 107/137 | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | During split-core temporary phase, existing MCR/server equipment remains active. Verify existing cooling remains in service until cutover and decommissioning are complete. | MCR¦33
MCR | 34 | MCR_Assessment | 41 | 4. HVAC / COOLING | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦34
MCR | 35 | MCR_Assessment | 42 | 5. ELECTRICAL / UPS | SECTION | 5. ELECTRICAL / UPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦35
MCR | 36 | MCR_Assessment | 43 | 5. ELECTRICAL / UPS | HEADER | Room | UPS Installed | UPS Size | PDU Installed | Rack Receptacles | Panel Assigned | Emergency Source | SPD / Labeling | Overall | Notes | MCR¦36
MCR | 37 | MCR_Assessment | 44 | 5. ELECTRICAL / UPS | DATA | 107 / MCR | UPS-A / UPS-B | Verify | Verify | Verify | MCRE-401/402/403/601/701/702 | Verify | Verify | Verify | Electrical set includes site plan, enlarged MCR plans, one-lines and schedules. Verify switchboard/service, ATS/generator integration, normal/emergency/UPS distribution, grounding, lightning protection, SPD, load measurements and commissioning. | MCR¦37
MCR | 38 | MCR_Assessment | 45 | 5. ELECTRICAL / UPS | DATA | MDA-A/B | Verify | Rack/PDU dependent | Verify | Verify | MCR telecom panels / verify | Verify | Verify | Verify | MDA rack elevations include new 4-post floor cabinets, LIUs and network elements. Verify redundant A/B power feeds and PDU arrangements. | MCR¦38
MCR | 39 | MCR_Assessment | 46 | 5. ELECTRICAL / UPS | DATA | HDA-A/B | Verify | Cabinet/PDU dependent | Verify | Verify | MCR telecom/UPS panels / verify | Verify | Verify | Verify | HDA cabinets include server cabinet front/rear elevations with patch panels and active equipment. Confirm A/B feed separation, PDU mounting, load capacity and labels. | MCR¦39
MCR | 40 | MCR_Assessment | 47 | 5. ELECTRICAL / UPS | DATA | Existing 107/137 | Existing / Verify | Existing rack UPS/PDU | Existing / Verify | Verify | Existing / verify | Verify | Verify | Verify | Existing rack elevations identify multiple APC/Chatsworth/HP PDUs, APC Smart UPS and Eaton 9PX units. Verify what transfers, what stays, and temporary power during migration. | MCR¦40
MCR | 41 | MCR_Assessment | 48 | 5. ELECTRICAL / UPS | DATA | Site / Utility | Verify | N/A | N/A | N/A | MCRES / MCRE site one-line | Verify | Verify | Verify | New MCR is standalone critical infrastructure. Verify utility service, generator/ATS paths, emergency distribution, grounding electrode and ductbank/site electrical coordination. | MCR¦41
MCR | 42 | MCR_Assessment | 49 | 5. ELECTRICAL / UPS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦42
MCR | 43 | MCR_Assessment | 50 | 6. TELECOMMUNICATIONS | SECTION | 6. TELECOMMUNICATIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦43
MCR | 44 | MCR_Assessment | 51 | 6. TELECOMMUNICATIONS | HEADER | Room | Rack Installed | Ladder Tray | Fiber Installed | Grounding | Labeling | Testing | VA Acceptance | Overall | Notes | MCR¦44
MCR | 45 | MCR_Assessment | 52 | 6. TELECOMMUNICATIONS | DATA | 107 / MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-101 shows new MCR with MDA-A/B, HDA-A/B, UPS-A/B, cameras and fiber path legend. MCRT-701 shows 10 WAO total, 720 WAO available, 98.1% expansion capacity, 10 total ports with 20% allowance and 359 ft cable tray. | MCR¦45
MCR | 46 | MCR_Assessment | 53 | 6. TELECOMMUNICATIONS | DATA | 031 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-701 Data Device and Circuit Schedule - Fiber Entrance Room 1: outlets 31-A/B/C/D plus security devices 07-CAM-03/04/07/08/11; Rack ID TR01-031-1. | MCR¦46
MCR | 47 | MCR_Assessment | 54 | 6. TELECOMMUNICATIONS | DATA | MDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-607: MDA A/B racks contain horizontal distribution LIUs, hybrid FOC, 48x Cat6A to HDA, and reserved LAN/spine/aggregation elements. Maintain A/B path separation. | MCR¦47
MCR | 48 | MCR_Assessment | 55 | 6. TELECOMMUNICATIONS | DATA | HDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-608/609: HDA A/B include 48-port Cat6A patch panels, HD fiber LIUs, backbone side A/B LIU and server cabinet arrangements. | MCR¦48
MCR | 49 | MCR_Assessment | 56 | 6. TELECOMMUNICATIONS | DATA | Existing 107/137 | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Verify | Existing MCR rows 1-3 and B61 server cabinet transfer references are extensive. Maintain service using temporary fiber/umbilical cords and phased core relocation. | MCR¦49
MCR | 50 | MCR_Assessment | 57 | 6. TELECOMMUNICATIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦50
MCR | 51 | MCR_Assessment | 58 | 7. SECURITY / PACS / CCTV | SECTION | 7. SECURITY / PACS / CCTV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦51
MCR | 52 | MCR_Assessment | 59 | 7. SECURITY / PACS / CCTV | HEADER | Room | PACS | Card Reader | Door Position | Electric Strike | CCTV | Motion Sensor | Integration | Overall | Notes | MCR¦52
MCR | 53 | MCR_Assessment | 60 | 7. SECURITY / PACS / CCTV | DATA | 107 / MCR | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-101 identifies cameras 07-CAM-01 through 07-CAM-12 around the MCR. Telecom notes call for IP-addressable network cameras integrated into existing VMS and PACS/access-control systems including iSTAR Edge/Avigilon ACM controller. | MCR¦53
MCR | 54 | MCR_Assessment | 61 | 7. SECURITY / PACS / CCTV | DATA | 031 | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | MCRT-701 includes security camera/data devices assigned to TR01-031-1. Confirm camera IDs, mounting, cabling, and VMS commissioning. | MCR¦54
MCR | 55 | MCR_Assessment | 62 | 7. SECURITY / PACS / CCTV | DATA | MDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify camera coverage, door/access points, VMS monitoring and access control zones for critical equipment. | MCR¦55
MCR | 56 | MCR_Assessment | 63 | 7. SECURITY / PACS / CCTV | DATA | HDA-A/B | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify coverage of HDA cabinets, doors, motion detection and any lockable cabinet/security requirements. | MCR¦56
MCR | 57 | MCR_Assessment | 64 | 7. SECURITY / PACS / CCTV | DATA | Existing 107/137 | Existing / Verify | Existing / Verify | Existing / Verify | Existing / Verify | Verify | Verify | Verify | Verify | Existing security systems must remain functional during transition; protect existing camera angles and access controls until final turnover. | MCR¦57
MCR | 58 | MCR_Assessment | 65 | 7. SECURITY / PACS / CCTV | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦58
MCR | 59 | MCR_Assessment | 66 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦59
MCR | 60 | MCR_Assessment | 67 | 8. OWNER RISKS | HEADER | Risk ID | Room | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | MCR¦60
MCR | 61 | MCR_Assessment | 68 | 8. OWNER RISKS | DATA | MCR-R1 | All | MCR is a new standalone critical facility with 120-sheet multi-discipline scope | Critical | Medium | 8 | Use discipline-by-discipline pre-install checklist, coordination drawings, third-party inspections and commissioning tracker | GCC / VA / Cx | Closed | New MCR cannot depend on another project or funding source to be usable. | MCR¦61
MCR | 62 | MCR_Assessment | 69 | 8. OWNER RISKS | DATA | MCR-R2 | Existing 107/137 | Existing MCR/server/core equipment transfer may interrupt hospital network operations | Critical | Medium | 8 | Require detailed OIT cutover plan, temporary fiber/umbilicals, rollback plan, VA activation windows and after-hours phasing | OIT / Telecom | Closed | Notes state MCR activation may need 3-6 months and WAO activation depends on fiber/core connections. | MCR¦62
MCR | 63 | MCR_Assessment | 70 | 8. OWNER RISKS | DATA | MCR-R3 | MDA/HDA | A/B fiber path diversity and backbone commissioning not verified | Critical | Medium | 8 | Verify OSP/ISP Path A/B routing, no intermediate splices, test results, labeling and geographic diversity | Telecom / OIT | Closed | New fiber risers require A-side and B-side redundant paths to every TR. | MCR¦63
MCR | 64 | MCR_Assessment | 71 | 8. OWNER RISKS | DATA | MCR-R4 | MCR / UPS | UPS-A/B, ATS/generator, panel source and PDU coordination could delay activation | Critical | Medium | 8 | Verify one-line, load banks, breaker settings, panel labels, generator/ATS tests, UPS start-up and A/B power mapping | Electrical / Cx | Closed | Electrical scope includes site electrical, enlarged MCR plans, one-lines and schedules. | MCR¦64
MCR | 65 | MCR_Assessment | 72 | 8. OWNER RISKS | DATA | MCR-R5 | MCR | CRAC capacity, redundancy, condensate, BMS/FMS alarms and emergency power not verified | Critical | Medium | 8 | Confirm mechanical schedules, CRAC start-up, controls, alarm points, emergency source, environmental monitoring and hot/cold aisle performance | Mechanical / Cx | Closed | Telecom notes explicitly call for indoor computer room air conditioner CRAC units and BMS coordination. | MCR¦65
MCR | 66 | MCR_Assessment | 73 | 8. OWNER RISKS | DATA | MCR-R6 | MCR | Clean-agent/preaction/fire alarm interface and room integrity acceptance risk | Critical | Medium | 8 | Track clean-agent calculations, room integrity test, release/abort stations, FA matrix, sprinkler/preaction tests and AHJ/third-party acceptance | FP / FA / Cx | Closed | MCR receives new fire alarm and clean-agent fire suppression system. | MCR¦66
MCR | 67 | MCR_Assessment | 74 | 8. OWNER RISKS | DATA | MCR-R7 | MCR / Site | Civil/site/utility ductbank, drainage, grading and security envelope could affect substantial completion | High | Medium | 6 | Track civil utility plan, stormwater, grading, ductbank, site fiber conduit encasement, access and landscape/hardscape restoration | Civil / Site / GC | Closed | MCR package includes civil, structural and architectural site work. | MCR¦67
MCR | 68 | MCR_Assessment | 75 | 8. OWNER RISKS | DATA | MCR-R8 | All | Commissioning/turnover package may be incomplete across all divisions | High | Medium | 6 | Maintain MCR-specific turnover matrix for electrical, mechanical, FP, FA, telecom, security, civil, structural and architectural systems | GC / Cx Manager | Closed | General notes require commissioning/recommissioning, third-party inspections and written reports. | MCR¦68
MCR | 69 | MCR_Assessment | 76 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦69
MCR | 70 | MCR_Assessment | 77 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦70
MCR | 71 | MCR_Assessment | 78 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | MCR¦71
MCR | 72 | MCR_Assessment | 79 | 9. OPEN QUESTIONS | DATA | MCR-Q1 | Confirm final room naming and PMIS mapping: MCR Room 107, Fiber Entrance Room 031, Existing 107/137 server/MCR references. | VA / OIT / Designer | Closed | 0 | 0 | Room inventory and turnover mapping could be wrong | 0 | 0 | 0 | MCR¦72
MCR | 73 | MCR_Assessment | 80 | 9. OPEN QUESTIONS | DATA | MCR-Q2 | What existing core/server/rack equipment is being relocated from the existing MCR/server rooms, and what remains? | OIT / Contractor | Closed | 0 | 0 | Cutover and outage risk | 0 | 0 | 0 | MCR¦73
MCR | 74 | MCR_Assessment | 81 | 9. OPEN QUESTIONS | DATA | MCR-Q3 | What is the approved MCR activation sequence and required VA/OIT hold points? | VA / OIT / COR | Closed | 0 | 0 | Schedule/cutover impact | 0 | 0 | General phasing notes mention 3-6 month MCR activation and split core operation. | MCR¦74
MCR | 75 | MCR_Assessment | 82 | 9. OPEN QUESTIONS | DATA | MCR-Q4 | Are UPS-A/B, generator/ATS and emergency power paths commissioned and mapped to each rack/PDU? | Electrical / Cx | Closed | 0 | 0 | Electrical readiness unknown | 0 | 0 | 0 | MCR¦75
MCR | 76 | MCR_Assessment | 83 | 9. OPEN QUESTIONS | DATA | MCR-Q5 | Are CRAC units fully commissioned with BMS/FMS alarms, redundancy and emergency power? | Mechanical / Cx | Closed | 0 | 0 | Cooling continuity risk | 0 | 0 | 0 | MCR¦76
MCR | 77 | MCR_Assessment | 84 | 9. OPEN QUESTIONS | DATA | MCR-Q6 | Are clean-agent/preaction/fire alarm systems fully designed, tested and accepted? | FP / FA / AHJ | Closed | 0 | 0 | Life-safety acceptance risk | 0 | 0 | 0 | MCR¦77
MCR | 78 | MCR_Assessment | 85 | 9. OPEN QUESTIONS | DATA | MCR-Q7 | Are redundant Path A/B fiber routes geographically diverse, tested, labeled and accepted? | Telecom / OIT | Closed | 0 | 0 | Backbone redundancy risk | 0 | 0 | 0 | MCR¦78
MCR | 79 | MCR_Assessment | 86 | 9. OPEN QUESTIONS | DATA | MCR-Q8 | Which third-party inspections, commissioning reports and OIT validation records are required before turnover/activation? | GC / Cx Manager / OIT | Closed | 0 | 0 | Turnover package gap | 0 | 0 | 0 | MCR¦79
MCR | 80 | MCR_Assessment | 87 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦80
MCR | 81 | MCR_Assessment | 88 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦81
MCR | 82 | MCR_Assessment | 89 | 10. PHOTO LOG | HEADER | Photo ID | Room | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | MCR¦82
MCR | 83 | MCR_Assessment | 90 | 10. PHOTO LOG | DATA | MCR-P001 | MCR 107 | Existing / New Condition | Full room envelope, doors, rated walls, ceiling/roof, floors, row layout, UPS-A/B, MDA/HDA, access points and cameras | 0 | Paul | 0 | MCR-R1/MCR-R6 | Closed | 0 | MCR¦83
MCR | 84 | MCR_Assessment | 91 | 10. PHOTO LOG | DATA | MCR-P002 | 031 | Fiber Entrance | Fiber Entrance Room 1, outlet locations 31-A/B/C/D, rack/cabinet location, sleeve/firestop and service entrance pathways | 0 | Paul | 0 | MCR-R3 | Closed | 0 | MCR¦84
MCR | 85 | MCR_Assessment | 92 | 10. PHOTO LOG | DATA | MCR-P003 | MDA-A/B | Rack / Fiber | MDA-A1/A2/A3 and MDA-B1/B2/B3 rack fronts/rears, LIUs, hybrid FOC, Cat6A to HDA, grounding and cable management | 0 | Paul | 0 | MCR-R3/MCR-R4 | Closed | 0 | MCR¦85
MCR | 86 | MCR_Assessment | 93 | 10. PHOTO LOG | DATA | MCR-P004 | HDA-A/B | Rack / Server Cabinets | HDA-A1/HDA-B1 front/rear, patch panels, HD LIUs, cabinet blanking panels, server cabinet airflow and labels | 0 | Paul | 0 | MCR-R3/MCR-R5 | Closed | 0 | MCR¦86
MCR | 87 | MCR_Assessment | 94 | 10. PHOTO LOG | DATA | MCR-P005 | Existing 107/137 | Existing Equipment | Existing rows 1-3 and B61 server cabinet transfer equipment, Cisco core, WAN aggregation, NetScout, Canoga, Ortronics, LIUs, UPS/PDU labels | 0 | Paul | 0 | MCR-R2 | Closed | 0 | MCR¦87
MCR | 88 | MCR_Assessment | 95 | 10. PHOTO LOG | DATA | MCR-P006 | MCR / Electrical | Electrical / UPS | UPS-A/B, switchboards, panels, ATS, generator tie, PDUs, rack receptacles, grounding, SPDs and load measurement labels | 0 | Paul | 0 | MCR-R4 | Closed | 0 | MCR¦88
MCR | 89 | MCR_Assessment | 96 | 10. PHOTO LOG | DATA | MCR-P007 | MCR / Mechanical | HVAC / Controls | CRAC units, condensate, controls/BACnet/BMS/FMS points, alarms, environmental monitoring and emergency power source | 0 | Paul | 0 | MCR-R5 | Closed | 0 | MCR¦89
MCR | 90 | MCR_Assessment | 97 | 10. PHOTO LOG | DATA | MCR-P008 | MCR / Life Safety | Fire / Security | Clean-agent cylinders/piping/nozzles, preaction/sprinkler, fire alarm, release/abort devices, cameras 07-CAM series, PACS/controller and door hardware | 0 | Paul | 0 | MCR-R6/MCR-R8 | Closed | 0 | MCR¦90
MCR | 91 | MCR_Assessment | 98 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR¦91
SITE | 1 | SITE_Assesment | 8 | 1. SITE ROUTE INVENTORY | SECTION | 1. SITE ROUTE INVENTORY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦1
SITE | 2 | SITE_Assesment | 9 | 1. SITE ROUTE INVENTORY | HEADER | Area / Segment | Buildings / Nodes | Path | Primary Scope | Handholes / Structures | Conduit / Ductbank | Status | Drawing Ref | Station / Length | Notes | SITE¦2
SITE | 3 | SITE_Assesment | 10 | 1. SITE ROUTE INVENTORY | DATA | Overall Site | Campus-wide / MCR / all EHRM buildings | Path A & B | Redundant site fiber backbone | THH #1-#19, communication manholes, concrete pullboxes | 4-inch PVC conduit in concrete ductbank; direct-bury communication conduit where noted | Verify | TS100 / T-601 / G-000 | Campus wide | New site fiber conduit must be concrete encased. Base bid is trenching with concrete ductbank and hand digging at existing utility crossings; directional boring requires Government approval. | SITE¦3
SITE | 4 | SITE_Assesment | 11 | 1. SITE ROUTE INVENTORY | DATA | B12 to B16 | B12 / B16 | Path A & B | Telecom plan and profile | THH #15-#19 | 2x4-inch PVC concrete ductbank | Verify | TS201 | 00+00 to 7+91.21 | Plan/profile shows B12 to B16 route with vertical ductbank angle transitions and concrete ductbank notes. | SITE¦4
SITE | 5 | SITE_Assesment | 12 | 1. SITE ROUTE INVENTORY | DATA | B1 to B70 | B1 / B70 backbone segment | Path A & B | Telecom plan and profile | THH #1-#7 plus pullbox | 2x4-inch and 4x4-inch PVC concrete ductbank | Verify | TS202 / TS203 / TS207 | 00+00 to 15+92.04 | Long backbone route with multiple THHs, concrete pullbox, and B70/B81 branches. Confirm all utility crossings and trench restoration limits. | SITE¦5
SITE | 6 | SITE_Assesment | 13 | 1. SITE ROUTE INVENTORY | DATA | B20 / B22 | B20 / B22 | Path A & B | Telecom plan and profile | THH #2, #8-#12 | 2x4-inch PVC concrete ductbank | Verify | TS204 | B20 00+00 to 7+34.47; B22 00+00 to 1+98.18 | Route feeds Building 20 and 22. Confirm common ductbank has separate conduits for A/B path where shown. | SITE¦6
SITE | 7 | SITE_Assesment | 14 | 1. SITE ROUTE INVENTORY | DATA | B15 / B9 | B15 / B9 | Path A & B | Telecom plan and profile | THH #14-#18 | 2x4-inch PVC concrete ductbank | Verify | TS205 | B15 00+00 to 1+70.82; B9 00+00 to 2+01.32 | Route includes ductbank transitions and utility verification requirements. | SITE¦7
SITE | 8 | SITE_Assesment | 15 | 1. SITE ROUTE INVENTORY | DATA | B13 / B14 | B13 / B14 | Path A & B | Telecom plan and profile | THH #15-#17 | 2x4-inch PVC concrete ductbank | Verify | TS206 | B13 00+00 to 1+67.85; B14 00+00 to 1+79.01 | Coordinate with nearby B12/B16/B15 infrastructure and handhole locations. | SITE¦8
SITE | 9 | SITE_Assesment | 16 | 1. SITE ROUTE INVENTORY | DATA | B70 / B81 | B70 / B81 | Path A & B | Telecom plan and profile | THH #7 / #14 | 2x4-inch PVC concrete ductbank | Verify | TS207 | B70 15+52.38 to 15+92.04; B81 00+00 to 1+49.54 | B70/B81 extension from B1-B70 backbone; verify west-campus access and restoration. | SITE¦9
SITE | 10 | SITE_Assesment | 17 | 1. SITE ROUTE INVENTORY | DATA | B33 / B17 | B33 / B17 | B33 Path A & B / B17 Path A | Telecom plan and profile | THH #8, #10, #13 | 2x4-inch PVC concrete ductbank | Verify | TS208 | B33 00+00 to 0+78.16; B17 00+00 to 1+16.82 | B17 Path A only on this sheet; Path B appears on TS210. Ensure PMIS tracks both A and B legs. | SITE¦10
SITE | 11 | SITE_Assesment | 18 | 1. SITE ROUTE INVENTORY | DATA | B18 / B19 | B18 / B19 | B18 Path A / B19 Path A & B | Telecom plan and profile | THH #9 / #10 | 2x4-inch PVC concrete ductbank | Verify | TS209 | B18 00+00 to 0+36.94; B19 00+00 to 0+42.25 | B18 Path A only on this sheet; Path B appears on TS210. Verify B19 A/B separation and building penetration. | SITE¦11
SITE | 12 | SITE_Assesment | 19 | 1. SITE ROUTE INVENTORY | DATA | B81 / B17 to B01 / B18 | B81 / B17 / B01 / B18 | Path B | Telecom plan and profile | THH #7 / #13 | 2x4-inch PVC concrete ductbank | Verify | TS210 | B17 to B01 00+00 to 1+63.50; B18 00+00 to 0+87.25 | Completes B-path routing for B17 and B18 and B81/B17-to-B01 interconnection. Critical for redundancy verification. | SITE¦12
SITE | 13 | SITE_Assesment | 20 | 1. SITE ROUTE INVENTORY | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦13
SITE | 14 | SITE_Assesment | 21 | 2. SITE READINESS | SECTION | 2. SITE READINESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦14
SITE | 15 | SITE_Assesment | 22 | 2. SITE READINESS | HEADER | Scope Area | Survey / Layout | Utility Locate | Access / Traffic | Excavation Permit | Ductbank Forms | Inspection Hold | Restoration | Overall | Comments | SITE¦15
SITE | 16 | SITE_Assesment | 23 | 2. SITE READINESS | DATA | Campus Backbone | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Survey notes state utility locations are approximate and conditions may vary; contractor must provide utility location service before excavation and verify location/depth of all utilities. | SITE¦16
SITE | 17 | SITE_Assesment | 24 | 2. SITE READINESS | DATA | THH / Manholes | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Field verify THH #1-#19, communication manholes, existing manholes, locking covers, drainage, elevations and pull radius before ductbank install. | SITE¦17
SITE | 18 | SITE_Assesment | 25 | 2. SITE READINESS | DATA | Concrete Ductbank | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Trench must remain open until inspection of concrete duct. Confirm conduit quantity per T-601 and ductbank size/detail per T-501. | SITE¦18
SITE | 19 | SITE_Assesment | 26 | 2. SITE READINESS | DATA | Building Tie-ins | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Each building sheet T-101 and T-601 riser diagram are continuation references. Confirm sleeve/penetration, firestop, patching and building downtime coordination. | SITE¦19
SITE | 20 | SITE_Assesment | 27 | 2. SITE READINESS | DATA | Restoration / Site | Verify | Verify | Verify | Verify | N/A | Verify | Verify | Verify | Restore trench/sidewalk/asphalt/landscape to match existing. Maintain fire lanes, hydrants, access and pedestrian controls. | SITE¦20
SITE | 21 | SITE_Assesment | 28 | 2. SITE READINESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦21
SITE | 22 | SITE_Assesment | 29 | 3. FIRE / LIFE SAFETY / SITE ACCESS | SECTION | 3. FIRE / LIFE SAFETY / SITE ACCESS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦22
SITE | 23 | SITE_Assesment | 30 | 3. FIRE / LIFE SAFETY / SITE ACCESS | HEADER | Area | Fire Lane | Hydrants / FDC | Egress | Temp Barriers | Hot Work | Impairment | Fire Watch | Overall | Risk / Notes | SITE¦23
SITE | 24 | SITE_Assesment | 31 | 3. FIRE / LIFE SAFETY / SITE ACCESS | DATA | Campus Work Areas | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | General notes require fire lanes, hydrants and fire department access roads operational at all times; maintain egress and provide fire watch/temporary protection when required. | SITE¦24
SITE | 25 | SITE_Assesment | 32 | 3. FIRE / LIFE SAFETY / SITE ACCESS | DATA | Trenching / Excavation | Verify | Verify | Verify | Verify | N/A | N/A | Verify | Verify | Trench barricades, accessible parking/public access and right-of-way impacts must be coordinated with owner prior to construction. | SITE¦25
SITE | 26 | SITE_Assesment | 33 | 3. FIRE / LIFE SAFETY / SITE ACCESS | DATA | Building Penetrations | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Rated wall/floor penetrations must be firestopped; temporary firestopping required if penetrations remain open between shifts. | SITE¦26
SITE | 27 | SITE_Assesment | 34 | 3. FIRE / LIFE SAFETY / SITE ACCESS | DATA | MCR / Critical Backbone | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Backbone work affects facility operations. Any required shutdowns must be limited to one at a time and coordinated with approved phasing plan. | SITE¦27
SITE | 28 | SITE_Assesment | 35 | 3. FIRE / LIFE SAFETY / SITE ACCESS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦28
SITE | 29 | SITE_Assesment | 36 | 4. CIVIL / DUCTBANK / RESTORATION | SECTION | 4. CIVIL / DUCTBANK / RESTORATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦29
SITE | 30 | SITE_Assesment | 37 | 4. CIVIL / DUCTBANK / RESTORATION | HEADER | Segment | Excavation Method | Ductbank Type | Concrete / Backfill | Structures | Profile Verified | Restoration | Testing / Inspection | Overall | Risk / Notes | SITE¦30
SITE | 31 | SITE_Assesment | 38 | 4. CIVIL / DUCTBANK / RESTORATION | DATA | All New Site Fiber | Trenching base bid | Concrete encased conduit | Verify | THH / manholes / pullboxes | Verify | Verify | Verify | Verify | General notes require all utilities installed with this project to be in concrete ductbank; directional boring must be approved by Government. | SITE¦31
SITE | 32 | SITE_Assesment | 39 | 4. CIVIL / DUCTBANK / RESTORATION | DATA | B1-B70 Backbone | Trench / hand dig at crossings | 2x4 and 4x4 PVC ductbank | Verify | THH #1-#7 / pullbox | Verify | Verify | Verify | Verify | Longest route and highest exposure to existing utilities and surface restoration. | SITE¦32
SITE | 33 | SITE_Assesment | 40 | 4. CIVIL / DUCTBANK / RESTORATION | DATA | B12-B16 / South/East Branches | Trench / hand dig at crossings | 2x4 PVC ductbank | Verify | THH #15-#19 | Verify | Verify | Verify | Verify | Verify vertical ductbank angles and utility crossing depths before concrete placement. | SITE¦33
SITE | 34 | SITE_Assesment | 41 | 4. CIVIL / DUCTBANK / RESTORATION | DATA | B20/B22/B33/B17/B18/B19 | Trench / hand dig at crossings | 2x4 PVC ductbank | Verify | THH #8-#13 | Verify | Verify | Verify | Verify | Dense campus area with multiple building tie-ins; coordinate outages and building access. | SITE¦34
SITE | 35 | SITE_Assesment | 42 | 4. CIVIL / DUCTBANK / RESTORATION | DATA | Restoration | Match existing | N/A | Concrete/asphalt/landscape | N/A | N/A | Verify | Verify | Verify | T-501 details include trenching, concrete edge, pullbox, locking cover and concrete mix details. Confirm patch widths, tie bars and replacement limits. | SITE¦35
SITE | 36 | SITE_Assesment | 43 | 4. CIVIL / DUCTBANK / RESTORATION | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦36
SITE | 37 | SITE_Assesment | 44 | 5. ELECTRICAL / SITE UTILITIES | SECTION | 5. ELECTRICAL / SITE UTILITIES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦37
SITE | 38 | SITE_Assesment | 45 | 5. ELECTRICAL / SITE UTILITIES | HEADER | Area | Electrical Conflict | Telecom Conflict | Storm/Sanitary Conflict | Utility Locate | Grounding/Bonding | Site Lighting | Power Source | Overall | Notes | SITE¦38
SITE | 39 | SITE_Assesment | 46 | 5. ELECTRICAL / SITE UTILITIES | DATA | Overall Site | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Electrical site plans ES101/ES401 are included. Existing utility locations are approximate; coordinate electrical vaults, underground electrical, storm drain manholes and sanitary manholes. | SITE¦39
SITE | 40 | SITE_Assesment | 47 | 5. ELECTRICAL / SITE UTILITIES | DATA | THH / Manholes | Verify | Verify | Verify | Verify | Verify | N/A | N/A | Verify | Locking covers and handhole/manhole locations must be field verified. Confirm bonding/grounding requirements where metallic components are present. | SITE¦40
SITE | 41 | SITE_Assesment | 48 | 5. ELECTRICAL / SITE UTILITIES | DATA | MCR / Provider Entrance | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | T-601 shows WAN/provider fiber entrances and new fiber Path A/B to the MCR. Coordinate with Century Link/service provider and MCR activation. | SITE¦41
SITE | 42 | SITE_Assesment | 49 | 5. ELECTRICAL / SITE UTILITIES | DATA | Building Tie-ins | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Coordinate conduit penetrations with building electrical/telecom/firestop scope and avoid conflicts with existing services. | SITE¦42
SITE | 43 | SITE_Assesment | 50 | 5. ELECTRICAL / SITE UTILITIES | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦43
SITE | 44 | SITE_Assesment | 51 | 6. TELECOMMUNICATIONS / FIBER | SECTION | 6. TELECOMMUNICATIONS / FIBER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦44
SITE | 45 | SITE_Assesment | 52 | 6. TELECOMMUNICATIONS / FIBER | HEADER | Scope | Path A | Path B | Fiber Type | Conduit Separation | Riser / Continuation | Testing | VA Acceptance | Overall | Notes | SITE¦45
SITE | 46 | SITE_Assesment | 53 | 6. TELECOMMUNICATIONS / FIBER | DATA | Campus Backbone | Verify | Verify | 24F OS2 10GB to each TR/building | Separate conduit where common ductbank shown | T-601 / building T-101 sheets | Verify | Verify | Verify | Legend identifies new fiber in A route, B route, and A+B routes in separate conduits. Confirm no cross-connect gaps at THHs/manholes. | SITE¦46
SITE | 47 | SITE_Assesment | 54 | 6. TELECOMMUNICATIONS / FIBER | DATA | MCR Provider / WAN | Verify | Verify | 48F OS2 temporary and provider extension noted | Verify | T-601 / MCR sheets | Verify | Verify | Verify | Site one-line shows WAN fiber from service provider and temporary/provider extension pathways. Coordinate with MCR activation and OIT. | SITE¦47
SITE | 48 | SITE_Assesment | 55 | 6. TELECOMMUNICATIONS / FIBER | DATA | Building Drops | Verify | Verify | 24F OS2 to each TR in each building | Verify | Building T-101 and T-601 | Verify | Verify | Verify | Each building tie-in must be tested, labeled, and accepted before connection to active operations. | SITE¦48
SITE | 49 | SITE_Assesment | 56 | 6. TELECOMMUNICATIONS / FIBER | DATA | THH Network | Verify | Verify | Varies by segment | Verify | T-601 | Verify | Verify | Verify | T-601 one-line lists THH #1-#19 and path counts such as 6 Path A + 4 Path B, 6 Path A + 6 Path B, 7 Path A + 7 Path B, 5 Path A + 4 Path B, and 9 Path A + 7 Path B. | SITE¦49
SITE | 50 | SITE_Assesment | 57 | 6. TELECOMMUNICATIONS / FIBER | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦50
SITE | 51 | SITE_Assesment | 58 | 7. SECURITY / SITE CONTROL | SECTION | 7. SECURITY / SITE CONTROL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦51
SITE | 52 | SITE_Assesment | 59 | 7. SECURITY / SITE CONTROL | HEADER | Area | Access Control | Barricades | Traffic Control | Pedestrian Control | After-hours Work | VA Escort | Public Impact | Overall | Notes | SITE¦52
SITE | 53 | SITE_Assesment | 60 | 7. SECURITY / SITE CONTROL | DATA | Campus Site Work | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Coordinate staging, access, material storage, noisy work, utility interruption, trench barricades and public access with owner. | SITE¦53
SITE | 54 | SITE_Assesment | 61 | 7. SECURITY / SITE CONTROL | DATA | Road / Parking Impacts | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | General notes specifically identify accessible parking and public right-of-way impacts; temporary barricades must prevent injury and protect parking signage. | SITE¦54
SITE | 55 | SITE_Assesment | 62 | 7. SECURITY / SITE CONTROL | DATA | Critical Utility Crossings | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Verify | Hand digging at existing utility crossings is in base bid. Confirm permits, Dig Safe, VA utility locate and escort requirements before excavation. | SITE¦55
SITE | 56 | SITE_Assesment | 63 | 7. SECURITY / SITE CONTROL | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦56
SITE | 57 | SITE_Assesment | 64 | 8. OWNER RISKS | SECTION | 8. OWNER RISKS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦57
SITE | 58 | SITE_Assesment | 65 | 8. OWNER RISKS | HEADER | Risk ID | Area | Risk | Impact | Probability | Score | Mitigation | Owner | Status | Notes | SITE¦58
SITE | 59 | SITE_Assesment | 66 | 8. OWNER RISKS | DATA | SITE-R1 | All | Existing utility locations are approximate and field conditions may vary from survey | Critical | High | 9 | Complete utility locate, GPR review, potholing/hand-digging at crossings and VA utility coordination before excavation | GC / Civil / VA | Closed | Multiple sheets repeat that survey conditions may vary and utility location service is required prior to excavation. | SITE¦59
SITE | 60 | SITE_Assesment | 67 | 8. OWNER RISKS | DATA | SITE-R2 | All | A/B fiber path separation may not be maintained through common ductbank or congested areas | Critical | Medium | 8 | Verify separate conduits, route diversity, THH labels, T-601 path counts and as-built documentation | Telecom / OIT | Closed | Legend allows A+B in common ductbank but separate conduits; redundancy must be validated. | SITE¦60
SITE | 61 | SITE_Assesment | 68 | 8. OWNER RISKS | DATA | SITE-R3 | All | Concrete ductbank could be backfilled before inspection | High | Medium | 6 | Establish inspection hold point; trench remains open until concrete duct inspection and photos are accepted | GC / QA / COR | Closed | Site notes state trench to remain open until inspection of concrete duct. | SITE¦61
SITE | 62 | SITE_Assesment | 69 | 8. OWNER RISKS | DATA | SITE-R4 | MCR / Provider | WAN/provider fiber and MCR activation sequence could delay campus cutover | Critical | Medium | 8 | Coordinate Century Link/service provider, temporary fiber, provider extension, MCR readiness and OIT activation plan | OIT / Telecom | Closed | T-601 references WAN fiber, temporary fiber and provider extension. | SITE¦62
SITE | 63 | SITE_Assesment | 70 | 8. OWNER RISKS | DATA | SITE-R5 | Roads / Parking / Pedestrian Areas | Trenching/restoration may disrupt accessible parking, fire lanes, public access and campus traffic | High | Medium | 6 | Submit traffic/pedestrian/staging plan, maintain fire lanes/hydrants and restore surfaces to match existing | GC / Site | Closed | General notes require coordination with owner and protection of accessible parking/public access. | SITE¦63
SITE | 64 | SITE_Assesment | 71 | 8. OWNER RISKS | DATA | SITE-R6 | All Building Tie-ins | Building entry penetrations/firestopping may not align with building PMIS packages | High | Medium | 6 | Cross-check every site tie-in against building assessment, T-101 continuation sheets and firestop photos | Telecom / Firestop / QA | Closed | Every building continuation references building T-101 and T-601. | SITE¦64
SITE | 65 | SITE_Assesment | 72 | 8. OWNER RISKS | DATA | SITE-R7 | Civil Restoration | Asphalt/concrete/landscape restoration quantities and limits may be underestimated | Medium | Medium | 4 | Verify trench patch details, tie bars, concrete/asphalt specs, landscape protection and final surface restoration photo log | GC / Civil | Closed | T-501 includes trenching/restoration details and concrete requirements. | SITE¦65
SITE | 66 | SITE_Assesment | 73 | 8. OWNER RISKS | DATA | SITE-R8 | Commissioning / Turnover | Fiber testing, labels, as-builts and site utility commissioning may be incomplete | High | Medium | 6 | Track OTDR/power meter tests, conduit as-builts, THH labels, route photos, redlines, third-party inspections and VA/OIT acceptance | GC / Cx / OIT | Closed | Commissioning and third-party inspection requirements apply to site utilities and communications. | SITE¦66
SITE | 67 | SITE_Assesment | 74 | 8. OWNER RISKS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦67
SITE | 68 | SITE_Assesment | 75 | 9. OPEN QUESTIONS | SECTION | 9. OPEN QUESTIONS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦68
SITE | 69 | SITE_Assesment | 76 | 9. OPEN QUESTIONS | HEADER | Question ID | Question | Assigned To | Status | Needed By | Answer / Resolution | Impact if Unanswered | Follow-up | Date Closed | Notes | SITE¦69
SITE | 70 | SITE_Assesment | 77 | 9. OPEN QUESTIONS | DATA | SITE-Q1 | Confirm final list of all site fiber buildings and whether Buildings 1-22, 33, 61, 62, 70, 78/78A, 80, 81, 82, Crescent House and MCR are included in one site backbone turnover package. | VA / OIT / Designer | Closed | 0 | 0 | Scope and turnover package mapping unclear | 0 | 0 | 0 | SITE¦70
SITE | 71 | SITE_Assesment | 78 | 9. OPEN QUESTIONS | DATA | SITE-Q2 | Which THH/manhole numbers are new versus existing, and which require locking cover replacement only? | Telecom / Civil | Closed | 0 | 0 | Structure inventory and inspection scope unclear | 0 | 0 | 0 | SITE¦71
SITE | 72 | SITE_Assesment | 79 | 9. OPEN QUESTIONS | DATA | SITE-Q3 | Are all A and B routes physically diverse enough and in separate conduit wherever common ductbank is used? | OIT / Designer | Closed | 0 | 0 | Redundancy risk | 0 | 0 | 0 | SITE¦72
SITE | 73 | SITE_Assesment | 80 | 9. OPEN QUESTIONS | DATA | SITE-Q4 | What are the approved utility-locate/potholing requirements before excavation at each crossing? | GC / VA / Civil | Closed | 0 | 0 | Utility strike risk | 0 | 0 | 0 | SITE¦73
SITE | 74 | SITE_Assesment | 81 | 9. OPEN QUESTIONS | DATA | SITE-Q5 | What inspection hold points are required for ductbank forms, conduit placement, concrete pour, pull string, mandrel and backfill? | QA / COR / Civil | Closed | 0 | 0 | QA acceptance risk | 0 | 0 | 0 | SITE¦74
SITE | 75 | SITE_Assesment | 82 | 9. OPEN QUESTIONS | DATA | SITE-Q6 | Are directional boring alternatives allowed anywhere, or is all base-bid work trenching unless separately approved by Government? | VA / COR | Closed | 0 | 0 | Means/methods and cost/schedule risk | 0 | 0 | 0 | SITE¦75
SITE | 76 | SITE_Assesment | 83 | 9. OPEN QUESTIONS | DATA | SITE-Q7 | What exact fiber test package is required for each path and building tie-in before connection to active operations? | OIT / Telecom / Cx | Closed | 0 | 0 | Acceptance/activation risk | 0 | 0 | 0 | SITE¦76
SITE | 77 | SITE_Assesment | 84 | 9. OPEN QUESTIONS | DATA | SITE-Q8 | How will MCR/provider temporary fiber, new fiber and campus building activation be sequenced to limit shutdowns to one at a time? | OIT / GC / COR | Closed | 0 | 0 | Operational outage risk | 0 | 0 | 0 | SITE¦77
SITE | 78 | SITE_Assesment | 85 | 9. OPEN QUESTIONS | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦78
SITE | 79 | SITE_Assesment | 86 | 10. PHOTO LOG | SECTION | 10. PHOTO LOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦79
SITE | 80 | SITE_Assesment | 87 | 10. PHOTO LOG | HEADER | Photo ID | Area | Category | Description | Date | Taken By | File / Link | Related Risk | Status | Notes | SITE¦80
SITE | 81 | SITE_Assesment | 88 | 10. PHOTO LOG | DATA | SITE-P001 | Overall Site | Existing Conditions | Campus-wide route photos before excavation, including pavement, sidewalks, landscaping, parking, fire lanes and building entry areas | 0 | 0 | 0 | SITE-R1/SITE-R5 | Closed | 0 | SITE¦81
SITE | 82 | SITE_Assesment | 89 | 10. PHOTO LOG | DATA | SITE-P002 | THH #1-#19 | Structures | Each handhole/manhole/pullbox location, cover, label, depth, drainage, conduit entry, and final installed condition | 0 | 0 | 0 | SITE-R2/SITE-R8 | Closed | 0 | SITE¦82
SITE | 83 | SITE_Assesment | 90 | 10. PHOTO LOG | DATA | SITE-P003 | Ductbank | Pre-pour Inspection | Conduit count, separation, supports/spacers, depth, utility crossings, warning tape, pull strings and concrete encasement before pour | 0 | 0 | 0 | SITE-R1/SITE-R3 | Closed | 0 | SITE¦83
SITE | 84 | SITE_Assesment | 91 | 10. PHOTO LOG | DATA | SITE-P004 | Utility Crossings | Existing Utilities | Potholing/hand-dig photos showing electric, storm, sanitary, water, gas/unknown utilities and clearance to new ductbank | 0 | 0 | 0 | SITE-R1 | Closed | 0 | SITE¦84
SITE | 85 | SITE_Assesment | 92 | 10. PHOTO LOG | DATA | SITE-P005 | Building Tie-ins | Penetrations / Firestop | Exterior entry points, wall/floor penetrations, sleeves, firestop, weatherproofing and interior continuation to building TR/TE | 0 | 0 | 0 | SITE-R6 | Closed | 0 | SITE¦85
SITE | 86 | SITE_Assesment | 93 | 10. PHOTO LOG | DATA | SITE-P006 | Fiber Pull / Testing | Telecom | Fiber reels, pull setup, mandrel/rope, splice/termination points, labels, OTDR/power meter screenshots and OIT acceptance | 0 | 0 | 0 | SITE-R8 | Closed | 0 | SITE¦86
SITE | 87 | SITE_Assesment | 94 | 10. PHOTO LOG | DATA | SITE-P007 | Restoration | Civil | Asphalt/concrete trench patches, sidewalk panels, landscaping, turf, drainage, curb/edge details and final cleanup | 0 | 0 | 0 | SITE-R5/SITE-R7 | Closed | 0 | SITE¦87
SITE | 88 | SITE_Assesment | 95 | 10. PHOTO LOG | DATA | SITE-P008 | MCR / Provider Entrance | Critical Cutover | Provider handoff, WAN fiber route, temporary fiber, Path A/B into MCR and activation/cutover coordination photos | 0 | 0 | 0 | SITE-R4/SITE-R8 | Closed | 0 | SITE¦88
SITE | 89 | SITE_Assesment | 96 | 10. PHOTO LOG | BLANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SITE¦89

## V4_Architecture_Map (hidden)
BEDFORD PMIS V4.1 ARCHITECTURE MAP
Layer
Source of Truth | Bxx_Assessment | Building-level assessment data | Do not replace; all scope remains here.
Rollup | PMIS_Data | Formula-fed building / area rollup | Existing workbook engine.
Helper | _V4_Helper | Normalized building snapshot | Hidden; source for action scoring.
Action Queue | _V4_ActionQueue | Sorted priority view | Hidden; no table objects to prevent Excel repair issues.
Front End | V4_Mission_Control | Final mission-control dashboard | Executive-facing, concise, card-based.

## _V4_ActionQueue (hidden)
V4 ACTION QUEUE — FORMULA DRIVEN FROM PMIS_Data
Priority is calculated from open risks, questions, photos, shutdowns, readiness, status, and ready gate. Dashboard reads this sheet.
Rank | Building | Source Sheet | Priority Score | Severity | Action Required | Why Summary | Next Action | Readiness | Status | Ready | Risks | Questions | Photos | Shutdowns | Owner Focus | Execution Gate | Risk Density | Question Density | Photo Density | Priority Key
1 | 01 | B01_Assessment | 75.0096 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
2 | 02 | B02_Assessment | 75.0095 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
3 | 03 | B03_Assessment | 75.0094 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
4 | 04 | B04_Assessment | 75.0093 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
28 | 05 | B05_Assessment | 73.5092 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.55 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 73.5
5 | 06 | B06_Assessment | 75.0091 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
6 | 07 | B07_Assessment | 75.009 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
7 | 08 | B08_Assessment | 75.0089 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
8 | 09 | B09_Assessment | 75.0088 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
9 | 10 | B10_Assessment | 75.0087 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
29 | 12 | B12_Assessment | 72.0086 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.6 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 72
10 | 13 | B13_Assessment | 75.0085 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
11 | 14 | B14_Assessment | 75.0084 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
12 | 15 | B15_Assessment | 75.0083 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
13 | 16 | B16_Assessment | 75.0082 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
14 | 17 | B17_Assessment | 75.0081 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
15 | 18 | B18_Assessment | 75.008 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
16 | 20 | B20_Assessment | 75.0079 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
17 | 21 | B21_Assessment | 75.0078 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
18 | 22 | B22_Assessment | 75.0077 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
19 | 33 | B33_Assessment | 75.0076 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
30 | 61 | B61_Assessment | 13.5075 | Low | MONITOR | No major exception detected. | Maintain monitoring. | 0.55 | PILOT PHASE | YES | 0 | 0 | 0 | 0 | Monitor | Ready | 0 | 0 | 0 | 13.5
20 | 62 | B62_TR_Assessment | 75.0074 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
21 | 70 | B70_TR_Assessment | 75.0073 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
22 | 78 | B78_Assessment | 75.0072 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
23 | 80 | B80_Assessment | 75.0071 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
24 | 82 | B82_Assessment | 75.007 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
25 | BCH | BCH_Assessment | 75.0069 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
26 | MCR | MCR_Assessment | 75.0068 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75
27 | SITE | SITE_Assesment | 75.0067 | Medium | READY BUILDING | No major exception detected. | Maintain monitoring. | 0.5 | Yellow | No | 0 | 0 | 0 | 0 | Monitor | Review | 0 | 0 | 0 | 75

## _Command_Trade_Notes (hidden)
Building_ID | Fire / Life Safety | HVAC / Cooling | Electrical / UPS | Telecom / Fiber | Security / PACS / CCTV | Owner Risks | Open Questions
01 | • Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems. • Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. • Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes. • Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place. | • Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup. • Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration. • Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear. • Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating. | • Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation. • Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements. • Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition. • Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope. | • 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1. • Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan. • Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence. • Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway. | • Electrical/telecom plans show new access control, power supply/battery backup for PACS, HDP12/FIPS-compliant PIV-ready card reader with PIN pad, and camera 107-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration and door hardware coordination. • Verify existing security/CCTV equipment and any retained cameras. Maintain camera angles where existing security cameras are recabled. • Verify existing security/access conditions and protection-in-place during rack transfer. • Verify second-level existing security/CCTV impacts during cabling and equipment transfer. | • High: Existing conditions for Room 107 and transition rooms B02/138/282 not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing equipment may remain active during transfer to Room 107 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat, humidity and high-temp alarms • High: B01-TR107A/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPD, labels, 30-day load measurement and LOTO needs • High: 394 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications across basement/first/second levels — Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | • B01-Q1 — Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? [Closed] Impact: Room inventory could miss scope • B01-Q2 — What active services are currently fed from existing Rooms B02, 138 and 282? [Closed] Impact: Potential communications/security outage • B01-Q3 — What equipment from existing racks transfers to new Room 107 versus remains/decommissions? [Closed] Impact: Cutover and rack elevation risk • B01-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? [Closed] Impact: Cooling continuity unclear • B01-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? [Closed] Impact: Life-safety acceptance risk • B01-Q6 — Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Closed] Impact: Electrical readiness unknown
02 | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping. • Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping. • Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | • Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms. • Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm. • Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration. • Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete. | • Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels. • Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping. • Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits. • Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs. | • 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray. • 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope. • 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count. • Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover. | • Plans show 174-CAM-01 associated with the first-level TR area and PACS/security requirements. Verify camera/VMS integration, access controller/power supply, CR/RX/DC/ES/MD and door hardware. • Plans show 236-CAM-01. Verify camera/VMS integration, access control, door hardware, motion/detection devices and power. • Plans show 342-CAM-01 and 342A-CK-A. Verify camera/VMS integration and access control/security rough-in. • Maintain existing camera angles when re-cabling and protect existing PACS/equipment racks during transfer. | • High: Existing conditions for Rooms 141/236/342 and existing B-06/141/236 not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing equipment may remain active during transfer to new TRs — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified — Confirm each IU/CU serving each TR, power source, condensate route, controls, BACnet, thermostat and high-temp alarms • High: B02-TR141/236/342 A/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPDs, labels, 30-day load measurement and LOTO needs • High: 2,560 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications across several floors — Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | • B02-Q1 — Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? [Open] Impact: Room inventory could miss scope • B02-Q2 — What active services are currently fed from existing Rooms B-06, 141 and 236? [Open] Impact: Potential communications/security outage • B02-Q3 — What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? [Open] Impact: Cutover and rack elevation risk • B02-Q4 — Which IU/CU pair serves each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B02-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? [Open] Impact: Life-safety acceptance risk • B02-Q6 — Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown
03 | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse. • Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer. • Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations. | • Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm. • Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete. • Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains. • No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements. | • Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements. • Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements. • Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer. • Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations. | • 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2. • Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover. • Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted. • Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced. | • Plans require PACS for TR doors and electrical details include access-controlled door rough-in. Verify access controller, power supply/battery backup, CR/RX/DC/ES/MD devices, reader, strike and door hardware coordination. • Enlarged plan and schedule identify 101C-CAM-01 and 101C-CK-A. Verify camera/VMS integration, existing camera angles and protection-in-place. • Verify existing security/CCTV/PACS impacts during basement telecom room transfer. • Maintain existing camera angles when re-cabling; verify WAP/security/clock/Centrak devices are relabeled and tested. | • High: Existing conditions for Room 101E and transition rooms 107/101C not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing DMARC/fiber/telecom equipment may remain active during transfer to Room 101E — Document active services, protect in place, identify OIT/provider cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified — Confirm CU-01/IU serving Room 101E, power source, condensate, controls, BACnet, thermostat and high-temp alarms • High: B03-TR101CA/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPDs, PXR20 trip units, labels, 30-day load measurement and LOTO needs • High: 961 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications and provider/DMARC services — Require cutover plan, test records, labels, as-builts, OIT/provider coordination and VA acceptance before active connection | • B03-Q1 — Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? [Open] Impact: Room inventory could miss scope • B03-Q2 — What active services are currently fed from existing Room 107 and DMARC Room 101C? [Open] Impact: Potential communications/provider outage • B03-Q3 — What existing equipment transfers to new Room 101E versus remains/decommissions? [Open] Impact: Cutover and rack elevation risk • B03-Q4 — Which IU/CU pair serves Room 101E and is it on emergency/backup power? [Open] Impact: Cooling continuity unclear • B03-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? [Open] Impact: Life-safety acceptance risk • B03-Q6 — Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown
04 | • Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning. • FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies. • Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations. | • Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up. • Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control. • Verify cooling unit, routing, condensate, controls, and emergency/backup power path. | • Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits. • Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting. • Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source. | • New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • TR/panel identified; verify rack elevation and pathway details against 04T sheets. | • Verify access-controlled TR door, camera, and VMS/PACS integration. • Architectural notes require door/access control coordination; verify card reader/electric strike rough-in. • Verify room security details and device integration with VA systems. | • High: Existing conditions across basement/first/second TR areas not verified — Perform existing conditions survey with photos before mobilization • High: Basement TR routing may conflict with existing utilities / abatement areas — Coordinate hazardous material survey, utility locations, penetrations, and pathway routing • High: 1-hour fire/smoke-rated envelope and 45-minute door not field verified — Inspect rated walls, door/frame, ceiling/open-to-deck conditions, and penetrations • Critical: Cooling emergency power / 24/7 continuity not verified — Confirm source power for indoor/outdoor units, controls, condensate pumps, and alarms • High: UPS/PDU/rack electrical source and load coordination unresolved — Verify panel schedules, source, SPD, breaker sizes, labeling, and load measurements • Critical: Telecom/fiber cutover could affect active hospital communications — Require phasing plan, test results, and VA/OIT acceptance before cutover | • B04-Q1 — Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? [Open] Impact: Incomplete room inventory / missed scope • B04-Q2 — Are B05, 141, and 244A cooling systems on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B04-Q3 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B04-Q4 — What is the approved migration and cutover sequence for active Building 04 services? [Open] Impact: Potential communications outage • B04-Q5 — Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? [Open] Impact: Work stoppage or exposure risk • B04-Q6 — Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? [Open] Impact: Electrical delay or overload risk
05 | • Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts. • Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling. | • Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling. • Existing wall/wall-mount TE area; verify existing environmental conditions during field survey. | • 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source. • Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover. | • New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU. • Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records. | • Project general scope includes CCTV and PACS for telecom spaces; verify whether TE location receives camera/access control or is served by existing room controls. • Verify existing security protection and whether access-control work is needed for existing TE area. | • High: Telecom Enclosure installation details not field verified — Survey wall/backing, clearances, power, conduit/wireway, and access path before installation • Critical: Existing legacy equipment/cabling may remain active during cutover — Document active services, create cutover plan, protect-in-place until new TE is operational • Medium: Mechanical/fire protection scope excluded may hide interface risks — Confirm no added cooling/sprinkler work is required and document basis for N/A • High: Electrical panel/circuit source for TE equipment not confirmed — Verify 05E-401/501/601/701 schedules, UPS/PDU receptacles, labels, and emergency power source • High: Firestopping/penetration sealing still required despite fire protection scope exclusion — Inspect all new and reused conduits, sleeves, wall/floor penetrations, and temporary firestop • Medium: Commissioning / acceptance documentation may be treated as minor due to TE scope — Track testing, labeling, OIT acceptance, third-party inspections, and as-builts | • B05-Q1 — Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? [Open] Impact: Room inventory could be wrong • B05-Q2 — What active services are currently fed from the existing 153-A TE/legacy patch panels? [Open] Impact: Potential communications outage • B05-Q3 — What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? [Open] Impact: Cutover risk • B05-Q4 — Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? [Open] Impact: Power source cannot be verified • B05-Q5 — Is emergency/backup power required or provided for the TE UPS/PDU source? [Open] Impact: Continuity requirement unclear • B05-Q6 — Are firestopping locations and surface raceway/conduit routes shown and coordinated? [Open] Impact: Rated assembly/firestop risk
06 | • Existing equipment area; verify no cabling penetrations are left unsealed. • Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs. • Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft. | • Verify basement equipment environmental condition and any heat/load issues during cutover. • Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route. • Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls. | • Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements. • Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation. • Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power. | • Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS. • Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification. • Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | • Verify existing basement access/security while protecting active equipment. • Electrical enlarged plan references existing card reader to remain/protect in place and new tri-tech motion sensor; verify PACS/CCTV integration. • Verify door hardware/access control, motion sensor, camera, and VA security integration. | • High: Existing conditions across B-01, 178 and 233 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing basement equipment may remain active during cutover — Document active services and protect in place until new system is tested and accepted • Critical: Electrical panel replacement/new telecom power could interrupt active systems — Coordinate load measurement, panel renovation, shutdowns and temporary power plan • High: Room 233 conversion/rated wall and door work may impact adjacent patient toilet/private bath areas — Verify phasing, barriers, infection control and temporary life-safety provisions • Critical: Dedicated cooling emergency power, controls, condensate and BACnet interface not verified — Confirm emergency power source, disconnects, condensate routes, BACnet adapter and high-temp alarms • Critical: Fire alarm/sprinkler impairments and penetrations may affect occupied operations — Track impairments, fire watch, temporary firestop and third-party reports | • B06-Q1 — Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? [Open] Impact: Room inventory could miss scope • B06-Q2 — What active services are fed from existing B-01 and Room 178 legacy equipment? [Open] Impact: Potential communications outage • B06-Q3 — What is the approved cutover sequence for B-01, 178 and 233? [Open] Impact: Cutover risk • B06-Q4 — Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B06-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B06-Q6 — Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? [Open] Impact: Electrical readiness unknown
07 | • Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination. • Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications. | • Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm. • Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route. | • Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement. • Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels. | • 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU. • TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover. | • Verify access control, door hardware and CCTV/PACS integration for basement TR. • Architectural notes require access control hardware modifications at new rated door; verify card reader, electric strike, door position switch, motion sensor and camera. | • High: Existing conditions for B-18 and 228A not field verified — Perform existing conditions survey with photos before mobilization • High: Basement TR conversion may conflict with existing utilities, office finishes or active pathways — Verify routing, clearances, penetrations, existing conduit and access before work • High: Second-floor rated wall/door work and exterior furring wall/window enclosure could affect schedule — Coordinate architectural work, door/frame, wall rating, furring wall, finishes and infection control barriers • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignments, emergency source, BACnet/interface, condensate pump routing and alarm points • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B07-TRB18A/B and B07-TR228A/B panel schedules, circuit labels, SPDs and load measurements • Critical: Telecom/fiber cutover may affect active hospital communications — Require cutover plan, test results, OIT coordination and VA acceptance before active connection | • B07-Q1 — Confirm final TR scope: B-18 basement and 228A second floor only? [Open] Impact: Room inventory could miss scope • B07-Q2 — Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? [Open] Impact: Cooling scope unclear • B07-Q3 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B07-Q4 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B07-Q5 — What active services are currently fed from B-18 and/or existing pathways serving 228A? [Open] Impact: Potential communications outage • B07-Q6 — Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? [Open] Impact: Electrical readiness unknown
08 | • Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected. • Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers. • Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades. | • Verify existing environmental conditions and whether active legacy equipment remains during cutover. • Field verify whether TE equipment load requires cooling or if served by existing building HVAC. • Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls. | • Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements. • Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel. • Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope. | • Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS. • Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance. • New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS. | • Verify existing basement access/security while protecting active equipment. • 45-minute door shown; verify access-control hardware applicability and whether TE is secured. • Door schedule/hardware note requires coordination with electrical/access control; verify card reader, electric strike, door position, motion sensor, camera and VA integration. | • High: Existing conditions for B-15, B12B and 2065A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing basement legacy equipment may remain active during cutover — Document active services, protect in place and define cutover/demo sequence • High: Basement B12B appears as Office in architectural schedule but TE in telecom/electrical schedules — Field verify actual TE location, room name, door/wall rating and panel/cable routing • High: Second-floor Telecom Room conversion includes rated wall/door/open-to-deck work and possible hazardous material impacts — Coordinate architectural work, dust barriers, floor abatement, FEC and rated assemblies before construction • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignment, emergency source, BACnet/interface, condensate routing and alarm points • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B08-TR2065AA/AB panel schedules, rack receptacles, SPD, labels and load measurement requirements | • B08-Q1 — Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? [Open] Impact: Room inventory may miss scope • B08-Q2 — What active services are currently fed from existing B-15 equipment? [Open] Impact: Potential communications outage • B08-Q3 — Is B12B truly a TE/equipment location or only a cabling pathway/service area? [Open] Impact: Scope ambiguity • B08-Q4 — Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? [Open] Impact: Cooling continuity unclear • B08-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? [Open] Impact: Life safety acceptance risk • B08-Q6 — Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown
09 | • Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR. • Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft. • Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations. | • Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms. • Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power. • Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power. | • Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes. • Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits. • Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits. | • Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover. • Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. • Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | • Enlarged plans show existing/new security boxes, network door controller, camera/security scope; verify PACS/CCTV integration and protection of active security systems. • First-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 104B camera designation; verify card reader, electric strike, door contact, motion and camera. • Second-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 206A camera designation; verify PACS/VMS integration and commissioning. | • High: Existing conditions for B01, 104B and 206A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Basement TR includes existing equipment and could remain active during cutover — Document active services, protect-in-place and define cutover/demo sequence • High: Hazardous material abatement plans exist for basement, first and second levels — Coordinate ACM/lead/abatement review before penetrations, flooring removal or ceiling/wall work • High: Rated wall/door work and fire/smoke assemblies could affect schedule and acceptance — Verify wall ratings, door/frame rating, penetrations, smoke/fire barriers and access control hardware • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignments, emergency source, BACnet/interface, condensate routing and alarms • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B09-TRB01A/B, B09-TR104BA/B, B09-TR206AA/B schedules, SPDs, labels and load measurements | • B09-Q1 — Confirm final TR scope: B01 basement, 104B first level, and 206A second level? [Open] Impact: Room inventory may miss scope • B09-Q2 — What active services are currently fed from B01 existing equipment/security/network devices? [Open] Impact: Potential communications/security outage • B09-Q3 — What hazardous/abatement steps apply to B01, 104B and 206A work areas? [Open] Impact: Work delay or exposure risk • B09-Q4 — Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B09-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B09-Q6 — Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown
10 | • Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping. • Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place. • Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment. | • Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm. • No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work. • No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted. | • Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels. • Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing. • Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required. | • 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover. • Coordinate telecom power pathways through/source from basement electrical room if applicable. • Coordinate emergency source/backup power pathways for telecom equipment and cooling. | • General scope requires PACS/CCTV for TR doors; verify door hardware, access controller, camera/VMS integration and any existing attic access/security constraints. • Verify security impact only if electrical source room access or devices are modified. • Verify emergency electrical room security impact if work requires access control changes. | • High: Attic Telecom Room existing conditions and access not field verified — Survey Room 200A, attic access route, existing rack/equipment, floor/deck conditions, clearances and utilities • High: Hazardous material abatement plan exists for attic level — Coordinate attic abatement/IH review before penetrations, ceiling/floor work, cabling or HVAC/electrical installation • Critical: Existing wall-mounted rack/equipment may remain active during cutover — Document active services, protect in place and develop night-shift cutover/temporary rack plan • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 capacity, power source, condensate routing, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, generator/ATS path and shutdown sequencing unclear — Verify B10-MDP, B10-L10-E, ATS-B10-LSD, panel feeders, load measurement and LOTO before electrical work • Critical: Fire alarm/sprinkler/firestopping work in attic TR could affect occupied operations — Track impairments, fire watch, sprinkler/head changes, FA device work, rated penetrations and temporary firestopping | • B10-Q1 — Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? [Open] Impact: Room inventory could miss scope • B10-Q2 — What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? [Open] Impact: Potential communications outage • B10-Q3 — What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? [Open] Impact: Work delay/exposure risk • B10-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? [Open] Impact: Cooling continuity unclear • B10-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? [Open] Impact: Life-safety acceptance risk • B10-Q6 — Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? [Open] Impact: Electrical readiness unknown
12 | • No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route. • No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work. | • No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment. • Field verify existing environmental conditions only if existing service point/equipment is accessed. | • No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown. • Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling. | • Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing. • 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only. | • No new TR door or PACS/CCTV package shown for Building 12; verify security access only for work areas and existing equipment rooms. • Confirm access requirements to existing closet/demarc while protecting active operations. | • High: Fiber-only scope could be mistaken for full TR scope or skipped as minor work — Clearly tag Building 12 as fiber-only and verify required fiber path, testing, labels and acceptance deliverables • High: Existing pull-through pathway not field verified — Trace basement/first/second level pathway, conduit/cable tray capacity, pull points and access before scheduled pull • Critical: Existing service continuity during fiber pull/cutover may not be defined — Coordinate with VA OIT, submit phasing/cutover plan, and maintain legacy service until new fiber is tested and accepted • High: Pathway penetrations/firestopping may be overlooked because there is no architectural/FP package — Inspect all new/reused penetrations and require permanent or temporary firestopping at end of shift • Medium: Existing termination/demarc location and ownership unclear — Field document existing rack/demarc/serving closet and confirm where new fiber terminates or passes through • High: Test reports, labels and as-builts may be incomplete for fiber-only work — Track fiber OTDR/certification, labeling, route documentation and VA/OIT acceptance before closeout | • B12-Q1 — Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? [Open] Impact: Scope misunderstanding • B12-Q2 — What exact pathway does the Building 12 fiber take through basement, first and second levels? [Open] Impact: Fiber pull and access risk • B12-Q3 — Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? [Open] Impact: Termination and ownership unclear • B12-Q4 — Are existing conduits/cable trays available and below fill limits for the new fiber? [Open] Impact: Pathway capacity risk • B12-Q5 — Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? [Open] Impact: Life safety/firestop risk • B12-Q6 — What is the approved cutover/testing/acceptance sequence for Building 12 fiber? [Open] Impact: Possible outage or acceptance delay
13 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | • Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B. • Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124. | • Electrical enlarged plan shows security/access-control device callouts at Room 124 and 124-CAM-01 camera designation; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 124 and existing Tel Room 222 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing Tel Room 222 equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B13-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B13-Q1 — Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? [Open] Impact: Room inventory could miss scope • B13-Q2 — What active services are currently fed from existing Tel Room 222 equipment? [Open] Impact: Potential communications/security outage • B13-Q3 — What hazardous/abatement steps apply to first-level Room 124 work? [Open] Impact: Work delay or exposure risk • B13-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? [Open] Impact: Cooling continuity unclear • B13-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? [Open] Impact: Life-safety acceptance risk • B13-Q6 — Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
14 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing basement tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Existing basement telecom room; verify no unsealed penetrations remain after cable transfer or reuse. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 119 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel/F Panel room; verify existing environmental conditions during cutover and whether legacy equipment remains active. • Existing telecom room reference; field verify cooling/ventilation and active equipment condition. | • Electrical plan/schedules identify B14-TR119A/B, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and panel load measurement requirements. • Existing basement wall-mounted TE/equipment area; verify power source, active equipment, UPS/PDU status, and transition requirements before disconnect or removal. • Existing telecom room photo reference; confirm power sources and any cutover requirements. | • 14T-701 identifies Room 119 schedule: 44 WAO total, 29 active ports per survey, 76 total ports per schedule, and 84 total ports with 10% allowance. New Rack ID TR01-119-1 serves first and second level outlets with Fiber Path A/B. • Existing Room B.01 equipment includes wall-mounted TE, Cisco switch/legacy patch panel, telco patch, plywood backboards, and legacy Fiber LIU; verify active services and transfer plan to Room 119. • Existing basement telecom room B2 is identified by photo reference; verify active devices, routing, and relation to B.01. | • Telecom/electrical plans show 119-CAM-01 and security/access-control scope for Room 119; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Verify whether existing security equipment remains, is relocated, or requires temporary protection during cutover. • Verify security/access conditions and whether any legacy security equipment is present. | • High: Existing conditions for Room 119 and existing basement telecom rooms B.01/B2 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing basement telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B14-TR119A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B14-Q1 — Confirm final telecom scope: new Room 119 and existing basement B.01/B2 transition only? [Open] Impact: Room inventory could miss scope • B14-Q2 — What active services are currently fed from existing B.01/B2 equipment? [Open] Impact: Potential communications/security outage • B14-Q3 — What hazardous/abatement steps apply to first-level Room 119 work? [Open] Impact: Work delay or exposure risk • B14-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 119? [Open] Impact: Cooling continuity unclear • B14-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 119? [Open] Impact: Life-safety acceptance risk • B14-Q6 — Are B14-TR119A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
15 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Existing basement telecom/crossover room; verify no unsealed penetrations remain after cable transfer or reuse. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124A and CU-1-01 outdoor heat-pump/A/C unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 is shown with existing/remain indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. • Existing basement telecom/crossover space; verify environmental conditions and whether active equipment remains during cutover. | • Electrical enlarged plans and schedules identify B15-TR124AA/AB, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and 30-day load measurement requirements. • Existing rack/equipment area; verify power source, active equipment, APC floor UPS status, and transition requirements before disconnect or removal. • Existing B-01 crossover; verify power sources and cutover needs for legacy patch panel/crossover. | • 15T-701 identifies Room 109A schedule but field plan/electrical room callouts identify Telecom Room 124A; schedule has 62 WAO total, 76 active ports per survey, 101 total ports per schedule, and 111 total ports with 10% allowance. New Rack ID TR15-109A-01 serves basement, first and second level outlets. • Existing Room 222 equipment includes wall/wall-mounted TE, Cisco switches, legacy 48-port patch panels, ground bar, plywood backboard, security cabinet, and floor UPS; verify active services and transfer plan to Room 124A. • Existing B-01 crossover includes legacy 24-port patch panel; verify active devices, routing, and relation to Room 222 and Room 124A. | • Telecom/electrical plans show 124A-CAM-1 and security/access-control scope for Room 124A; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Verify security/access conditions and whether any legacy security equipment is present. | • High: Existing conditions for Room 124A and existing telecom rooms 222/B01 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B15-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B15-Q1 — Confirm final telecom scope: new Room 124A and existing Rooms 222/B01 transition only? [Open] Impact: Room inventory could miss scope • B15-Q2 — Why does 15T-701 reference RM 109A while plans and electrical schedules identify Telecom Room 124A? [Open] Impact: Room naming mismatch could affect PMIS tracking • B15-Q3 — What active services are currently fed from existing Room 222 and B01 equipment? [Open] Impact: Potential communications/security outage • B15-Q4 — What hazardous/abatement steps apply to first-level Room 124A work? [Open] Impact: Work delay or exposure risk • B15-Q5 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124A? [Open] Impact: Cooling continuity unclear • B15-Q6 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124A? [Open] Impact: Life-safety acceptance risk
16 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 015 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Telecom Room 014; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • Electrical plans/schedules identify B16-TR015A/B, 240V rack UPS requirements, rack receptacles, TR receptacles, lighting, access controller, CU-1-01, SPD requirements, existing panel demolition/replacement, and 30-day load measurement requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 16T-701 identifies Room 015-A schedule: 25 WAO total, 25 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. New Rack ID TR01-015-A-1 serves basement, first, second and attic level outlets. • Existing Room 014 equipment includes wall/TE rack, floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU; verify active services and transfer plan to Room 015. | • Telecom/electrical plans show 015-CAM-1 and security/access-control scope for Room 015; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Room 014; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 015 and existing Telecom Room 014 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • High: Basement TR buildout may conflict with existing utilities, water heater/stair/storage conditions and pathway routing — Survey adjacent Water Heater 010, Vacant 011/012/013, Stair 014, pathway/ductbank routing, and constructability constraints • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B16-TR015A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B16-Q1 — Confirm final telecom scope: new Room 015 and existing Room 014 transition only? [Open] Impact: Room inventory could miss scope • B16-Q2 — What active services are currently fed from existing Room 014 equipment? [Open] Impact: Potential communications/security outage • B16-Q3 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 015? [Open] Impact: Cooling continuity unclear • B16-Q4 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 015? [Open] Impact: Life-safety acceptance risk • B16-Q5 — Are B16-TR015A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown • B16-Q6 — Which existing panel/circuit breaker/feeder demolition and replacement affects Room 015 telecom power? [Open] Impact: Panel outage/cutover risk
17 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom closet; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Verify firestopping at pathway penetrations between Building 17 and Building 29 and any rated floor/wall assemblies. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 118 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing B35A is shown with existing indoor AC unit; verify whether it remains active, is abandoned, or needs temporary protection during cutover. • No dedicated cooling expected for pathway; verify any equipment cabinets or active service locations in Building 29 if applicable. | • Electrical plans/schedules identify B17-TR118A fed from BUS-B17-NPB1-R and B17-TR118B fed from BUS-B17-EQDP, with TR RM118 rack receptacles, 208V UPS/PDU equipment, CU-1-01, SPD requirements, and 30-day load measurement requirements. • Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. • Verify whether any Building 29 equipment or extension path requires power, grounding, bonding, or labeling tied back to B17 TR 118. | • 17_29T-701 identifies Room 118 schedule: 113 WAO total, 67 active ports per survey, 154 total ports per schedule, and 169 total ports with 10% allowance. Rack ID TR17-118-1 serves basement, first, second-level outlets and Building 29 path. • Existing Room B35A equipment includes SERTEX utility service ports, legacy Ortronics patch panels, Cisco switches, wall-mounted TE, Fiber/legacy equipment, security cabinet, and floor UPS; verify active services and transfer plan to Room 118. • Building 29 is shown served from B17; verify fiber from Building 17 to Building 29, path to B29 4-inch PVC, outlet labels, test records and as-builts. | • Telecom/electrical plans show 118-CAM-01 and security/access-control scope for Room 118; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in B35A; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Verify Building 29 pathway and any security scope tied into B17 TR 118/VMS/PACS. | • High: Existing conditions for Room 118, B35A and Building 29 service path not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 208V UPS/PDU and panel source coordination could delay energization — Verify B17-TR118A/B schedules, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, SPD, labels, load measurement and LOTO needs • High: Cable tray and pathway scope is large and crosses multiple levels/building service boundary — Verify 517 ft cable tray, supports, seismic bracing, 40% fill, path to B29 4-inch PVC, penetrations and labeling before install | • B17-Q1 — Confirm final telecom scope: new Room 118, existing B35A, and Building 29 served from B17? [Open] Impact: Room inventory or PMIS mapping could miss scope • B17-Q2 — What active services are currently fed from existing B35A equipment? [Open] Impact: Potential communications/security outage • B17-Q3 — What exact Building 29 outlets/devices are served through TR17-118-1? [Open] Impact: Building 29 scope boundary unclear • B17-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 118? [Open] Impact: Cooling continuity unclear • B17-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 118? [Open] Impact: Life-safety acceptance risk • B17-Q6 — Are B17-TR118A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
18 | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing TE room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. • Existing second-level closet; verify protection-in-place and firestopping after transfer or abandonment. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 110 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing TE 111B; verify existing environmental conditions during cutover and whether legacy equipment remains active. • Existing Closet 213; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • Electrical plans/schedules identify B18-TR110A/B, 208V rack UPS requirements, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and telecom panelboard schedule requirements. • Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. • Existing rack/equipment area; verify active equipment, APC UPS status, source circuits, SERTEX utility service and transfer requirements before disconnect/removal. | • 18T-701 identifies RM 111A schedule: 86 WAO total, 61 active ports per survey, 122 ports per schedule, and 134 total ports with 10% allowance. New rack elevation is Room 110, 1 rack plus future, with UPS, Future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. • Existing Room 111B equipment includes wall-mounted rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber optic housing; verify active services and transfer plan to Room 110. • Existing Room 213 equipment includes SERTEX utility service ports, Cisco switch, multiple legacy Ortronics patch panels, wall/wall-mount TE and APC floor UPS; verify active services and transfer plan to Room 110. | • Telecom/electrical plans show 111A-CAM-01 and security/access-control scope for the new TR area; verify room naming, CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in 111B; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Existing security cabinet shown in 213; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 110, Room 111B and Room 213 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material / lead-based paint abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 208V UPS/PDU and panel source coordination could delay energization — Verify B18-TR110A/B schedules, rack receptacles, SPD, labels, source circuits and LOTO needs • High: Cable tray and pathway scope crosses first and second levels — Verify 315 ft cable tray, supports, seismic bracing, 40% fill, penetrations, coordination with lighting/HVAC and labeling before install | • B18-Q1 — Confirm final telecom scope: new Room 110 with existing 111B and 213 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B18-Q2 — Why does 18T-701 reference RM 111A while new rack/electrical plans identify Telecom Room 110? [Open] Impact: Room naming mismatch could affect PMIS tracking • B18-Q3 — What active services are currently fed from existing 111B and 213 equipment? [Open] Impact: Potential communications/security outage • B18-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 110? [Open] Impact: Cooling continuity unclear • B18-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 110? [Open] Impact: Life-safety acceptance risk • B18-Q6 — Are B18-TR110A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
20 | • Cover sheet states Building 20 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. • Existing closet; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Office 1B ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing Tel/Data Closet 8A includes indoor AC unit to remain/protect in place; verify operation during cutover and whether equipment remains after transition. | • 20T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing 8A elevation shows UPS on ground, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 20T-701 identifies TE01-1B-1: 21 WAO total, 24 active ports per survey, 30 ports per schedule, 33 total ports with 10% allowance. Provide new wall-mount TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing Tel/Data Closet 8A contains open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy 48-port patch panel and Fiber LIU. Field verify all active services. | • Building 20 does not appear to create a new TR door/PACS package. Verify any existing cameras/security devices in Office 1B and ensure no camera angle or VMS integration is disrupted. • Keynotes indicate existing cameras are to be retained and re-used/protected in place; verify existing security equipment and cabinet impacts during cutover. | • High: Existing conditions for new Office 1B TE and existing Tel/Data Closet 8A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in 8A may remain active during transfer to new TE in 1B — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Room naming and TE designation could cause PMIS mapping confusion — Track as Building 20 / Office 1B / TE01-1B-1 and link existing Room 8A as transition point • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Office 1B — Verify heat load, office ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 459 feet of cable tray/pathway requires coordination despite small port count — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B20-Q1 — Confirm final scope: new wall-mount TE enclosure in Office 1B and existing Tel/Data Closet 8A transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B20-Q2 — What active services are currently fed from existing 8A open TE cabinet and related equipment? [Open] Impact: Potential communications/security outage • B20-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Office 1B? [Open] Impact: Electrical readiness unknown • B20-Q4 — Is Office 1B HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B20-Q5 — Are existing cameras/security devices in Building 20 protected and retained with no VMS/PACS changes? [Open] Impact: Security continuity unclear • B20-Q6 — Are all 459 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
21 | • Cover sheet states Building 21_19 receives a Telecom Enclosure and fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. • Existing B21 basement TR; verify protection-in-place and firestopping after cable transfer or reuse. • Existing B19 B05TR; verify protection-in-place and firestopping after cable transfer or reuse. | • Mechanical sheets exist in index. Verify whether new TE heat load in Office 100A is supported by existing/new HVAC and whether any mechanical scope applies despite TE designation. • Existing B21 B1.TR; verify environmental conditions during cutover and whether legacy equipment remains active. • Existing B19 B05TR; verify environmental conditions and whether equipment remains active during/after Building 21 transfer. | • 21_19T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switches, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing B21 B1.TR elevation shows UPS on ground, Cisco switch, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements. • Existing B19 B05TR elevations show APC floor UPS, legacy patch panels, Cisco switch and Fiber LIU; verify power source, active equipment and transfer/retention requirements. | • 21_19T-701 identifies RM 104 schedule: 90 WAO total, 67 active ports per survey, 119 ports per schedule, and 131 total ports with 10% allowance. 659 ft cable tray total: 63 ft basement and 596 ft first level. • Existing B21 B1.TR equipment includes multiple legacy patch panels, Cisco switch, UPS on ground, Fiber LIU and APC floor UPS; verify active services and transfer plan to new TE. • Existing B19 B05TR equipment includes legacy Ortronics patch panels, Cisco switch, Fiber LIU and APC floor UPS; verify active services and whether B19/B21 devices are served from new enclosure. | • Building 21_19 appears to create a TE enclosure rather than a full TR door/PACS package. Verify any existing cameras/security devices in Room 100A and ensure no camera angle or VMS integration is disrupted. • Verify any existing security device/cabinet impacts during cutover. • Verify existing security/camera protection-in-place and any impact from B19/B21 shared telecom equipment. | • High: Existing conditions for new 100A TE, B21 B1.TR and B19 B05TR not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment may remain active during transfer to new TE enclosure — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • High: Room naming mismatch: schedule says RM 104 / TR01-104-1 while plan/enlarged view identifies Room 100A — Track PMIS as Building 21 / Room 100A / Schedule RM 104 / Rack ID TR01-104-1 and confirm with designer • High: B19/B21 combined package may blur scope boundary and ownership of ports — Separate Building 21 work, Building 19 transition work, and shared service/cross-connect items in PMIS notes • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 659 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B21-Q1 — Confirm final scope: new TE enclosure at Room 100A/RM 104 and existing B21 B1.TR plus B19 B05TR transition? [Open] Impact: Room inventory or PMIS mapping could miss scope • B21-Q2 — Why does 21_19T-701 list RM 104 / TR01-104-1 while enlarged plan identifies Room 100A? [Open] Impact: Room naming mismatch could affect PMIS tracking • B21-Q3 — What active services are currently fed from existing B21 B1.TR and B19 B05TR equipment? [Open] Impact: Potential communications/security outage • B21-Q4 — What exactly is meant by '19 serving 21' on the new TE enclosure elevation? [Open] Impact: Building 19/21 boundary unclear • B21-Q5 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in 100A? [Open] Impact: Electrical readiness unknown • B21-Q6 — Are all 659 ft of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
22 | • Cover sheet states Building 22 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. • Existing TE room; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Break Room 102 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing Room 103 equipment area; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • 22T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing 103 elevation shows APC UPS, Cisco switch, SERTEX utility service, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 22T-701 identifies TR01-102-1: 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total port quantities, and 8 total ports with 10% allowance. Provide new wall-mount 12RU TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing Room 103 contains APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall and ports 1-24 to Bldg 19 ports 73-96. Field verify all active services and B19 handoff. | • Building 22 does not appear to create a new full TR door/PACS package. Verify any existing cameras/security devices in Break Room 102 and ensure no camera angle or VMS integration is disrupted. • Verify security/access conditions and whether any legacy security equipment is present at existing TE location. | • High: Existing conditions for new Break Room 102 TE and existing Room 103 TE not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in 103 may remain active during transfer to new TE in 102 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Break Room 102 use may conflict with wall-mount TE access and clearances — Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Break Room 102 — Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 139 feet of cable tray/pathway requires coordination despite small port count — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B22-Q1 — Confirm final scope: new wall-mount TE enclosure in Break Room 102 and existing Room 103 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B22-Q2 — What active services are currently fed from existing Room 103 equipment? [Open] Impact: Potential communications/security outage • B22-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? [Open] Impact: Electrical readiness unknown • B22-Q4 — Is Break Room 102 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B22-Q5 — Are existing cameras/security devices in Building 22 protected and retained with no VMS/PACS changes? [Open] Impact: Security continuity unclear • B22-Q6 — Are all 139 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
33 | • Cover sheet states Building 33 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. • Existing Tel Closet; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Office B23 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing B17 enlarged plan identifies an existing indoor AC unit. Verify operation during cutover and determine whether active legacy equipment remains after transfer to B23. | • 33T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing B17 elevations show UPS on floor, Cisco switches, SERTEX utility service, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 33T-701 identifies TE01-B23-1: 55 WAO total, 34 active ports per survey, 88 total ports per schedule, and 97 total ports with 10% allowance. Basement cable tray schedule totals 102 ft. Provide 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing B17 rack elevations include Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, passive Fiber LIU/wall mount, UPS on floor and cross-building port references to Bldgs 3, 80 and 82. | • Building 33 does not appear to create a new full TR door/PACS package. Verify existing cameras/security devices in B23 and ensure no camera angle or VMS integration is disrupted. • Existing B17 enlarged plan identifies network door controller, keypad and equipment box; verify protection-in-place and whether any security equipment is relocated or recabled. | • High: Existing conditions for new B23 TE and existing B17 Tel Closet not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in B17 may remain active during transfer to new TE in B23 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Office B23 use may conflict with wall-mount TE access and clearances — Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Office B23 — Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 102 feet of basement cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B33-Q1 — Confirm final scope: new wall-mount TE enclosure in B23 and existing B17 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B33-Q2 — What active services are currently fed from existing B17 equipment? [Open] Impact: Potential communications/security outage • B33-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in B23? [Open] Impact: Electrical readiness unknown • B33-Q4 — Is Office B23 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B33-Q5 — Are existing cameras/security devices in Building 33 protected and retained with no VMS/PACS disruption? [Open] Impact: Security continuity unclear • B33-Q6 — Are all 102 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
61 | • Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. • Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. • Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. • Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | • Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. • Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. • Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. • Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | • Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. • Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. • Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. • Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | • 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. • 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. • 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. • 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service. | • Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. • Verify TR door hardware and access control, CCTV camera, network door controller and integration. • Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. • Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | • High: Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • High: Hazardous material abatement plans exist for first and second levels — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation • Critical: Existing server/demarc equipment may remain active during cutover — Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path • Critical: Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified — Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements • High: Large cable tray scope creates coordination and firestop risk — Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | • B61-Q1 — Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? [Open] Impact: Room inventory could miss scope • B61-Q2 — What active services and circuits are currently housed in Room 137/137A? [Open] Impact: Potential outage/cutover risk • B61-Q3 — Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? [Open] Impact: Electrical PMIS mapping risk • B61-Q4 — Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? [Open] Impact: Cooling continuity unclear • B61-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B61-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown
62 | • Verify | • Verify | • Verify | • Verify | • No security / pacs / cctv items captured for this building. | • High: Cooling redundancy / emergency power not verified — Confirm power path for cooling, controls, condensate pump • High: Firestopping condition unknown — Survey penetrations and temporary/permanent firestop plan • Medium: Existing room conditions undocumented — Create photo record before construction begins • High: Condensate leak risk near IT equipment — Verify condensate routing and alarms | • B62-Q1 — Are cooling units emergency powered? [Open] Impact: Cannot confirm continuity of operations • B62-Q2 — Are future rack loads included in HVAC sizing? [Open] Impact: Cooling may be undersized after expansion • B62-Q3 — Is extinguisher location identified within 75 feet? [Open] Impact: Life safety / acceptance risk • B62-Q4 — Are all penetrations fully documented and firestopped? [Open] Impact: Fire/smoke spread risk
70 | • Verify | • Verify | • Verify | • Verify | • No security / pacs / cctv items captured for this building. | • High: Cooling emergency power / continuity not verified — Confirm power path for cooling, controls, BACnet adapter, and condensate pump • High: 1-hour rated/smoke-rated TR envelope and penetrations not field verified — Survey walls, doors, sleeves, trays, firestop, and head-of-wall conditions • Medium: Existing basement service conditions may constrain routing and access — Document existing utilities, clearances, and phasing around active systems • High: Existing TR/service equipment transfer could affect active operations — Require phasing plan and maintain analog/low-voltage systems operational • High: Condensate leak risk near IT equipment — Verify condensate routing, insulation, pump power, and alarms | • B70-Q1 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cannot confirm continuity of operations • B70-Q2 — Are future rack loads included in HVAC sizing for B27, 125A, and 262A? [Open] Impact: Cooling may be undersized after expansion • B70-Q3 — Are extinguisher cabinet locations identified within 75 feet of each TR? [Open] Impact: Acceptance / life safety risk • B70-Q4 — Are all wall/floor penetrations and speed sleeves shown and firestopped? [Open] Impact: Fire/smoke spread risk • B70-Q5 — What phasing is required to keep existing low-voltage/analog systems operational? [Open] Impact: Potential communications interruption
78 | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, and rated penetrations. • Verify FP/FA modifications, FEC location, temporary firestopping and final UL systems. • Verify first-level TR sprinkler/FA work, FEC location and cable tray penetrations. • Verify second-level TR sprinkler/FA work, FEC location, vertical riser penetrations and firestopping. • Verify third-level TR fire protection/fire alarm coordination and firestop work. | • Mechanical sheets included for basement. Verify dedicated cooling equipment, capacity, condensate, emergency source, controls/BACnet and high-temperature alarm. • Verify dedicated cooling and relationship to B30/B35 telecom buildout. • Verify first-level TR cooling, controls, emergency power and alarm tie-in. • Verify second-level TR cooling, condensate route and 24/7 operation. • Verify third-level TR cooling and control/alarm integration. | • Rack elevations identify new rack UPS/PDU and future rack. Verify panelboard/source, SPD, rack receptacles, PDU feeds, labels, load measurement and LOTO. • Verify rack UPS/PDU source, spare/future rack provisions and grounding/bonding. • Verify first-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. • Verify second-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. • Verify third-level rack receptacles for two racks, UPS/PDU, panel sources and labels. | • 78_78AT-701: 210 WAO total, 23 active ports, 311 scheduled ports, 342 with allowance; rack IDs TR01-B30-1/-2. Basement cable tray total 1,702 ft. • 78_78AT-702: 53 WAO total, 23 active ports, 64 scheduled ports, 70 with allowance. Confirm rack ID/room relation and active services. • 78_78AT-702/703: 301 WAO total, 388 active ports, 404 scheduled ports, 444 with allowance. Large active port count; high cutover risk. • 78_78AT-703/704: 256 WAO total, 153 active ports, 348 scheduled ports, 383 with allowance. Verify second-level test records and riser labels. • 78_78AT-704: 158 WAO total, 163 active ports, 289 scheduled ports, 318 with allowance. Rack IDs TR01-342-1/-2. | • TR scope includes wall-mounted CCTV cameras and PACS for TR doors. Verify CR/RX/DC/ES/MD, controller and VMS integration. • Verify PACS/CCTV integration and door hardware coordination. • Verify first-level TR PACS/CCTV and VMS integration. • Verify second-level TR PACS/CCTV and VMS integration. • Verify third-level TR PACS/CCTV and VMS integration. | • High: Existing conditions and active equipment across six TRs and existing telecom rooms not field verified — Perform detailed room-by-room existing condition survey with photos and active-service inventory • High: Hazardous material abatement plans exist for basement and third level — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or MEP installation • Critical: Existing telecom equipment may remain active during cutover — Document active services, OIT windows, rack inventory, temporary utilities and rollback plan • Critical: Dedicated cooling sequence, emergency power, condensate and alarms not verified — Confirm HVAC equipment serving each TR, emergency source, condensate, controls/BACnet and high-temp alarms • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify telecom panelboards, breakers, rack receptacles, UPS/PDU sources, SPDs, labels and LOTO requirements • High: Large cable tray scope creates coordination and firestop risk — Verify 4,849 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | • B78-Q1 — Confirm final telecom room list and PMIS mapping: B30, B35, 1232, 227A, 342, 401 plus existing rooms 15E/1234/353/308A/408A? [Open] Impact: Room inventory could miss scope • B78-Q2 — What active services currently remain in each existing telecom room/photo reference location? [Open] Impact: Potential outage/cutover risk • B78-Q3 — Are Room 1232 and existing Room 1234 separate rooms or naming/mapping references for the same telecom space? [Open] Impact: PMIS mapping risk • B78-Q4 — Which dedicated cooling units serve each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B78-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B78-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown
80 | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom closet/room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 102 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet interface, thermostat/control point, condensate pump/path, disconnects, and high-temperature alarm. • Existing telecom room/closet may remain active during cutover. Verify existing environmental condition and whether any active equipment remains after migration to Room 102. | • Electrical plans/schedules identify B80-TR102A fed from BUS-B80-MDP and B80-TR102B fed from BUS-B80-E1, with rack receptacles, normal/emergency circuits, CU-1-01, SPD requirements and 30-day load measurement requirements. • Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | • 80T-701 identifies RM102 with 117 WAO total, 98 active ports per survey, 195 total ports per schedule, and 215 total ports with 10% allowance. Rack IDs include TR01-102-1 and TR01-102-2; rack elevation shows 1 new rack plus future rack with switches, Cat6A patch panels, Cat5e patch panel, Fiber LIU, UPS and PDU. • Existing rack elevation shows Cisco switches, legacy optical Fiber LIU on wall, multiple legacy Ortronics 24/48-port patch panels, legacy Cat5e 24-port patch panel, and APC floor UPS. Contractor must transfer existing devices to new rack and protect active services. | • Electrical/telecom plans show access-control scope and camera 102-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, electric strike, camera/VMS integration, and door hardware coordination. • Verify existing security/PACS equipment conditions and whether any existing camera/security device is protected, recabled, or removed during cutover. | • High: Existing conditions for Room 102 and existing 127A/126 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing telecom equipment may remain active during transfer to Room 102 — Document active services, protect in place, identify OIT cutover windows, phasing and rollback plan • High: Room-number mismatch between Tel Closet 127A and photo/rack reference Room 126/127-A — Track both IDs in PMIS and confirm field room signage/owner mapping before punch list and turnover • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: B80-TR102A/B UPS/PDU and panel source coordination could delay energization — Verify panel sources BUS-B80-MDP and BUS-B80-E1, breakers, receptacles, SPD, labels, load measurement and LOTO needs • High: 811 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | • B80-Q1 — Confirm final telecom scope: new Room 102 with existing 127A/126 transition only? [Open] Impact: Room inventory could miss scope • B80-Q2 — What active services are currently fed from existing Room 127A/126 equipment? [Open] Impact: Potential communications/security outage • B80-Q3 — Are Room 127A and Room 126 the same telecom room, or separate locations? [Open] Impact: PMIS mapping and turnover risk • B80-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? [Open] Impact: Cooling continuity unclear • B80-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 102? [Open] Impact: Life-safety acceptance risk • B80-Q6 — Are B80-TR102A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown
82 | • Cover sheet states Building 82 receives a Telecom Enclosure and fire protection scope is excluded. Still verify rated penetrations, 4-inch sleeve, wall/floor openings, temporary firestopping, and life-safety device impacts. • Existing telecom room; verify protection-in-place and firestopping after cable transfer or reuse. | • Mechanical and electrical drawings show IU-1-01 in/near Telecom Room 102 and CU-1-01 outdoor unit. Mechanical notes call for BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency/standby source, condensate pump/path, disconnects, controls, and high-temp alarm. • Existing telecom room may remain active during cutover. Verify existing environmental conditions and whether active equipment remains after transfer to Room 102. | • Electrical plans/schedules identify TE receptacle, CU-1-01, B82-MDP and B82-P-EMER sources, with SPD devices integral to new telecom panelboards. Verify receptacle type, grounding/bonding, emergency source, labels, and circuit loading. • Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | • 82T-701 identifies RM102 with 26 WAO total, 31 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. Rack ID TR01-102-01. Cable tray schedule totals 278 ft on first level. New enclosure includes APC UPS, two PDUs, network switch, Cat6A patch panel and Fiber LIU. • Existing B01-A elevations identify Cisco switches, cable management, two Ortronics 24-port patch panels with 11 and 6 used, existing patch panels and APC floor UPS. Field verify active services and transfer plan to new TE. | • Building 82 appears to create a TE enclosure rather than a full TR door/PACS package. Verify existing cameras/security devices in Room 102 and ensure no camera angle or VMS integration is disrupted. • Keynotes indicate existing cameras are to be retained and re-used. Verify security/access conditions and whether any legacy security equipment is present at existing telecom room. | • High: Existing conditions for new Room 102 TE and existing B01-A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in B01-A may remain active during transfer to new TE in 102 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • High: Cover sheet says TE, but mechanical cooling is included for Room 102 — Confirm scope interpretation with VA/AE and ensure cooling is commissioned if it serves active TE equipment • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding, SPD and labels • High: 278 feet of first-level cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light/HVAC conflicts and firestop assemblies | • B82-Q1 — Confirm final scope: new 12RU wall-mount TE enclosure in Room 102 and existing B01-A transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B82-Q2 — What active services are currently fed from existing B01-A equipment? [Open] Impact: Potential communications/security outage • B82-Q3 — Is Room 102 officially a TE-only scope or a conditioned telecom room with mechanical support? [Open] Impact: Scope and commissioning responsibility unclear • B82-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? [Open] Impact: Cooling continuity unclear • B82-Q5 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? [Open] Impact: Electrical readiness unknown • B82-Q6 — Are all 278 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap
BCH | • Cover sheet states BCH receives a Telecom Enclosure and mechanical/fire protection scope has been excluded. Still verify existing life-safety protection, rated penetrations, 4-inch sleeve fire caulk, temporary firestopping and abandoned penetration patching. • TE-only scope does not appear to require new FEC/fire sprinkler work, but all wall/floor/ceiling penetrations must be sealed and rated assemblies maintained. | • Cover sheet explicitly excludes mechanical scope. Verify existing room ambient conditions are acceptable for TE equipment and that no active network equipment will overheat. • If the final scope is a 45RU new telecom room rather than a small TE, HVAC exclusion should be confirmed with VA/AE because telecom-room heat load may differ from TE assumptions. | • Electrical plan includes first-level electrical work and notes for new wall-mount telecom enclosure, grounding/bonding and camera. Verify circuit source, receptacle type, UPS/PDU load, emergency source if required, grounding/bonding and labels. • BCHT-604 shows 12RU TE equipment with APC UPS and PDUs and also a BCH 45RU new telecom room elevation. Confirm exact UPS/PDU/rack power requirement before acceptance. | • BCHT-101 identifies telecom plan first level and enlarged Room 107. BCHT-604 identifies new telecom room/no existing elevations. There is no BCHT-701 schedule in the drawing index, so WAO/cable-tray totals must be field verified from plans and contractor coordination drawings. • BCHT-604 identifies a 12RU TE elevation: APC UPS, two PDUs, network switch, 48-port Cat6A patch panel and Fiber LIU. Also shows BCH Crescent House Room 107 new telecom room elevation. Confirm governing rack/enclosure and labeling. | • Telecom/electrical notes reference new IP-addressable camera with wall mount at 8'-6" A.F.F. and VMS integration. Verify whether PACS applies; TE buildings typically do not create full TR door/PACS scope. • Verify existing camera/security conditions, protection-in-place, and any recabling or VMS integration required. | • High: Existing conditions for Crescent House Room 107 not field verified — Perform existing conditions survey with photos before mobilization • High: Mechanical and fire protection are excluded despite telecom/electronics installation — Verify existing environmental and life-safety conditions support TE equipment; confirm no dedicated HVAC/FP requirement applies • High: Rack/elevation conflict: TE 12RU enclosure versus BCH Room 107 new telecom room elevation — Submit RFI/confirm with AE which elevation governs and map room/equipment in PMIS • Critical: Active services and existing devices may require phasing/temporary service — Document active services, maintain existing service, use phasing plan, temporary utilities and OIT cutover windows • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: Cable tray, sleeve and pathway quantities not scheduled in a BCHT-701 sheet — Require coordination drawings showing route, supports, fill, penetrations, sleeves and cable counts | • BCH-Q1 — Confirm final BCH scope: Room 107 TE enclosure only, or a new telecom room/rack buildout? [Open] Impact: PMIS scope and acceptance criteria unclear • BCH-Q2 — Why does BCHT-604 show a T78 12RU TE enclosure and a separate BCH Crescent House Room 107 new telecom room elevation? [Open] Impact: Rack/equipment mapping conflict • BCH-Q3 — What active services currently serve Crescent House and where are existing terminations located? [Open] Impact: Cutover/outage risk • BCH-Q4 — What is the approved power source, receptacle type and circuit capacity for the new UPS/PDU? [Open] Impact: Electrical readiness unknown • BCH-Q5 — Is existing HVAC/ambient condition acceptable for TE/network equipment since mechanical scope is excluded? [Open] Impact: Heat/load risk • BCH-Q6 — Are cable tray route, sleeve locations, supports and firestopping details shown/field verified without a BCHT-701 schedule? [Open] Impact: Install delay or firestop gap
MCR | • MCR has full fire protection scope including wet pipe and clean-agent fire suppression system. Verify preaction/clean-agent design, agent release interface, fire alarm matrix, detection, abort/release stations, room integrity and acceptance testing. • Verify fiber entrance room protection, rated penetrations, firestopping, detector/strobe coverage and no gaps after cable tray installation. • Verify sprinkler/clean-agent coverage around MDA equipment, fire alarm devices, rack clearance and final firestop assemblies. • Verify clean-agent coverage, detector placement, alarm interfaces, and open cabinet airflow protection. • Existing systems must remain protected during temporary fiber, umbilical cord and core relocation work. Verify no impairment without approved fire watch/impairment plan. | • Telecom notes call for indoor computer room air conditioner (CRAC) units tied to building management system. Mechanical sheets included; verify redundant capacity, setpoints, humidity, condensate, controls, alarms and emergency power. • UPS rooms/equipment require thermal load validation, ventilation, emergency power and alarm integration. Verify battery/UPS environmental requirements. • Verify airflow/cold aisle/hot aisle assumptions, blanking panels, floor/ceiling distribution and temperature monitoring. • Server cabinets and patch fields require stable 24/7 cooling and monitoring. Confirm no local hot spots at dense LIU/patch panel zones. • During split-core temporary phase, existing MCR/server equipment remains active. Verify existing cooling remains in service until cutover and decommissioning are complete. | • Electrical set includes site plan, enlarged MCR plans, one-lines and schedules. Verify switchboard/service, ATS/generator integration, normal/emergency/UPS distribution, grounding, lightning protection, SPD, load measurements and commissioning. • MDA rack elevations include new 4-post floor cabinets, LIUs and network elements. Verify redundant A/B power feeds and PDU arrangements. • HDA cabinets include server cabinet front/rear elevations with patch panels and active equipment. Confirm A/B feed separation, PDU mounting, load capacity and labels. • Existing rack elevations identify multiple APC/Chatsworth/HP PDUs, APC Smart UPS and Eaton 9PX units. Verify what transfers, what stays, and temporary power during migration. • New MCR is standalone critical infrastructure. Verify utility service, generator/ATS paths, emergency distribution, grounding electrode and ductbank/site electrical coordination. | • MCRT-101 shows new MCR with MDA-A/B, HDA-A/B, UPS-A/B, cameras and fiber path legend. MCRT-701 shows 10 WAO total, 720 WAO available, 98.1% expansion capacity, 10 total ports with 20% allowance and 359 ft cable tray. • MCRT-701 Data Device and Circuit Schedule - Fiber Entrance Room 1: outlets 31-A/B/C/D plus security devices 07-CAM-03/04/07/08/11; Rack ID TR01-031-1. • MCRT-607: MDA A/B racks contain horizontal distribution LIUs, hybrid FOC, 48x Cat6A to HDA, and reserved LAN/spine/aggregation elements. Maintain A/B path separation. • MCRT-608/609: HDA A/B include 48-port Cat6A patch panels, HD fiber LIUs, backbone side A/B LIU and server cabinet arrangements. • Existing MCR rows 1-3 and B61 server cabinet transfer references are extensive. Maintain service using temporary fiber/umbilical cords and phased core relocation. | • MCRT-101 identifies cameras 07-CAM-01 through 07-CAM-12 around the MCR. Telecom notes call for IP-addressable network cameras integrated into existing VMS and PACS/access-control systems including iSTAR Edge/Avigilon ACM controller. • MCRT-701 includes security camera/data devices assigned to TR01-031-1. Confirm camera IDs, mounting, cabling, and VMS commissioning. • Verify camera coverage, door/access points, VMS monitoring and access control zones for critical equipment. • Verify coverage of HDA cabinets, doors, motion detection and any lockable cabinet/security requirements. • Existing security systems must remain functional during transition; protect existing camera angles and access controls until final turnover. | • Critical: MCR is a new standalone critical facility with 120-sheet multi-discipline scope — Use discipline-by-discipline pre-install checklist, coordination drawings, third-party inspections and commissioning tracker • Critical: Existing MCR/server/core equipment transfer may interrupt hospital network operations — Require detailed OIT cutover plan, temporary fiber/umbilicals, rollback plan, VA activation windows and after-hours phasing • Critical: A/B fiber path diversity and backbone commissioning not verified — Verify OSP/ISP Path A/B routing, no intermediate splices, test results, labeling and geographic diversity • Critical: UPS-A/B, ATS/generator, panel source and PDU coordination could delay activation — Verify one-line, load banks, breaker settings, panel labels, generator/ATS tests, UPS start-up and A/B power mapping • Critical: CRAC capacity, redundancy, condensate, BMS/FMS alarms and emergency power not verified — Confirm mechanical schedules, CRAC start-up, controls, alarm points, emergency source, environmental monitoring and hot/cold aisle performance • Critical: Clean-agent/preaction/fire alarm interface and room integrity acceptance risk — Track clean-agent calculations, room integrity test, release/abort stations, FA matrix, sprinkler/preaction tests and AHJ/third-party acceptance | • MCR-Q1 — Confirm final room naming and PMIS mapping: MCR Room 107, Fiber Entrance Room 031, Existing 107/137 server/MCR references. [Open] Impact: Room inventory and turnover mapping could be wrong • MCR-Q2 — What existing core/server/rack equipment is being relocated from the existing MCR/server rooms, and what remains? [Open] Impact: Cutover and outage risk • MCR-Q3 — What is the approved MCR activation sequence and required VA/OIT hold points? [Open] Impact: Schedule/cutover impact • MCR-Q4 — Are UPS-A/B, generator/ATS and emergency power paths commissioned and mapped to each rack/PDU? [Open] Impact: Electrical readiness unknown • MCR-Q5 — Are CRAC units fully commissioned with BMS/FMS alarms, redundancy and emergency power? [Open] Impact: Cooling continuity risk • MCR-Q6 — Are clean-agent/preaction/fire alarm systems fully designed, tested and accepted? [Open] Impact: Life-safety acceptance risk
SPEC | • No fire / life safety items captured for this building. | • No hvac / cooling items captured for this building. | • No electrical / ups items captured for this building. | • No telecom / fiber items captured for this building. | • No security / pacs / cctv items captured for this building. | • No owner risks items captured for this building. | • No open questions items captured for this building.
Campus | • No fire / life safety items captured for this building. | • No hvac / cooling items captured for this building. | • No electrical / ups items captured for this building. | • No telecom / fiber items captured for this building. | • No security / pacs / cctv items captured for this building. | • No owner risks items captured for this building. | • No open questions items captured for this building.
SITE | • General notes require fire lanes, hydrants and fire department access roads operational at all times; maintain egress and provide fire watch/temporary protection when required. • Trench barricades, accessible parking/public access and right-of-way impacts must be coordinated with owner prior to construction. • Rated wall/floor penetrations must be firestopped; temporary firestopping required if penetrations remain open between shifts. • Backbone work affects facility operations. Any required shutdowns must be limited to one at a time and coordinated with approved phasing plan. | • No hvac / cooling items captured for this building. | • Electrical site plans ES101/ES401 are included. Existing utility locations are approximate; coordinate electrical vaults, underground electrical, storm drain manholes and sanitary manholes. • Locking covers and handhole/manhole locations must be field verified. Confirm bonding/grounding requirements where metallic components are present. • T-601 shows WAN/provider fiber entrances and new fiber Path A/B to the MCR. Coordinate with Century Link/service provider and MCR activation. • Coordinate conduit penetrations with building electrical/telecom/firestop scope and avoid conflicts with existing services. | • Legend identifies new fiber in A route, B route, and A+B routes in separate conduits. Confirm no cross-connect gaps at THHs/manholes. • Site one-line shows WAN fiber from service provider and temporary/provider extension pathways. Coordinate with MCR activation and OIT. • Each building tie-in must be tested, labeled, and accepted before connection to active operations. • T-601 one-line lists THH #1-#19 and path counts such as 6 Path A + 4 Path B, 6 Path A + 6 Path B, 7 Path A + 7 Path B, 5 Path A + 4 Path B, and 9 Path A + 7 Path B. | • Coordinate staging, access, material storage, noisy work, utility interruption, trench barricades and public access with owner. • General notes specifically identify accessible parking and public right-of-way impacts; temporary barricades must prevent injury and protect parking signage. • Hand digging at existing utility crossings is in base bid. Confirm permits, Dig Safe, VA utility locate and escort requirements before excavation. | • Critical: Existing utility locations are approximate and field conditions may vary from survey — Complete utility locate, GPR review, potholing/hand-digging at crossings and VA utility coordination before excavation • Critical: A/B fiber path separation may not be maintained through common ductbank or congested areas — Verify separate conduits, route diversity, THH labels, T-601 path counts and as-built documentation • High: Concrete ductbank could be backfilled before inspection — Establish inspection hold point; trench remains open until concrete duct inspection and photos are accepted • Critical: WAN/provider fiber and MCR activation sequence could delay campus cutover — Coordinate Century Link/service provider, temporary fiber, provider extension, MCR readiness and OIT activation plan • High: Trenching/restoration may disrupt accessible parking, fire lanes, public access and campus traffic — Submit traffic/pedestrian/staging plan, maintain fire lanes/hydrants and restore surfaces to match existing • High: Building entry penetrations/firestopping may not align with building PMIS packages — Cross-check every site tie-in against building assessment, T-101 continuation sheets and firestop photos | • SITE-Q1 — Confirm final list of all site fiber buildings and whether Buildings 1-22, 33, 61, 62, 70, 78/78A, 80, 81, 82, Crescent House and MCR are included in one site backbone turnover package. [Open] Impact: Scope and turnover package mapping unclear • SITE-Q2 — Which THH/manhole numbers are new versus existing, and which require locking cover replacement only? [Open] Impact: Structure inventory and inspection scope unclear • SITE-Q3 — Are all A and B routes physically diverse enough and in separate conduit wherever common ductbank is used? [Open] Impact: Redundancy risk • SITE-Q4 — What are the approved utility-locate/potholing requirements before excavation at each crossing? [Open] Impact: Utility strike risk • SITE-Q5 — What inspection hold points are required for ductbank forms, conduit placement, concrete pour, pull string, mandrel and backfill? [Open] Impact: QA acceptance risk • SITE-Q6 — Are directional boring alternatives allowed anywhere, or is all base-bid work trenching unless separately approved by Government? [Open] Impact: Means/methods and cost/schedule risk

## PMIS_Trade_Notes (hidden)
Building_ID | Display_Label | Assessment_Sheet | Fire / Life Safety | HVAC / Cooling | Electrical / UPS | Telecom / Fiber | Security / PACS / CCTV | Owner Risks | Open Questions | Major Blocker
01 | B01 | B01_Assessment | • Full fire protection scope included. Verify sprinkler head modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL firestop systems. • Existing telecom room; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. • Existing telecom room; verify fire alarm/sprinkler impacts, protection-in-place and final firestop at cable changes. • Existing second-level telecom room; verify riser penetrations, firestopping and protection-in-place. | • Mechanical drawings show IU-1-01 split-system indoor unit and CU-1-01 outdoor unit for Room 107. Notes call for condensate pump, pumped condensate line, BACnet adapter adjacent to unit, FMS integration, room temperature/humidity points and alarms. Confirm capacity, emergency source, condensate path, controls and startup. • Existing basement telecom equipment may remain active during cutover. Verify environmental conditions and whether active equipment remains after migration. • Existing first-level equipment may remain active during transfer; verify temperature, ventilation and protection of active gear. • Existing second-level equipment may remain active until cutover; verify existing cooling/ambient conditions and no overheating. | • Electrical plans/schedules identify B01-TR107A and B01-TR107B, rack receptacles, normal/emergency receptacles, redundant vertical PDUs, CU-1-01, access controller, lighting/receptacle circuits, SPDs integral to new telecom panels, and 30-day load measurement requirements before panel renovation. • Existing B02 rack elevations show UPS on floor and Tripp Lite Smart Pro UPS; verify active source circuits and transfer requirements. • Existing 138 rack elevation shows APC UPS floor and patch panels; verify active source circuits and transition. • Existing Room 282 equipment includes active rack gear and patch panels; verify source circuits, UPS/PDU condition and final decommission/retain scope. | • 01T-701 identifies RM107 with 96 WAO total, 88 active ports per survey, 146 total ports per schedule, and 161 total ports with 10% allowance. Cable tray schedule totals 394 ft: 58 ft basement, 212 ft first level and 124 ft second level. Rack ID TR01-107-1. • Existing B02 racks/TE support active services and legacy equipment. Contractor must field verify equipment to be demolished or transferred and provide phasing plan. • Existing Room 138 racks and patch panels act as transition/legacy equipment point. Verify active service labels and transfer sequence. • Existing Room 282 racks and patch panels act as second-level transition point. Verify all active services, WAP/camera cabling, and riser pathway. | • Electrical/telecom plans show new access control, power supply/battery backup for PACS, HDP12/FIPS-compliant PIV-ready card reader with PIN pad, and camera 107-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration and door hardware coordination. • Verify existing security/CCTV equipment and any retained cameras. Maintain camera angles where existing security cameras are recabled. • Verify existing security/access conditions and protection-in-place during rack transfer. • Verify second-level existing security/CCTV impacts during cabling and equipment transfer. | • High: Existing conditions for Room 107 and transition rooms B02/138/282 not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing equipment may remain active during transfer to Room 107 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat, humidity and high-temp alarms • High: B01-TR107A/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPD, labels, 30-day load measurement and LOTO needs • High: 394 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications across basement/first/second levels — Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | • B01-Q1 — Confirm final telecom scope: new Room 107 with existing B02, 138 and 282 transition/transfer points? [Closed] Impact: Room inventory could miss scope • B01-Q2 — What active services are currently fed from existing Rooms B02, 138 and 282? [Closed] Impact: Potential communications/security outage • B01-Q3 — What equipment from existing racks transfers to new Room 107 versus remains/decommissions? [Closed] Impact: Cutover and rack elevation risk • B01-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 107? [Closed] Impact: Cooling continuity unclear • B01-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 107? [Closed] Impact: Life-safety acceptance risk • B01-Q6 — Are B01-TR107A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Closed] Impact: Electrical readiness unknown | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning.
02 | B02 | B02_Assessment | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Verify second-level TR sprinkler/fire alarm modifications, FEC location, cable tray penetrations, and temporary/final firestopping. • Verify third-level TR sprinkler/fire alarm modifications, FEC location, riser penetrations and firestopping. • Existing telecom rooms; verify FP/FA protection-in-place and seal penetrations after cable removal/reuse. | • Electrical schedule references CU-1-01, CU-2-01 and CU-3-01 on B02-TR141B; mechanical sheets include dedicated TR cooling. Confirm which indoor/outdoor unit serves Room 141, capacity, emergency power, condensate, controls/BACnet and alarms. • Confirm dedicated cooling equipment serving Room 236, condensate route, 24/7 operation, emergency source and FMS/BACnet high-temperature alarm. • Confirm dedicated cooling equipment serving Room 342, condensate route, controls, emergency source and alarm integration. • Existing telecom equipment may remain active during cutover. Verify ambient temperature/cooling protection until migration complete. | • Electrical one-line/schedules identify B02-TR141A/B with rack receptacles, lighting/receptacles, SPDs integral to new telecom panelboards and cooling equipment references. Verify source, 30-day load measurement, LOTO and labels. • Electrical one-line/schedules identify B02-TR236A/B with rack receptacles, lighting/receptacles, SPDs and normal/emergency power requirements. Verify source and rack PDU mapping. • Electrical one-line/schedules identify B02-TR342A/B with rack receptacles, lighting/receptacles and SPDs. Verify source panels and UPS/PDU circuits. • Existing racks/panels remain active during transfer; verify power source, UPS status and temporary power needs. | • 02T-701 identifies RM141 with 211 WAO total, 215 active ports, 322 scheduled ports, 354 ports with allowance. Rack IDs TR01-141-01/02. Cable tray schedule total includes 1,069 ft first-level cable tray. • 02T-702 identifies RM236 with 179 WAO total, 178 active ports, 314 scheduled ports and approx. 345 with allowance. Rack IDs TR01-236-01/02. Verify second-level cable tray, riser and cutover from existing 282/236 scope. • 02T-703 identifies RM342 with 274 WAO total, 96 active ports, 353 scheduled ports, 388 with allowance. Rack IDs TR01-342-01/02. Verify third-level cable tray and high outlet count. • Existing B-06/141/236 racks support legacy services. Field verify all active circuits, existing patch panels, labels, and transfer plan before cutover. | • Plans show 174-CAM-01 associated with the first-level TR area and PACS/security requirements. Verify camera/VMS integration, access controller/power supply, CR/RX/DC/ES/MD and door hardware. • Plans show 236-CAM-01. Verify camera/VMS integration, access control, door hardware, motion/detection devices and power. • Plans show 342-CAM-01 and 342A-CK-A. Verify camera/VMS integration and access control/security rough-in. • Maintain existing camera angles when re-cabling and protect existing PACS/equipment racks during transfer. | • High: Existing conditions for Rooms 141/236/342 and existing B-06/141/236 not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing equipment may remain active during transfer to new TRs — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified — Confirm each IU/CU serving each TR, power source, condensate route, controls, BACnet, thermostat and high-temp alarms • High: B02-TR141/236/342 A/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPDs, labels, 30-day load measurement and LOTO needs • High: 2,560 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications across several floors — Require cutover plan, test records, labels, as-builts, OIT coordination and VA acceptance before active connection | • B02-Q1 — Confirm final telecom scope: new Rooms 141, 236 and 342 with existing B-06/141/236 transition points? [Open] Impact: Room inventory could miss scope • B02-Q2 — What active services are currently fed from existing Rooms B-06, 141 and 236? [Open] Impact: Potential communications/security outage • B02-Q3 — What existing equipment is transferred, relocated, removed or protected in Rooms 141 and 236? [Open] Impact: Cutover and rack elevation risk • B02-Q4 — Which IU/CU pair serves each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B02-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of Rooms 141, 236 and 342? [Open] Impact: Life-safety acceptance risk • B02-Q6 — Are B02-TR141/236/342 A/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance.
03 | B03 | B03_Assessment | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent/CO2 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, temporary firestopping and final UL systems. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal penetrations after fiber/cable transfer or reuse. • Existing DMARC/telecom room; fire alarm/sprinkler and firestopping must remain in service during transfer. • Coordinate ceiling removal, temporary barriers/upright sprinklers if ceiling tiles remain open, and firestopping at all rated penetrations. | • Electrical schedule references CU-01 on B03-TR101CB and mechanical package includes dedicated TR cooling. Confirm indoor/outdoor unit serving Room 101E, capacity, emergency source, condensate route, controls/BACnet and high-temperature alarm. • Existing basement telecom equipment may remain active during transfer. Verify ambient temperature/cooling protection until migration is complete. • Existing DMARC/fiber services may remain active during cutover; verify existing environmental conditions and heat load if equipment remains. • No dedicated HVAC for WAO areas; maintain infection control/IAQ and ceiling restoration requirements. | • Electrical one-line/schedules identify B03-TR101CA/B with rack receptacles, TR receptacles, access controller, CU-01 on B03-TR101CB, SPDs integral to telecom panels, PXR20 trip units, and 30-day load measurement requirements. • Existing Room 107 rack elevation shows UPS on floor and legacy telecom equipment. Verify active source circuits and transfer requirements. • Existing DMARC plan shows existing branch panel and patch panel removal/relocation scope. Verify source circuits before demolition or transfer. • Verify power/data coordination at outlets, cameras, WAPs, Centrak/clock devices and hard-lid ceiling locations. | • 03T-701 identifies RM101E with 143 WAO total, 213 active ports, 187 scheduled ports and 206 total ports with 10% allowance. Cable tray schedule totals 961 ft: 615 ft basement level and 346 ft first level. Rack IDs TR01-101E-1 and TR01-101E-2. • Existing Room 107 rack supports legacy active services; verify B3-LB-B13-TC-FIBER equipment inventory, fiber LIU, patch panels, Cisco switch and UPS before cutover. • Existing DMARC/telecom room 101C includes patch panels/cabinet/branch panel and 101C-CAM-01; protect active provider/fiber/DMARC services until new fiber/rack work is accepted. • Existing ports replaced; 3- and 4-port outlets reduced to two Cat6A ports where coordinated. WAPs remain protected in place while cabling/faceplate/jack are replaced. | • Plans require PACS for TR doors and electrical details include access-controlled door rough-in. Verify access controller, power supply/battery backup, CR/RX/DC/ES/MD devices, reader, strike and door hardware coordination. • Enlarged plan and schedule identify 101C-CAM-01 and 101C-CK-A. Verify camera/VMS integration, existing camera angles and protection-in-place. • Verify existing security/CCTV/PACS impacts during basement telecom room transfer. • Maintain existing camera angles when re-cabling; verify WAP/security/clock/Centrak devices are relabeled and tested. | • High: Existing conditions for Room 101E and transition rooms 107/101C not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • Critical: Existing DMARC/fiber/telecom equipment may remain active during transfer to Room 101E — Document active services, protect in place, identify OIT/provider cutover windows, phasing, rollback path and temporary utilities • Critical: Dedicated cooling assignment, emergency power, condensate, BACnet and alarms not verified — Confirm CU-01/IU serving Room 101E, power source, condensate, controls, BACnet, thermostat and high-temp alarms • High: B03-TR101CA/B UPS/PDU and panel source coordination could delay energization — Verify panels, breakers, receptacles, SPDs, PXR20 trip units, labels, 30-day load measurement and LOTO needs • High: 961 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies • Critical: Telecom/fiber cutover could affect active hospital communications and provider/DMARC services — Require cutover plan, test records, labels, as-builts, OIT/provider coordination and VA acceptance before active connection | • B03-Q1 — Confirm final telecom scope: new Room 101E with existing Basement Room 107 and existing DMARC Room 101C transition points? [Open] Impact: Room inventory could miss scope • B03-Q2 — What active services are currently fed from existing Room 107 and DMARC Room 101C? [Open] Impact: Potential communications/provider outage • B03-Q3 — What existing equipment transfers to new Room 101E versus remains/decommissions? [Open] Impact: Cutover and rack elevation risk • B03-Q4 — Which IU/CU pair serves Room 101E and is it on emergency/backup power? [Open] Impact: Cooling continuity unclear • B03-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 101E? [Open] Impact: Life-safety acceptance risk • B03-Q6 — Are B03-TR101CA/B sources, rack receptacles, SPDs, labels and 30-day load measurements approved? [Open] Impact: Electrical readiness unknown | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance.
04 | B04 | B04_Assessment | • Fully sprinklered building; basement TR requires verification of sprinkler coverage and impairment planning. • FEC with clean-agent 2A:10B:C extinguisher within 75 ft; TR open to deck; maintain rated assemblies. • Verify sprinkler/fire alarm device locations and firestop for riser/pathway penetrations. | • Verify dedicated cooling for two-rack basement TR and whether unit/controls/condensate are backed up. • Verify dedicated cooling and coordination with open-to-deck room, racks, cable tray, and access control. • Verify cooling unit, routing, condensate, controls, and emergency/backup power path. | • Panel schedule shows B04-NPA-TR in Telecom Room B05, feeding B04-TRB05A/B; TRB05A includes rack receptacle and branch circuits. • Panel schedule identifies B04-TR141A 60A 3-pole load; verify rack/UPS/PDU circuiting. • Panel schedule identifies B04-TR244A 60A 3-pole load; confirm panel/circuit locations and source. | • New rack elevations show two 4-post floor racks with UPS, Zone PDU, cable managers, network switches, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • New rack elevation shows one 4-post rack plus future rack; includes UPS, future Zone PDU, switches, cable managers, Cat6A patch panels, Cat5E patch panel, and Fiber LIU. • TR/panel identified; verify rack elevation and pathway details against 04T sheets. | • Verify access-controlled TR door, camera, and VMS/PACS integration. • Architectural notes require door/access control coordination; verify card reader/electric strike rough-in. • Verify room security details and device integration with VA systems. | • High: Existing conditions across basement/first/second TR areas not verified — Perform existing conditions survey with photos before mobilization • High: Basement TR routing may conflict with existing utilities / abatement areas — Coordinate hazardous material survey, utility locations, penetrations, and pathway routing • High: 1-hour fire/smoke-rated envelope and 45-minute door not field verified — Inspect rated walls, door/frame, ceiling/open-to-deck conditions, and penetrations • Critical: Cooling emergency power / 24/7 continuity not verified — Confirm source power for indoor/outdoor units, controls, condensate pumps, and alarms • High: UPS/PDU/rack electrical source and load coordination unresolved — Verify panel schedules, source, SPD, breaker sizes, labeling, and load measurements • Critical: Telecom/fiber cutover could affect active hospital communications — Require phasing plan, test results, and VA/OIT acceptance before cutover | • B04-Q1 — Confirm final TR room list: B05, 141, and 244A; are there additional served-from rooms? [Open] Impact: Incomplete room inventory / missed scope • B04-Q2 — Are B05, 141, and 244A cooling systems on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B04-Q3 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B04-Q4 — What is the approved migration and cutover sequence for active Building 04 services? [Open] Impact: Potential communications outage • B04-Q5 — Are hazardous/abatement impacts cleared for basement and first-level penetrations/floor work? [Open] Impact: Work stoppage or exposure risk • B04-Q6 — Are all B04 panelboards/feeders/breakers/SPDs/load measurements approved before renovation? [Open] Impact: Electrical delay or overload risk | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open.
05 | B05 | B05_Assessment | • Cover sheet note states mechanical and fire protection scope excluded; still verify firestopping and existing fire alarm/life safety impacts. • Existing conditions only; verify protection-in-place and no unsealed penetrations after cabling. | • Mechanical scope is excluded for Building 05; verify TE heat load is acceptable in existing space and does not require added cooling. • Existing wall/wall-mount TE area; verify existing environmental conditions during field survey. | • 05T-604 shows APC UPS, two PDU L-530 input / NEMA 5-20 output units, 1200V outlet UPS, and 1200V outlet PDU; verify actual electrical schedule/panel/circuit source. • Existing elevation shows floor UPS and legacy wall-mounted TE equipment; protect active equipment until cutover. | • New Room 150 Telecom Enclosure: 12RU TE with APC UPS, PDUs, cable managers, 48-port angled patch panels, 48-port Cat6A patch panel, and Fiber LIU. • Existing Room 153-A wall/wall-mount TE contains Cisco switches and legacy 24-port patch panels; confirm cutover, reuse, demo, and records. | • Project general scope includes CCTV and PACS for telecom spaces; verify whether TE location receives camera/access control or is served by existing room controls. • Verify existing security protection and whether access-control work is needed for existing TE area. | • High: Telecom Enclosure installation details not field verified — Survey wall/backing, clearances, power, conduit/wireway, and access path before installation • Critical: Existing legacy equipment/cabling may remain active during cutover — Document active services, create cutover plan, protect-in-place until new TE is operational • Medium: Mechanical/fire protection scope excluded may hide interface risks — Confirm no added cooling/sprinkler work is required and document basis for N/A • High: Electrical panel/circuit source for TE equipment not confirmed — Verify 05E-401/501/601/701 schedules, UPS/PDU receptacles, labels, and emergency power source • High: Firestopping/penetration sealing still required despite fire protection scope exclusion — Inspect all new and reused conduits, sleeves, wall/floor penetrations, and temporary firestop • Medium: Commissioning / acceptance documentation may be treated as minor due to TE scope — Track testing, labeling, OIT acceptance, third-party inspections, and as-builts | • B05-Q1 — Confirm final TE room/location: Room 150 new TE and Room 153-A existing TE transition point? [Open] Impact: Room inventory could be wrong • B05-Q2 — What active services are currently fed from the existing 153-A TE/legacy patch panels? [Open] Impact: Potential communications outage • B05-Q3 — What is the approved cutover sequence from existing 153-A equipment to new Room 150 TE? [Open] Impact: Cutover risk • B05-Q4 — Which electrical panel/circuit serves the Room 150 UPS/PDU outlets? [Open] Impact: Power source cannot be verified • B05-Q5 — Is emergency/backup power required or provided for the TE UPS/PDU source? [Open] Impact: Continuity requirement unclear • B05-Q6 — Are firestopping locations and surface raceway/conduit routes shown and coordinated? [Open] Impact: Rated assembly/firestop risk | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified.
06 | B06 | B06_Assessment | • Existing equipment area; verify no cabling penetrations are left unsealed. • Fully sprinklered building; verify sprinkler modifications, fire alarm devices, FEC location, and impairment/fire watch needs. • Architectural enlarged views call for 1-hour fire/smoke-rated walls, 45-minute door/frame, and FEC within 75 ft. | • Verify basement equipment environmental condition and any heat/load issues during cutover. • Mechanical enlarged plan shows new indoor unit IU-1-01 and outdoor CU-1-01; confirm 208V emergency power, BACnet adapter, thermostat, condensate route. • Mechanical enlarged plan shows new indoor unit IU-2-01 and outdoor CU-2-01; confirm 208V emergency power, condensate and controls. | • Existing UPS on floor shown at B-01; protect active service and confirm any transition/demo requirements. • Panel schedule shows B06-EP-TR in Telecom Room 178; B06-TR178A/B panels and SPD requirements; load measurement required prior to panel renovation. • Panel schedule identifies B06-TR233A/B in Telecom Room 233; verify source, circuits, rack receptacles and emergency power. | • Existing Cisco switches, legacy 48-port patch panels, wall/wall-mount TE and floor UPS. • Existing Room 178 rack elevations show multiple existing 2-post racks; new electrical, cable path, grounding and cutover require verification. • Room 233 future new rack elevation shows UPS, network switches, cable managers, Cat6A patch panels, Cat5E patch panel and Fiber LIU. | • Verify existing basement access/security while protecting active equipment. • Electrical enlarged plan references existing card reader to remain/protect in place and new tri-tech motion sensor; verify PACS/CCTV integration. • Verify door hardware/access control, motion sensor, camera, and VA security integration. | • High: Existing conditions across B-01, 178 and 233 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing basement equipment may remain active during cutover — Document active services and protect in place until new system is tested and accepted • Critical: Electrical panel replacement/new telecom power could interrupt active systems — Coordinate load measurement, panel renovation, shutdowns and temporary power plan • High: Room 233 conversion/rated wall and door work may impact adjacent patient toilet/private bath areas — Verify phasing, barriers, infection control and temporary life-safety provisions • Critical: Dedicated cooling emergency power, controls, condensate and BACnet interface not verified — Confirm emergency power source, disconnects, condensate routes, BACnet adapter and high-temp alarms • Critical: Fire alarm/sprinkler impairments and penetrations may affect occupied operations — Track impairments, fire watch, temporary firestop and third-party reports | • B06-Q1 — Confirm final TR/TE scope: B-01 existing equipment, Room 178, and Room 233? [Open] Impact: Room inventory could miss scope • B06-Q2 — What active services are fed from existing B-01 and Room 178 legacy equipment? [Open] Impact: Potential communications outage • B06-Q3 — What is the approved cutover sequence for B-01, 178 and 233? [Open] Impact: Cutover risk • B06-Q4 — Are IU-1-01/CU-1-01 and IU-2-01/CU-2-01 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B06-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B06-Q6 — Are all panel load measurements, replacement panels, breakers, SPDs and labels approved? [Open] Impact: Electrical readiness unknown | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open.
07 | B07 | B07_Assessment | • Fully sprinklered building; basement TR requires sprinkler coverage verification, firestop at cabling/sleeves and impairment coordination. • Architectural notes require clean-agent 2A:10B:C extinguisher within 75 ft, 45-minute rated door/frame and rated wall construction; verify FA/FP modifications. | • Mechanical schedule lists 18,000 BTUH wall-mounted IU-0-01 and CU-0-01; verify exact room assignment, emergency power, condensate, controls and high-temp alarm. • Mechanical schedule lists 36,000 BTUH wall-mounted IU-2-01 and CU-2-01; electrical enlarged plan shows IU-2-01 at TR 228A; verify emergency power and condensate route. | • Electrical enlarged plans identify B07-TRB18A/B circuits serving basement TR equipment; verify panel source, receptacles, SPD, emergency source and load measurement. • Electrical enlarged plans identify B07-TR228A/B circuits serving TR 228A equipment and IU-2-01; verify rack receptacles, cooling power, SPD and labels. | • 07T-604 rack elevation: 1 rack plus future; includes UPS, future Zone PDU, cable managers, network switches, three 48-port Cat6A angled patch panels, 24-port Cat5E patch panel and Fiber LIU. • TR 228A is shown on second-level telecom/electrical enlarged plans; verify rack elevation, fiber paths, Cat6A replacement, labeling/testing and VA acceptance before cutover. | • Verify access control, door hardware and CCTV/PACS integration for basement TR. • Architectural notes require access control hardware modifications at new rated door; verify card reader, electric strike, door position switch, motion sensor and camera. | • High: Existing conditions for B-18 and 228A not field verified — Perform existing conditions survey with photos before mobilization • High: Basement TR conversion may conflict with existing utilities, office finishes or active pathways — Verify routing, clearances, penetrations, existing conduit and access before work • High: Second-floor rated wall/door work and exterior furring wall/window enclosure could affect schedule — Coordinate architectural work, door/frame, wall rating, furring wall, finishes and infection control barriers • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignments, emergency source, BACnet/interface, condensate pump routing and alarm points • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B07-TRB18A/B and B07-TR228A/B panel schedules, circuit labels, SPDs and load measurements • Critical: Telecom/fiber cutover may affect active hospital communications — Require cutover plan, test results, OIT coordination and VA acceptance before active connection | • B07-Q1 — Confirm final TR scope: B-18 basement and 228A second floor only? [Open] Impact: Room inventory could miss scope • B07-Q2 — Are IU-0-01/CU-0-01 assigned to B-18 and IU-2-01/CU-2-01 assigned to 228A? [Open] Impact: Cooling scope unclear • B07-Q3 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cooling continuity not confirmed • B07-Q4 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B07-Q5 — What active services are currently fed from B-18 and/or existing pathways serving 228A? [Open] Impact: Potential communications outage • B07-Q6 — Are all B07 panelboard sources, circuits, SPDs, labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open.
08 | B08 | B08_Assessment | • Existing equipment area; verify no new penetrations are left unsealed and active systems remain protected. • Door schedule shows 45-minute door; verify fire/smoke requirements, FEC requirement applicability, firestopping and temporary barriers. • Architectural notes require new 45-minute door, clean-agent 2A:10B:C extinguisher within 75 ft, open-to-deck telecom room and 1-hour fire/smoke-rated existing wall upgrades. | • Verify existing environmental conditions and whether active legacy equipment remains during cutover. • Field verify whether TE equipment load requires cooling or if served by existing building HVAC. • Mechanical schedule lists IU-2-01/CU-2-01 at 36,000 BTUH; verify room assignment, emergency power, condensate pump/route, BACnet controller and controls. | • Existing rack elevation shows floor UPS and legacy equipment; protect active service and verify transition/demo requirements. • Electrical schedule includes TE receptacle Room B12B; confirm panel/circuit source and if B12B is served from telecom panel. • Electrical schedule identifies B08-TR2065AB in Telecom Room 2065A with TR receptacles, rack receptacles, lighting, access controller, CU-2-01 and SPD notes; verify B08-TR2065AA source/scope. | • Existing Room B-15 rack elevations show wall/wall-mounted TE, legacy 24/48-port patch panels, legacy Fiber LIU and UPS. • Telecom schedule uses Rack ID TE01-B12B-1; 80 WAO total, 159 active ports per survey, 116 total ports per schedule, and 128 total ports with 10% allowance. • New Room 2065A rack elevations show two 4-post floor racks; Rack 1 includes Fiber LIU, 24-port Cat5E patch panel, four 48-port Cat6A patch panels, network switches, Zone PDU and UPS; Rack 2 includes future switches and UPS. | • Verify existing basement access/security while protecting active equipment. • 45-minute door shown; verify access-control hardware applicability and whether TE is secured. • Door schedule/hardware note requires coordination with electrical/access control; verify card reader, electric strike, door position, motion sensor, camera and VA integration. | • High: Existing conditions for B-15, B12B and 2065A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing basement legacy equipment may remain active during cutover — Document active services, protect in place and define cutover/demo sequence • High: Basement B12B appears as Office in architectural schedule but TE in telecom/electrical schedules — Field verify actual TE location, room name, door/wall rating and panel/cable routing • High: Second-floor Telecom Room conversion includes rated wall/door/open-to-deck work and possible hazardous material impacts — Coordinate architectural work, dust barriers, floor abatement, FEC and rated assemblies before construction • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignment, emergency source, BACnet/interface, condensate routing and alarm points • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B08-TR2065AA/AB panel schedules, rack receptacles, SPD, labels and load measurement requirements | • B08-Q1 — Confirm final scope: existing B-15 equipment, B12B TE/cabling area, and new TR 2065A? [Open] Impact: Room inventory may miss scope • B08-Q2 — What active services are currently fed from existing B-15 equipment? [Open] Impact: Potential communications outage • B08-Q3 — Is B12B truly a TE/equipment location or only a cabling pathway/service area? [Open] Impact: Scope ambiguity • B08-Q4 — Is IU-2-01/CU-2-01 dedicated to TR 2065A and on emergency/backup power? [Open] Impact: Cooling continuity unclear • B08-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR/TE? [Open] Impact: Life safety acceptance risk • B08-Q6 — Are all B08 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open.
09 | B09 | B09_Assessment | • Fully sprinklered building; verify sprinkler head coverage, rated penetrations, temporary firestopping, and FEC location for basement TR. • Fire protection enlarged plan shows Telecom Room 104B and rated wall legend; verify sprinkler/fire alarm modifications and clean-agent extinguisher within 75 ft. • Fire protection enlarged plan shows Telecom Room 206A; verify sprinkler cage/coverage, fire alarm device relocation/additions, and rated penetrations. | • Electrical enlarged/panel data identifies CU-0-1 serving basement work; verify mechanical schedule, emergency source, condensate, controls and alarms. • Electrical enlarged plan identifies IU-1-01 in Telecom Room 104B and CU-1-1; verify dedicated 24/7 cooling and emergency power. • Electrical enlarged plan identifies IU-2-01 in Telecom Room 206A and CU-2-1; verify dedicated 24/7 cooling and emergency power. | • Panel schedule lists B09-TRB01A/B in Telecom Room B01 with 208Y/120V panels, rack receptacles, access controller, mechanical equipment, lighting and SPD notes. • Electrical enlarged plan shows panel references B09-TR104BA/B, IU-1-01, security devices, lighting and receptacle/rack circuits. • Electrical enlarged plan shows panel references B09-TR206AA/B, IU-2-01, security devices, lighting and receptacle/rack circuits. | • Fiber riser identifies Building 09 basement B01 with two-rack TR; verify rack elevations, fiber Path A/B, Cat6A replacement, LIU, bonding and cutover. • Fiber riser identifies first-level Room 104B with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. • Fiber riser identifies second-level Room 206A with two-rack TR; verify rack elevation details, patch panels, UPS/PDU, fiber LIU, grounding and test records. | • Enlarged plans show existing/new security boxes, network door controller, camera/security scope; verify PACS/CCTV integration and protection of active security systems. • First-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 104B camera designation; verify card reader, electric strike, door contact, motion and camera. • Second-level enlarged plan shows CR/RX/DC/ES/MD-type device symbols and 206A camera designation; verify PACS/VMS integration and commissioning. | • High: Existing conditions for B01, 104B and 206A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Basement TR includes existing equipment and could remain active during cutover — Document active services, protect-in-place and define cutover/demo sequence • High: Hazardous material abatement plans exist for basement, first and second levels — Coordinate ACM/lead/abatement review before penetrations, flooring removal or ceiling/wall work • High: Rated wall/door work and fire/smoke assemblies could affect schedule and acceptance — Verify wall ratings, door/frame rating, penetrations, smoke/fire barriers and access control hardware • Critical: Dedicated cooling emergency power, controls, condensate and high-temp alarms not verified — Confirm IU/CU assignments, emergency source, BACnet/interface, condensate routing and alarms • High: Electrical panel/circuit source and rack load coordination unresolved — Verify B09-TRB01A/B, B09-TR104BA/B, B09-TR206AA/B schedules, SPDs, labels and load measurements | • B09-Q1 — Confirm final TR scope: B01 basement, 104B first level, and 206A second level? [Open] Impact: Room inventory may miss scope • B09-Q2 — What active services are currently fed from B01 existing equipment/security/network devices? [Open] Impact: Potential communications/security outage • B09-Q3 — What hazardous/abatement steps apply to B01, 104B and 206A work areas? [Open] Impact: Work delay or exposure risk • B09-Q4 — Are IU-0-01/CU-0-1, IU-1-01/CU-1-1 and IU-2-01/CU-2-1 on emergency/backup power? [Open] Impact: Cooling continuity unclear • B09-Q5 — Where are clean-agent/CO2 extinguisher cabinets located within 75 ft of each TR? [Open] Impact: Life safety acceptance risk • B09-Q6 — Are all B09 panelboard sources, circuits, SPDs, rack receptacles and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open.
10 | B10 | B10_Assessment | • Attic-level TR requires verification of sprinkler/fire alarm modifications, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations and temporary firestopping. • Electrical work may require penetrations or shutdowns; verify firestopping and protection-in-place. • Emergency electrical room coordination; verify no unsealed penetrations or life-safety impairment. | • Mechanical/electrical drawings identify IU-1-01 in Telecom Room 200A and CU-1-01 outdoor unit; verify capacity, emergency power, condensate route, BACnet adapter and high-temp alarm. • No dedicated TR cooling scope; verify electrical room ventilation is not impacted by new work. • No dedicated TR cooling scope; verify emergency electrical room ventilation is not impacted. | • Electrical schedule identifies B10-TR200AA/AB in Telecom Room 200A with rack receptacles, TR receptacles, lighting, access controller, CU-1-01 and SPD requirements; verify source and labels. • Basement normal electrical source; verify load measurement, new breakers/feeders, panel access, LOTO and shutdown sequencing. • Emergency source coordination; verify generator/ATS feed to TR critical loads and cooling where required. | • 10T sheets show attic telecom plan/rack elevations; provide 4-post racks, UPS, redundant PDUs, switches, Cat6A patch panels, Fiber LIU, bonding/grounding, labeling, testing and VA acceptance before cutover. • Coordinate telecom power pathways through/source from basement electrical room if applicable. • Coordinate emergency source/backup power pathways for telecom equipment and cooling. | • General scope requires PACS/CCTV for TR doors; verify door hardware, access controller, camera/VMS integration and any existing attic access/security constraints. • Verify security impact only if electrical source room access or devices are modified. • Verify emergency electrical room security impact if work requires access control changes. | • High: Attic Telecom Room existing conditions and access not field verified — Survey Room 200A, attic access route, existing rack/equipment, floor/deck conditions, clearances and utilities • High: Hazardous material abatement plan exists for attic level — Coordinate attic abatement/IH review before penetrations, ceiling/floor work, cabling or HVAC/electrical installation • Critical: Existing wall-mounted rack/equipment may remain active during cutover — Document active services, protect in place and develop night-shift cutover/temporary rack plan • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 capacity, power source, condensate routing, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, generator/ATS path and shutdown sequencing unclear — Verify B10-MDP, B10-L10-E, ATS-B10-LSD, panel feeders, load measurement and LOTO before electrical work • Critical: Fire alarm/sprinkler/firestopping work in attic TR could affect occupied operations — Track impairments, fire watch, sprinkler/head changes, FA device work, rated penetrations and temporary firestopping | • B10-Q1 — Confirm final scope: attic Telecom Room 200A only, with basement electrical source coordination in B24/B25? [Open] Impact: Room inventory could miss scope • B10-Q2 — What active services are currently fed from the existing wall-mounted rack/equipment in Room 200A? [Open] Impact: Potential communications outage • B10-Q3 — What attic hazardous material/abatement steps apply before cabling, penetrations, HVAC or electrical work? [Open] Impact: Work delay/exposure risk • B10-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and does it serve Room 200A only? [Open] Impact: Cooling continuity unclear • B10-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 200A? [Open] Impact: Life-safety acceptance risk • B10-Q6 — Are B10-TR200AA/AB, B10-MDP, B10-L10-E and ATS-B10-LSD source circuits/load measurements approved? [Open] Impact: Electrical readiness unknown | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination.
12 | B12 | B12_Assessment | • No fire protection drawing package beyond general notes; verify penetrations/firestopping for fiber pull-through route. • No new TR/FEC shown; verify no rated assemblies are compromised by fiber pathway work. | • No HVAC drawing package for Building 12; fiber-only scope does not indicate new cooling equipment. • Field verify existing environmental conditions only if existing service point/equipment is accessed. | • No electrical drawing package for Building 12; no new panel/UPS/PDU/rack receptacle scope shown. • Confirm whether any existing equipment is touched. Scope appears limited to fiber pull-through and testing/labeling. | • Building 12 receives fiber only. Verify pull-through path on basement/first/second telecom plans, redundant Path A/B fiber, pathway capacity, grounding/bonding where applicable, labeling and testing. • 12T-604 shows rack number 00/room 00 and notes fiber-only with no mounting type; verify existing service/termination point and whether fiber passes through only. | • No new TR door or PACS/CCTV package shown for Building 12; verify security access only for work areas and existing equipment rooms. • Confirm access requirements to existing closet/demarc while protecting active operations. | • High: Fiber-only scope could be mistaken for full TR scope or skipped as minor work — Clearly tag Building 12 as fiber-only and verify required fiber path, testing, labels and acceptance deliverables • High: Existing pull-through pathway not field verified — Trace basement/first/second level pathway, conduit/cable tray capacity, pull points and access before scheduled pull • Critical: Existing service continuity during fiber pull/cutover may not be defined — Coordinate with VA OIT, submit phasing/cutover plan, and maintain legacy service until new fiber is tested and accepted • High: Pathway penetrations/firestopping may be overlooked because there is no architectural/FP package — Inspect all new/reused penetrations and require permanent or temporary firestopping at end of shift • Medium: Existing termination/demarc location and ownership unclear — Field document existing rack/demarc/serving closet and confirm where new fiber terminates or passes through • High: Test reports, labels and as-builts may be incomplete for fiber-only work — Track fiber OTDR/certification, labeling, route documentation and VA/OIT acceptance before closeout | • B12-Q1 — Confirm Building 12 scope is fiber-only with no new TR, no new rack, no new electrical, HVAC, fire protection, PACS or CCTV work? [Open] Impact: Scope misunderstanding • B12-Q2 — What exact pathway does the Building 12 fiber take through basement, first and second levels? [Open] Impact: Fiber pull and access risk • B12-Q3 — Where does the Building 12 fiber terminate, and is the existing rack/demarc/closet to be touched? [Open] Impact: Termination and ownership unclear • B12-Q4 — Are existing conduits/cable trays available and below fill limits for the new fiber? [Open] Impact: Pathway capacity risk • B12-Q5 — Are there any floor/rated wall penetrations requiring firestop or temporary firestop during cable pull? [Open] Impact: Life safety/firestop risk • B12-Q6 — What is the approved cutover/testing/acceptance sequence for Building 12 fiber? [Open] Impact: Possible outage or acceptance delay | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover.
13 | B13 | B13_Assessment | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 photo/reference notes show existing indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. | • Electrical enlarged plans and schedules identify B13-TR124AA/AB, 240V 1-phase UPS circuits, normal/emergency rack power, rack receptacles, TR receptacles, access/security devices, lighting, CU-1-01, and SPD requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 13T-701 identifies Room 124 schedule: 58 WAO total, 65 active ports per survey, 91 total ports per schedule, and 100 total ports with 10% allowance. New Rack ID TR01-124-1 serves first and second level outlets with Fiber Path A/B. • Existing Room 222 equipment includes wall-mounted rack, telco patch, plywood backboard, patch panel, security cabinet, and existing AC; verify active services and transfer plan to Room 124. | • Electrical enlarged plan shows security/access-control device callouts at Room 124 and 124-CAM-01 camera designation; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 124 and existing Tel Room 222 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing Tel Room 222 equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B13-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B13-Q1 — Confirm final telecom scope: new Room 124 and existing Tel Room 222 transition only? [Open] Impact: Room inventory could miss scope • B13-Q2 — What active services are currently fed from existing Tel Room 222 equipment? [Open] Impact: Potential communications/security outage • B13-Q3 — What hazardous/abatement steps apply to first-level Room 124 work? [Open] Impact: Work delay or exposure risk • B13-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124? [Open] Impact: Cooling continuity unclear • B13-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124? [Open] Impact: Life-safety acceptance risk • B13-Q6 — Are B13-TR124AA/AB sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open.
14 | B14 | B14_Assessment | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing basement tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Existing basement telecom room; verify no unsealed penetrations remain after cable transfer or reuse. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 119 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel/F Panel room; verify existing environmental conditions during cutover and whether legacy equipment remains active. • Existing telecom room reference; field verify cooling/ventilation and active equipment condition. | • Electrical plan/schedules identify B14-TR119A/B, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and panel load measurement requirements. • Existing basement wall-mounted TE/equipment area; verify power source, active equipment, UPS/PDU status, and transition requirements before disconnect or removal. • Existing telecom room photo reference; confirm power sources and any cutover requirements. | • 14T-701 identifies Room 119 schedule: 44 WAO total, 29 active ports per survey, 76 total ports per schedule, and 84 total ports with 10% allowance. New Rack ID TR01-119-1 serves first and second level outlets with Fiber Path A/B. • Existing Room B.01 equipment includes wall-mounted TE, Cisco switch/legacy patch panel, telco patch, plywood backboards, and legacy Fiber LIU; verify active services and transfer plan to Room 119. • Existing basement telecom room B2 is identified by photo reference; verify active devices, routing, and relation to B.01. | • Telecom/electrical plans show 119-CAM-01 and security/access-control scope for Room 119; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Verify whether existing security equipment remains, is relocated, or requires temporary protection during cutover. • Verify security/access conditions and whether any legacy security equipment is present. | • High: Existing conditions for Room 119 and existing basement telecom rooms B.01/B2 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing basement telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B14-TR119A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B14-Q1 — Confirm final telecom scope: new Room 119 and existing basement B.01/B2 transition only? [Open] Impact: Room inventory could miss scope • B14-Q2 — What active services are currently fed from existing B.01/B2 equipment? [Open] Impact: Potential communications/security outage • B14-Q3 — What hazardous/abatement steps apply to first-level Room 119 work? [Open] Impact: Work delay or exposure risk • B14-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 119? [Open] Impact: Cooling continuity unclear • B14-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 119? [Open] Impact: Life-safety acceptance risk • B14-Q6 — Are B14-TR119A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 14 includes new first-level Telecom Room 119 and existing basement telecom rooms B.01/B2; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open.
15 | B15 | B15_Assessment | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling penetrations, and temporary firestopping during cable pulls. • Existing tel room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Existing basement telecom/crossover room; verify no unsealed penetrations remain after cable transfer or reuse. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 124A and CU-1-01 outdoor heat-pump/A/C unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Tel Room 222 is shown with existing/remain indoor AC unit; verify whether it remains active, is abandoned, or needs protection during cutover. • Existing basement telecom/crossover space; verify environmental conditions and whether active equipment remains during cutover. | • Electrical enlarged plans and schedules identify B15-TR124AA/AB, 240V rack UPS requirements, normal/emergency rack power, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and 30-day load measurement requirements. • Existing rack/equipment area; verify power source, active equipment, APC floor UPS status, and transition requirements before disconnect or removal. • Existing B-01 crossover; verify power sources and cutover needs for legacy patch panel/crossover. | • 15T-701 identifies Room 109A schedule but field plan/electrical room callouts identify Telecom Room 124A; schedule has 62 WAO total, 76 active ports per survey, 101 total ports per schedule, and 111 total ports with 10% allowance. New Rack ID TR15-109A-01 serves basement, first and second level outlets. • Existing Room 222 equipment includes wall/wall-mounted TE, Cisco switches, legacy 48-port patch panels, ground bar, plywood backboard, security cabinet, and floor UPS; verify active services and transfer plan to Room 124A. • Existing B-01 crossover includes legacy 24-port patch panel; verify active devices, routing, and relation to Room 222 and Room 124A. | • Telecom/electrical plans show 124A-CAM-1 and security/access-control scope for Room 124A; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Tel Room 222; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Verify security/access conditions and whether any legacy security equipment is present. | • High: Existing conditions for Room 124A and existing telecom rooms 222/B01 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B15-TR124AA/AB schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B15-Q1 — Confirm final telecom scope: new Room 124A and existing Rooms 222/B01 transition only? [Open] Impact: Room inventory could miss scope • B15-Q2 — Why does 15T-701 reference RM 109A while plans and electrical schedules identify Telecom Room 124A? [Open] Impact: Room naming mismatch could affect PMIS tracking • B15-Q3 — What active services are currently fed from existing Room 222 and B01 equipment? [Open] Impact: Potential communications/security outage • B15-Q4 — What hazardous/abatement steps apply to first-level Room 124A work? [Open] Impact: Work delay or exposure risk • B15-Q5 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 124A? [Open] Impact: Cooling continuity unclear • B15-Q6 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 124A? [Open] Impact: Life-safety acceptance risk | Building 15 includes new first-level Telecom Room 124A and existing telecom transition points at second-level Tel Room 222 and basement B01; field verification, active service cutover, 240V UPS/PDU power, dedicated heat-pump cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open.
16 | B16 | B16_Assessment | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom room; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 015 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing Telecom Room 014; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • Electrical plans/schedules identify B16-TR015A/B, 240V rack UPS requirements, rack receptacles, TR receptacles, lighting, access controller, CU-1-01, SPD requirements, existing panel demolition/replacement, and 30-day load measurement requirements. • Existing rack/equipment area; verify power source, active equipment, UPS status, and transition requirements before disconnect or removal. | • 16T-701 identifies Room 015-A schedule: 25 WAO total, 25 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. New Rack ID TR01-015-A-1 serves basement, first, second and attic level outlets. • Existing Room 014 equipment includes wall/TE rack, floor-mounted UPS, Cisco switch, legacy 12-port modular patch panel and Fiber LIU; verify active services and transfer plan to Room 015. | • Telecom/electrical plans show 015-CAM-1 and security/access-control scope for Room 015; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in Room 014; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 015 and existing Telecom Room 014 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • High: Basement TR buildout may conflict with existing utilities, water heater/stair/storage conditions and pathway routing — Survey adjacent Water Heater 010, Vacant 011/012/013, Stair 014, pathway/ductbank routing, and constructability constraints • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 240V UPS/PDU and panel source coordination could delay energization — Verify B16-TR015A/B schedules, breakers, receptacles, SPD, labels, load measurement, normal/emergency source and LOTO needs • High: Rated wall/door/firestop scope may affect life-safety acceptance — Inspect 1-hour wall/smoke barrier conditions, rated door/frame, penetrations, FEC location, temporary firestopping and final UL systems | • B16-Q1 — Confirm final telecom scope: new Room 015 and existing Room 014 transition only? [Open] Impact: Room inventory could miss scope • B16-Q2 — What active services are currently fed from existing Room 014 equipment? [Open] Impact: Potential communications/security outage • B16-Q3 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 015? [Open] Impact: Cooling continuity unclear • B16-Q4 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 015? [Open] Impact: Life-safety acceptance risk • B16-Q5 — Are B16-TR015A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown • B16-Q6 — Which existing panel/circuit breaker/feeder demolition and replacement affects Room 015 telecom power? [Open] Impact: Panel outage/cutover risk | Building 16 includes new basement Telecom Room 015 and existing basement Telecom Room 014; field verification, active service transfer, 240V UPS/PDU power, dedicated cooling, panel replacement/source coordination, firestopping, PACS/CCTV integration, and cable tray coordination remain open.
17 | B17 | B17_Assessment | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom closet; verify fire alarm/sprinkler protection-in-place and seal any removed/reused penetration after cutover. • Verify firestopping at pathway penetrations between Building 17 and Building 29 and any rated floor/wall assemblies. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 118 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing B35A is shown with existing indoor AC unit; verify whether it remains active, is abandoned, or needs temporary protection during cutover. • No dedicated cooling expected for pathway; verify any equipment cabinets or active service locations in Building 29 if applicable. | • Electrical plans/schedules identify B17-TR118A fed from BUS-B17-NPB1-R and B17-TR118B fed from BUS-B17-EQDP, with TR RM118 rack receptacles, 208V UPS/PDU equipment, CU-1-01, SPD requirements, and 30-day load measurement requirements. • Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. • Verify whether any Building 29 equipment or extension path requires power, grounding, bonding, or labeling tied back to B17 TR 118. | • 17_29T-701 identifies Room 118 schedule: 113 WAO total, 67 active ports per survey, 154 total ports per schedule, and 169 total ports with 10% allowance. Rack ID TR17-118-1 serves basement, first, second-level outlets and Building 29 path. • Existing Room B35A equipment includes SERTEX utility service ports, legacy Ortronics patch panels, Cisco switches, wall-mounted TE, Fiber/legacy equipment, security cabinet, and floor UPS; verify active services and transfer plan to Room 118. • Building 29 is shown served from B17; verify fiber from Building 17 to Building 29, path to B29 4-inch PVC, outlet labels, test records and as-builts. | • Telecom/electrical plans show 118-CAM-01 and security/access-control scope for Room 118; verify CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in B35A; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Verify Building 29 pathway and any security scope tied into B17 TR 118/VMS/PACS. | • High: Existing conditions for Room 118, B35A and Building 29 service path not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 208V UPS/PDU and panel source coordination could delay energization — Verify B17-TR118A/B schedules, BUS-B17-EQDP, BUS-B17-NPB1-R, rack receptacles, SPD, labels, load measurement and LOTO needs • High: Cable tray and pathway scope is large and crosses multiple levels/building service boundary — Verify 517 ft cable tray, supports, seismic bracing, 40% fill, path to B29 4-inch PVC, penetrations and labeling before install | • B17-Q1 — Confirm final telecom scope: new Room 118, existing B35A, and Building 29 served from B17? [Open] Impact: Room inventory or PMIS mapping could miss scope • B17-Q2 — What active services are currently fed from existing B35A equipment? [Open] Impact: Potential communications/security outage • B17-Q3 — What exact Building 29 outlets/devices are served through TR17-118-1? [Open] Impact: Building 29 scope boundary unclear • B17-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 118? [Open] Impact: Cooling continuity unclear • B17-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 118? [Open] Impact: Life-safety acceptance risk • B17-Q6 — Are B17-TR118A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 17_29 includes new first-level Telecom Room 118 serving Building 17 and Building 29, plus existing basement Telecom Closet B35A; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, cable tray, firestopping, and PACS/CCTV integration remain open.
18 | B18 | B18_Assessment | • Fully sprinklered building; confirm sprinkler/fire alarm modifications, clean-agent 2A:10B:C extinguisher within 75 ft, rated wall/ceiling/floor penetrations, and temporary firestopping during cable pulls. • Existing TE room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. • Existing second-level closet; verify protection-in-place and firestopping after transfer or abandonment. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 110 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet adapter, thermostat/control point, condensate path, disconnects, and high-temperature alarm. • Existing TE 111B; verify existing environmental conditions during cutover and whether legacy equipment remains active. • Existing Closet 213; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • Electrical plans/schedules identify B18-TR110A/B, 208V rack UPS requirements, rack receptacles, TR receptacles, lighting, CU-1-01, SPD requirements, and telecom panelboard schedule requirements. • Existing rack/equipment area; verify active equipment, floor UPS status, source circuits, and transfer requirements before disconnect/removal. • Existing rack/equipment area; verify active equipment, APC UPS status, source circuits, SERTEX utility service and transfer requirements before disconnect/removal. | • 18T-701 identifies RM 111A schedule: 86 WAO total, 61 active ports per survey, 122 ports per schedule, and 134 total ports with 10% allowance. New rack elevation is Room 110, 1 rack plus future, with UPS, Future Zone PDU, switches, Cat6A patch panels, Cat5E patch panel and Fiber LIU. • Existing Room 111B equipment includes wall-mounted rack, plywood backboard, patch panel, security cabinet, floor UPS and 5RU fiber optic housing; verify active services and transfer plan to Room 110. • Existing Room 213 equipment includes SERTEX utility service ports, Cisco switch, multiple legacy Ortronics patch panels, wall/wall-mount TE and APC floor UPS; verify active services and transfer plan to Room 110. | • Telecom/electrical plans show 111A-CAM-01 and security/access-control scope for the new TR area; verify room naming, CR/RX/DC/ES/MD devices, controller, camera/VMS integration, and door hardware coordination. • Existing security cabinet shown in 111B; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. • Existing security cabinet shown in 213; verify whether security equipment remains, is relocated, or requires temporary protection during cutover. | • High: Existing conditions for Room 110, Room 111B and Room 213 not field verified — Perform existing conditions survey with photos before mobilization • High: First-level hazardous material / lead-based paint abatement plan exists — Coordinate IH/abatement review before wall, floor, ceiling, conduit, or penetration work • Critical: Existing telecom equipment may remain active during cutover — Document active services, protect in place, identify owner/OIT cutover windows, and preserve rollback path • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: 208V UPS/PDU and panel source coordination could delay energization — Verify B18-TR110A/B schedules, rack receptacles, SPD, labels, source circuits and LOTO needs • High: Cable tray and pathway scope crosses first and second levels — Verify 315 ft cable tray, supports, seismic bracing, 40% fill, penetrations, coordination with lighting/HVAC and labeling before install | • B18-Q1 — Confirm final telecom scope: new Room 110 with existing 111B and 213 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B18-Q2 — Why does 18T-701 reference RM 111A while new rack/electrical plans identify Telecom Room 110? [Open] Impact: Room naming mismatch could affect PMIS tracking • B18-Q3 — What active services are currently fed from existing 111B and 213 equipment? [Open] Impact: Potential communications/security outage • B18-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 110? [Open] Impact: Cooling continuity unclear • B18-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 110? [Open] Impact: Life-safety acceptance risk • B18-Q6 — Are B18-TR110A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 18 includes new first-level Telecom Room 110 and existing telecom transition rooms 111B and 213; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, lead-paint/first-level hazardous material coordination, firestopping, cable tray, and PACS/CCTV integration remain open.
20 | B20 | B20_Assessment | • Cover sheet states Building 20 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. • Existing closet; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Office 1B ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing Tel/Data Closet 8A includes indoor AC unit to remain/protect in place; verify operation during cutover and whether equipment remains after transition. | • 20T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing 8A elevation shows UPS on ground, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 20T-701 identifies TE01-1B-1: 21 WAO total, 24 active ports per survey, 30 ports per schedule, 33 total ports with 10% allowance. Provide new wall-mount TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing Tel/Data Closet 8A contains open TE cabinet, ground bar, patch panel, equipment box, indoor AC unit, plywood backboard, BIX blocks, Cisco switch, legacy 48-port patch panel and Fiber LIU. Field verify all active services. | • Building 20 does not appear to create a new TR door/PACS package. Verify any existing cameras/security devices in Office 1B and ensure no camera angle or VMS integration is disrupted. • Keynotes indicate existing cameras are to be retained and re-used/protected in place; verify existing security equipment and cabinet impacts during cutover. | • High: Existing conditions for new Office 1B TE and existing Tel/Data Closet 8A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in 8A may remain active during transfer to new TE in 1B — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Room naming and TE designation could cause PMIS mapping confusion — Track as Building 20 / Office 1B / TE01-1B-1 and link existing Room 8A as transition point • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Office 1B — Verify heat load, office ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 459 feet of cable tray/pathway requires coordination despite small port count — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B20-Q1 — Confirm final scope: new wall-mount TE enclosure in Office 1B and existing Tel/Data Closet 8A transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B20-Q2 — What active services are currently fed from existing 8A open TE cabinet and related equipment? [Open] Impact: Potential communications/security outage • B20-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Office 1B? [Open] Impact: Electrical readiness unknown • B20-Q4 — Is Office 1B HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B20-Q5 — Are existing cameras/security devices in Building 20 protected and retained with no VMS/PACS changes? [Open] Impact: Security continuity unclear • B20-Q6 — Are all 459 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 20 is a telecom-enclosure building, not a full TR buildout. Scope centers on new first-level Office 1B wall-mount TE enclosure and existing Tel/Data Closet 8A; mechanical and fire protection scope are excluded by the cover sheet, but field verification, active equipment transfer, fiber/copper cutover, cable tray, firestopping, power/UPS/PDU, and existing equipment protection remain open.
21 | B21 | B21_Assessment | • Cover sheet states Building 21_19 receives a Telecom Enclosure and fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and any life-safety device impacts. • Existing B21 basement TR; verify protection-in-place and firestopping after cable transfer or reuse. • Existing B19 B05TR; verify protection-in-place and firestopping after cable transfer or reuse. | • Mechanical sheets exist in index. Verify whether new TE heat load in Office 100A is supported by existing/new HVAC and whether any mechanical scope applies despite TE designation. • Existing B21 B1.TR; verify environmental conditions during cutover and whether legacy equipment remains active. • Existing B19 B05TR; verify environmental conditions and whether equipment remains active during/after Building 21 transfer. | • 21_19T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switches, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing B21 B1.TR elevation shows UPS on ground, Cisco switch, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements. • Existing B19 B05TR elevations show APC floor UPS, legacy patch panels, Cisco switch and Fiber LIU; verify power source, active equipment and transfer/retention requirements. | • 21_19T-701 identifies RM 104 schedule: 90 WAO total, 67 active ports per survey, 119 ports per schedule, and 131 total ports with 10% allowance. 659 ft cable tray total: 63 ft basement and 596 ft first level. • Existing B21 B1.TR equipment includes multiple legacy patch panels, Cisco switch, UPS on ground, Fiber LIU and APC floor UPS; verify active services and transfer plan to new TE. • Existing B19 B05TR equipment includes legacy Ortronics patch panels, Cisco switch, Fiber LIU and APC floor UPS; verify active services and whether B19/B21 devices are served from new enclosure. | • Building 21_19 appears to create a TE enclosure rather than a full TR door/PACS package. Verify any existing cameras/security devices in Room 100A and ensure no camera angle or VMS integration is disrupted. • Verify any existing security device/cabinet impacts during cutover. • Verify existing security/camera protection-in-place and any impact from B19/B21 shared telecom equipment. | • High: Existing conditions for new 100A TE, B21 B1.TR and B19 B05TR not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment may remain active during transfer to new TE enclosure — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • High: Room naming mismatch: schedule says RM 104 / TR01-104-1 while plan/enlarged view identifies Room 100A — Track PMIS as Building 21 / Room 100A / Schedule RM 104 / Rack ID TR01-104-1 and confirm with designer • High: B19/B21 combined package may blur scope boundary and ownership of ports — Separate Building 21 work, Building 19 transition work, and shared service/cross-connect items in PMIS notes • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 659 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B21-Q1 — Confirm final scope: new TE enclosure at Room 100A/RM 104 and existing B21 B1.TR plus B19 B05TR transition? [Open] Impact: Room inventory or PMIS mapping could miss scope • B21-Q2 — Why does 21_19T-701 list RM 104 / TR01-104-1 while enlarged plan identifies Room 100A? [Open] Impact: Room naming mismatch could affect PMIS tracking • B21-Q3 — What active services are currently fed from existing B21 B1.TR and B19 B05TR equipment? [Open] Impact: Potential communications/security outage • B21-Q4 — What exactly is meant by '19 serving 21' on the new TE enclosure elevation? [Open] Impact: Building 19/21 boundary unclear • B21-Q5 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in 100A? [Open] Impact: Electrical readiness unknown • B21-Q6 — Are all 659 ft of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 21 is combined with Building 19 and is primarily a telecom-enclosure scope. New first-level M&O Foreman Office 100A / RM 104 schedule is served by a new 12RU TE enclosure, while existing Building 21 B1.TR and Building 19 B05TR equipment remain transition points. Fire protection scope is excluded, but mechanical/electrical sheets exist for equipment support. Field verification, active-service transfer, 659 ft cable tray, firestopping, UPS/PDU power, fiber/copper cutover, and B19/B21 scope boundary remain open.
22 | B22 | B22_Assessment | • Cover sheet states Building 22 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. • Existing TE room; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Break Room 102 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing Room 103 equipment area; verify existing environmental conditions during cutover and whether legacy equipment remains active. | • 22T-701 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing 103 elevation shows APC UPS, Cisco switch, SERTEX utility service, legacy patch equipment and Fiber LIU on wall; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 22T-701 identifies TR01-102-1: 6 WAO total, 96 WAO available, 93% expansion capacity, 7 total port quantities, and 8 total ports with 10% allowance. Provide new wall-mount 12RU TE cabinet and 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing Room 103 contains APC UPS, Cisco switch, SERTEX utility service, legacy Ortronics 24-port patch panel, Fiber LIU on wall and ports 1-24 to Bldg 19 ports 73-96. Field verify all active services and B19 handoff. | • Building 22 does not appear to create a new full TR door/PACS package. Verify any existing cameras/security devices in Break Room 102 and ensure no camera angle or VMS integration is disrupted. • Verify security/access conditions and whether any legacy security equipment is present at existing TE location. | • High: Existing conditions for new Break Room 102 TE and existing Room 103 TE not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in 103 may remain active during transfer to new TE in 102 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Break Room 102 use may conflict with wall-mount TE access and clearances — Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Break Room 102 — Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 139 feet of cable tray/pathway requires coordination despite small port count — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B22-Q1 — Confirm final scope: new wall-mount TE enclosure in Break Room 102 and existing Room 103 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B22-Q2 — What active services are currently fed from existing Room 103 equipment? [Open] Impact: Potential communications/security outage • B22-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? [Open] Impact: Electrical readiness unknown • B22-Q4 — Is Break Room 102 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B22-Q5 — Are existing cameras/security devices in Building 22 protected and retained with no VMS/PACS changes? [Open] Impact: Security continuity unclear • B22-Q6 — Are all 139 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 22 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new first-level Break Room 102 TE enclosure and existing first-level wall/wall-mount TE Room 103. Field verification, active service transfer, 139 ft cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, and B19 utility service relationship remain open.
33 | B33 | B33_Assessment | • Cover sheet states Building 33 receives a Telecom Enclosure and mechanical/fire protection scope is excluded. Still verify firestopping of rated penetrations, 4-inch sleeve, wall/floor openings, and life-safety device impacts. • Existing Tel Closet; verify protection-in-place and firestopping after cable transfer or reuse. | • Cover sheet states mechanical scope is excluded. Verify whether Office B23 ambient conditions are acceptable for wall-mount TE/UPS/PDU/network equipment. • Existing B17 enlarged plan identifies an existing indoor AC unit. Verify operation during cutover and determine whether active legacy equipment remains after transfer to B23. | • 33T-604 new enclosure elevation shows APC UPS, two PDU L5-30 input / NEMA 5-20 output units, 120V outlet UPS, 120V outlet PDU, network switch, 48-port Cat6A patch panel and Fiber LIU. Verify circuit source, receptacle type, grounding/bonding and labels. • Existing B17 elevations show UPS on floor, Cisco switches, SERTEX utility service, legacy patch panels and Fiber LIU; verify source circuits, UPS status, and transition requirements before disconnect/removal. | • 33T-701 identifies TE01-B23-1: 55 WAO total, 34 active ports per survey, 88 total ports per schedule, and 97 total ports with 10% allowance. Basement cable tray schedule totals 102 ft. Provide 10 new Cat6A cross-connect cables from existing TE to new TE location. • Existing B17 rack elevations include Cisco switches, legacy 24/48-port patch panels, SERTEX utility service, legacy Fiber LIU, passive Fiber LIU/wall mount, UPS on floor and cross-building port references to Bldgs 3, 80 and 82. | • Building 33 does not appear to create a new full TR door/PACS package. Verify existing cameras/security devices in B23 and ensure no camera angle or VMS integration is disrupted. • Existing B17 enlarged plan identifies network door controller, keypad and equipment box; verify protection-in-place and whether any security equipment is relocated or recabled. | • High: Existing conditions for new B23 TE and existing B17 Tel Closet not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in B17 may remain active during transfer to new TE in B23 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • Medium: Office B23 use may conflict with wall-mount TE access and clearances — Verify wall backing, enclosure clearances, working space, furniture/occupant impacts and owner acceptance • High: No mechanical scope, but TE/UPS/network equipment may add heat load to Office B23 — Verify heat load, room ventilation, equipment clearances and owner acceptance before energizing enclosure • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: 102 feet of basement cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light fixtures and coordination drawings before install | • B33-Q1 — Confirm final scope: new wall-mount TE enclosure in B23 and existing B17 transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B33-Q2 — What active services are currently fed from existing B17 equipment? [Open] Impact: Potential communications/security outage • B33-Q3 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in B23? [Open] Impact: Electrical readiness unknown • B33-Q4 — Is Office B23 HVAC/ambient condition acceptable for a wall-mount TE with UPS/PDU/network switch? [Open] Impact: Heat/load risk after mechanical scope excluded • B33-Q5 — Are existing cameras/security devices in Building 33 protected and retained with no VMS/PACS disruption? [Open] Impact: Security continuity unclear • B33-Q6 — Are all 102 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 33 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new basement EEO Manager Office B23 TE enclosure and existing Tel Closet B17. Field verification, active service transfer, 102 ft basement cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, fiber/copper cutover, and legacy service relationships to Buildings 3, 80 and 82 remain open.
61 | B61 | B61_Assessment | • Dedicated TR scope includes fire protection drawings. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated penetrations, and temporary firestopping. • Verify sprinkler/fire alarm modifications, clean-agent FEC location, penetrations, cable tray/riser openings, and final UL firestop systems. • Verify second-level TR sprinkler/fire alarm modifications, clean-agent FEC location, vertical riser penetrations, and firestopping. • Existing demarc/server rooms may remain active; verify protection-in-place, FA/FP continuity, and no unsealed penetrations after cabling work. | • Mechanical sheets identify dedicated split-system cooling with BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency source, condensate, disconnect, controls, and alarms. • Mechanical/electrical plans identify IU-1-01/CU-1-01 for first-level TR. Confirm 24/7 operation, emergency/standby source and high-temp alarm. • Mechanical/electrical plans identify IU-2-01/CU-2-01 for second-level TR. Confirm refrigerant route, condensate route, controls and alarm tie-in. • Existing demarc/server equipment likely has existing cooling dependencies. Verify active equipment heat load, airflow, operational temperatures and whether any existing cooling is modified or protected. | • Electrical enlarged plans and schedules identify rack receptacles, UPS circuits, PDUs, panelboards, SPD devices and dedicated cooling power for B13H-A. Verify B61-TRB13A/B source, LOTO and labels. • Electrical schedules identify B61-TR124A/B and rack receptacles. Verify apparent room-name mismatch with RM137B rack receptacles in schedules. • Electrical schedules identify B61-TR226A/B, rack receptacles, CU-2-01 and SPD requirements. Verify source circuits and labels. • Existing rack inventory includes APC UPS/PDU and server/demarc equipment. Electrical one-line/schedules list B61-TR137AA/AB and PD-B61-TR137 panels; verify active sources and transition impact. | • 61T-701: 88 WAO total, 74 active ports, 129 scheduled ports, 142 with 10% allowance. Rack ID TR01-B13H-A-1. Basement cable tray included in 890 ft basement total. • 61T-701: first-level Room 124 / Rack ID TR01-124-1. Schedule data runs across first-level outlets. Include labels, Fiber LIU, Cat6A patch panels, UPS/PDU and VA/OIT acceptance. • 61T-702: 109 WAO total, 126 active ports, 156 scheduled ports, 172 with 10% allowance. Rack ID TR01-226-1. Verify second-level cable tray and riser penetrations. • 61T-402/606/607 inventory existing demarc/server racks and equipment. Protect active systems, coordinate cutover, preserve labels, document equipment remaining in service. | • Telecom plans call for wall-mounted CCTV at TRs and PACS for TR doors. Verify camera, controller, CR/RX/DC/ES/MD, and VMS/PACS integration. • Verify TR door hardware and access control, CCTV camera, network door controller and integration. • Verify second-level TR access control, CCTV camera, door hardware, and VMS/PACS integration. • Existing PACS/equipment racks are referenced. Verify existing security devices protected-in-place and any new recabling or integration scope. | • High: Existing conditions and active equipment across B13H-A, 124, 226 and 137/137A not field verified — Perform existing conditions survey with photos and active-service inventory before mobilization • High: Hazardous material abatement plans exist for first and second levels — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or mechanical/electrical installation • Critical: Existing server/demarc equipment may remain active during cutover — Document active services, service provider circuits, rack inventory, OIT windows, temporary utilities and rollback path • Critical: Dedicated cooling sequence, emergency power, condensate, BACnet and alarms not verified — Confirm IU/CU-0/1/2 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify B61-TRB13A/B, B61-TR124A/B, B61-TR226A/B, B61-TR137AA/AB, PD panels, SPDs and load measurements • High: Large cable tray scope creates coordination and firestop risk — Verify 1,966 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | • B61-Q1 — Confirm final telecom room list and PMIS mapping: B13H-A, 124, 226 and existing 137/137A demarc/server rooms? [Open] Impact: Room inventory could miss scope • B61-Q2 — What active services and circuits are currently housed in Room 137/137A? [Open] Impact: Potential outage/cutover risk • B61-Q3 — Are B61-TR137AA/AB panel references tied to Room 137 or a schedule naming mismatch for Room 124? [Open] Impact: Electrical PMIS mapping risk • B61-Q4 — Are IU/CU-0-01, 1-01 and 2-01 on emergency/backup power and dedicated to the TRs they serve? [Open] Impact: Cooling continuity unclear • B61-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B61-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown | Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing.
62 | B62 | B62_TR_Assessment | • Verify | • Verify | • Verify | • Verify | • No security / pacs / cctv items captured for this building. | • High: Cooling redundancy / emergency power not verified — Confirm power path for cooling, controls, condensate pump • High: Firestopping condition unknown — Survey penetrations and temporary/permanent firestop plan • Medium: Existing room conditions undocumented — Create photo record before construction begins • High: Condensate leak risk near IT equipment — Verify condensate routing and alarms | • B62-Q1 — Are cooling units emergency powered? [Open] Impact: Cannot confirm continuity of operations • B62-Q2 — Are future rack loads included in HVAC sizing? [Open] Impact: Cooling may be undersized after expansion • B62-Q3 — Is extinguisher location identified within 75 feet? [Open] Impact: Life safety / acceptance risk • B62-Q4 — Are all penetrations fully documented and firestopped? [Open] Impact: Fire/smoke spread risk | Cooling / emergency power not verified
70 | B70 | B70_TR_Assessment | • Verify | • Verify | • Verify | • Verify | • No security / pacs / cctv items captured for this building. | • High: Cooling emergency power / continuity not verified — Confirm power path for cooling, controls, BACnet adapter, and condensate pump • High: 1-hour rated/smoke-rated TR envelope and penetrations not field verified — Survey walls, doors, sleeves, trays, firestop, and head-of-wall conditions • Medium: Existing basement service conditions may constrain routing and access — Document existing utilities, clearances, and phasing around active systems • High: Existing TR/service equipment transfer could affect active operations — Require phasing plan and maintain analog/low-voltage systems operational • High: Condensate leak risk near IT equipment — Verify condensate routing, insulation, pump power, and alarms | • B70-Q1 — Are cooling units and controls on emergency/backup power? [Open] Impact: Cannot confirm continuity of operations • B70-Q2 — Are future rack loads included in HVAC sizing for B27, 125A, and 262A? [Open] Impact: Cooling may be undersized after expansion • B70-Q3 — Are extinguisher cabinet locations identified within 75 feet of each TR? [Open] Impact: Acceptance / life safety risk • B70-Q4 — Are all wall/floor penetrations and speed sleeves shown and firestopped? [Open] Impact: Fire/smoke spread risk • B70-Q5 — What phasing is required to keep existing low-voltage/analog systems operational? [Open] Impact: Potential communications interruption | Cooling / emergency power and existing TR phasing not verified
78 | B78 | B78_Assessment | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, and rated penetrations. • Verify FP/FA modifications, FEC location, temporary firestopping and final UL systems. • Verify first-level TR sprinkler/FA work, FEC location and cable tray penetrations. • Verify second-level TR sprinkler/FA work, FEC location, vertical riser penetrations and firestopping. • Verify third-level TR fire protection/fire alarm coordination and firestop work. | • Mechanical sheets included for basement. Verify dedicated cooling equipment, capacity, condensate, emergency source, controls/BACnet and high-temperature alarm. • Verify dedicated cooling and relationship to B30/B35 telecom buildout. • Verify first-level TR cooling, controls, emergency power and alarm tie-in. • Verify second-level TR cooling, condensate route and 24/7 operation. • Verify third-level TR cooling and control/alarm integration. | • Rack elevations identify new rack UPS/PDU and future rack. Verify panelboard/source, SPD, rack receptacles, PDU feeds, labels, load measurement and LOTO. • Verify rack UPS/PDU source, spare/future rack provisions and grounding/bonding. • Verify first-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. • Verify second-level rack receptacles, UPS/PDU, panel sources, SPDs and labeling. • Verify third-level rack receptacles for two racks, UPS/PDU, panel sources and labels. | • 78_78AT-701: 210 WAO total, 23 active ports, 311 scheduled ports, 342 with allowance; rack IDs TR01-B30-1/-2. Basement cable tray total 1,702 ft. • 78_78AT-702: 53 WAO total, 23 active ports, 64 scheduled ports, 70 with allowance. Confirm rack ID/room relation and active services. • 78_78AT-702/703: 301 WAO total, 388 active ports, 404 scheduled ports, 444 with allowance. Large active port count; high cutover risk. • 78_78AT-703/704: 256 WAO total, 153 active ports, 348 scheduled ports, 383 with allowance. Verify second-level test records and riser labels. • 78_78AT-704: 158 WAO total, 163 active ports, 289 scheduled ports, 318 with allowance. Rack IDs TR01-342-1/-2. | • TR scope includes wall-mounted CCTV cameras and PACS for TR doors. Verify CR/RX/DC/ES/MD, controller and VMS integration. • Verify PACS/CCTV integration and door hardware coordination. • Verify first-level TR PACS/CCTV and VMS integration. • Verify second-level TR PACS/CCTV and VMS integration. • Verify third-level TR PACS/CCTV and VMS integration. | • High: Existing conditions and active equipment across six TRs and existing telecom rooms not field verified — Perform detailed room-by-room existing condition survey with photos and active-service inventory • High: Hazardous material abatement plans exist for basement and third level — Coordinate IH/abatement review before penetrations, wall/ceiling work, cabling or MEP installation • Critical: Existing telecom equipment may remain active during cutover — Document active services, OIT windows, rack inventory, temporary utilities and rollback plan • Critical: Dedicated cooling sequence, emergency power, condensate and alarms not verified — Confirm HVAC equipment serving each TR, emergency source, condensate, controls/BACnet and high-temp alarms • Critical: Panel source, UPS/PDU and rack receptacle coordination could delay energization — Verify telecom panelboards, breakers, rack receptacles, UPS/PDU sources, SPDs, labels and LOTO requirements • High: Large cable tray scope creates coordination and firestop risk — Verify 4,849 ft cable tray route, supports, seismic bracing, 40% fill, MEP conflicts, sleeves and final firestop assemblies | • B78-Q1 — Confirm final telecom room list and PMIS mapping: B30, B35, 1232, 227A, 342, 401 plus existing rooms 15E/1234/353/308A/408A? [Open] Impact: Room inventory could miss scope • B78-Q2 — What active services currently remain in each existing telecom room/photo reference location? [Open] Impact: Potential outage/cutover risk • B78-Q3 — Are Room 1232 and existing Room 1234 separate rooms or naming/mapping references for the same telecom space? [Open] Impact: PMIS mapping risk • B78-Q4 — Which dedicated cooling units serve each TR and are they on emergency/backup power? [Open] Impact: Cooling continuity unclear • B78-Q5 — Where are clean-agent/CO2 FEC cabinets located within 75 ft of each new TR? [Open] Impact: Life-safety acceptance risk • B78-Q6 — Are rack UPS/PDU circuits, SPDs, labels, load measurements and LOTO requirements approved for all TR panelboards? [Open] Impact: Electrical readiness unknown | Building 78/78A is a very large full-scope TR building with basement through fourth-level telecom rooms, existing telecom rooms, hazardous abatement, architectural, fire protection, mechanical, electrical, security, telecom, rack elevations and photo references. Major open issues include active service cutover, dedicated HVAC validation, panel/UPS/PDU coordination, 4,849 ft cable tray routes, firestopping, PACS/CCTV, existing rack transfers, and turnover testing.
80 | B80 | B80_Assessment | • Full fire protection scope included. Verify sprinkler modifications, fire alarm devices, clean-agent 2A:10B:C FEC within 75 ft, rated wall/floor penetrations, and temporary firestopping during cable pulls. • Existing telecom closet/room; verify fire alarm/sprinkler protection-in-place and seal removed/reused penetrations after cutover. | • Mechanical/electrical drawings show IU-1-01 in Telecom Room 102 and CU-1-01 outdoor unit. Confirm capacity, emergency/standby source, BACnet interface, thermostat/control point, condensate pump/path, disconnects, and high-temperature alarm. • Existing telecom room/closet may remain active during cutover. Verify existing environmental condition and whether any active equipment remains after migration to Room 102. | • Electrical plans/schedules identify B80-TR102A fed from BUS-B80-MDP and B80-TR102B fed from BUS-B80-E1, with rack receptacles, normal/emergency circuits, CU-1-01, SPD requirements and 30-day load measurement requirements. • Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | • 80T-701 identifies RM102 with 117 WAO total, 98 active ports per survey, 195 total ports per schedule, and 215 total ports with 10% allowance. Rack IDs include TR01-102-1 and TR01-102-2; rack elevation shows 1 new rack plus future rack with switches, Cat6A patch panels, Cat5e patch panel, Fiber LIU, UPS and PDU. • Existing rack elevation shows Cisco switches, legacy optical Fiber LIU on wall, multiple legacy Ortronics 24/48-port patch panels, legacy Cat5e 24-port patch panel, and APC floor UPS. Contractor must transfer existing devices to new rack and protect active services. | • Electrical/telecom plans show access-control scope and camera 102-CAM-1. Verify CR/RX/DC/ES/MD devices, controller, electric strike, camera/VMS integration, and door hardware coordination. • Verify existing security/PACS equipment conditions and whether any existing camera/security device is protected, recabled, or removed during cutover. | • High: Existing conditions for Room 102 and existing 127A/126 not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing telecom equipment may remain active during transfer to Room 102 — Document active services, protect in place, identify OIT cutover windows, phasing and rollback plan • High: Room-number mismatch between Tel Closet 127A and photo/rack reference Room 126/127-A — Track both IDs in PMIS and confirm field room signage/owner mapping before punch list and turnover • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate route, controls, BACnet adapter, thermostat and high-temp alarm • High: B80-TR102A/B UPS/PDU and panel source coordination could delay energization — Verify panel sources BUS-B80-MDP and BUS-B80-E1, breakers, receptacles, SPD, labels, load measurement and LOTO needs • High: 811 feet of cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, lighting/HVAC conflicts and firestop assemblies | • B80-Q1 — Confirm final telecom scope: new Room 102 with existing 127A/126 transition only? [Open] Impact: Room inventory could miss scope • B80-Q2 — What active services are currently fed from existing Room 127A/126 equipment? [Open] Impact: Potential communications/security outage • B80-Q3 — Are Room 127A and Room 126 the same telecom room, or separate locations? [Open] Impact: PMIS mapping and turnover risk • B80-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? [Open] Impact: Cooling continuity unclear • B80-Q5 — Where is the clean-agent/CO2 extinguisher cabinet located within 75 ft of Room 102? [Open] Impact: Life-safety acceptance risk • B80-Q6 — Are B80-TR102A/B sources, rack receptacles, SPDs, circuit labels and load measurements approved? [Open] Impact: Electrical readiness unknown | Building 80 includes a new first-level Telecom Room 102 and existing Tel Closet 127A / photo-reference Room 126 transition point. Field verification, active equipment transfer, dedicated cooling IU-1-01/CU-1-01, B80-TR102A/B power, 811 ft cable tray, firestopping, PACS/CCTV, existing two-post rack migration, and room-number mapping remain open.
82 | B82 | B82_Assessment | • Cover sheet states Building 82 receives a Telecom Enclosure and fire protection scope is excluded. Still verify rated penetrations, 4-inch sleeve, wall/floor openings, temporary firestopping, and life-safety device impacts. • Existing telecom room; verify protection-in-place and firestopping after cable transfer or reuse. | • Mechanical and electrical drawings show IU-1-01 in/near Telecom Room 102 and CU-1-01 outdoor unit. Mechanical notes call for BACnet adapter mounted adjacent to unit in telecom room. Confirm capacity, emergency/standby source, condensate pump/path, disconnects, controls, and high-temp alarm. • Existing telecom room may remain active during cutover. Verify existing environmental conditions and whether active equipment remains after transfer to Room 102. | • Electrical plans/schedules identify TE receptacle, CU-1-01, B82-MDP and B82-P-EMER sources, with SPD devices integral to new telecom panelboards. Verify receptacle type, grounding/bonding, emergency source, labels, and circuit loading. • Existing rack/equipment area includes APC floor UPS and legacy telecom power. Verify source circuits, active equipment, UPS status, and transfer requirements before disconnect/removal. | • 82T-701 identifies RM102 with 26 WAO total, 31 active ports per survey, 36 total ports per schedule, and 40 total ports with 10% allowance. Rack ID TR01-102-01. Cable tray schedule totals 278 ft on first level. New enclosure includes APC UPS, two PDUs, network switch, Cat6A patch panel and Fiber LIU. • Existing B01-A elevations identify Cisco switches, cable management, two Ortronics 24-port patch panels with 11 and 6 used, existing patch panels and APC floor UPS. Field verify active services and transfer plan to new TE. | • Building 82 appears to create a TE enclosure rather than a full TR door/PACS package. Verify existing cameras/security devices in Room 102 and ensure no camera angle or VMS integration is disrupted. • Keynotes indicate existing cameras are to be retained and re-used. Verify security/access conditions and whether any legacy security equipment is present at existing telecom room. | • High: Existing conditions for new Room 102 TE and existing B01-A not field verified — Perform existing conditions survey with photos before mobilization • Critical: Existing equipment in B01-A may remain active during transfer to new TE in 102 — Document active services, protect in place, identify OIT cutover windows, phasing, rollback path and temporary utilities • High: Cover sheet says TE, but mechanical cooling is included for Room 102 — Confirm scope interpretation with VA/AE and ensure cooling is commissioned if it serves active TE equipment • Critical: Dedicated cooling emergency power, condensate, BACnet and alarms not verified — Confirm IU-1-01/CU-1-01 power source, condensate, controls, BACnet adapter, thermostat and high-temp alarm • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding, SPD and labels • High: 278 feet of first-level cable tray/pathway requires coordination and firestop tracking — Verify route, supports, seismic bracing, 40% fill, penetrations, light/HVAC conflicts and firestop assemblies | • B82-Q1 — Confirm final scope: new 12RU wall-mount TE enclosure in Room 102 and existing B01-A transition only? [Open] Impact: Room inventory or PMIS mapping could miss scope • B82-Q2 — What active services are currently fed from existing B01-A equipment? [Open] Impact: Potential communications/security outage • B82-Q3 — Is Room 102 officially a TE-only scope or a conditioned telecom room with mechanical support? [Open] Impact: Scope and commissioning responsibility unclear • B82-Q4 — Is IU-1-01/CU-1-01 on emergency/backup power and dedicated to Room 102? [Open] Impact: Cooling continuity unclear • B82-Q5 — What is the approved power source, receptacle type and circuit capacity for the new APC UPS/PDU in Room 102? [Open] Impact: Electrical readiness unknown • B82-Q6 — Are all 278 feet of cable tray route, sleeves, supports and firestopping details field verified? [Open] Impact: Install delay or firestop gap | Building 82 is identified as a Telecom Enclosure (TE) building on the cover sheet, with fire protection scope excluded, but mechanical sheets show IU-1-01/CU-1-01 dedicated cooling for Room 102 and electrical drawings show B82-MDP/B82-P-EMER power. Scope centers on new first-level Telecom Room 102 / 12RU enclosure and existing first-level Telecom Room B01-A transition point. Field verification, active-equipment transfer, 278 ft cable tray, firestopping, UPS/PDU power, HVAC controls, fiber/copper cutover, and room/equipment mapping remain open.
BCH | BCH | BCH_Assessment | • Cover sheet states BCH receives a Telecom Enclosure and mechanical/fire protection scope has been excluded. Still verify existing life-safety protection, rated penetrations, 4-inch sleeve fire caulk, temporary firestopping and abandoned penetration patching. • TE-only scope does not appear to require new FEC/fire sprinkler work, but all wall/floor/ceiling penetrations must be sealed and rated assemblies maintained. | • Cover sheet explicitly excludes mechanical scope. Verify existing room ambient conditions are acceptable for TE equipment and that no active network equipment will overheat. • If the final scope is a 45RU new telecom room rather than a small TE, HVAC exclusion should be confirmed with VA/AE because telecom-room heat load may differ from TE assumptions. | • Electrical plan includes first-level electrical work and notes for new wall-mount telecom enclosure, grounding/bonding and camera. Verify circuit source, receptacle type, UPS/PDU load, emergency source if required, grounding/bonding and labels. • BCHT-604 shows 12RU TE equipment with APC UPS and PDUs and also a BCH 45RU new telecom room elevation. Confirm exact UPS/PDU/rack power requirement before acceptance. | • BCHT-101 identifies telecom plan first level and enlarged Room 107. BCHT-604 identifies new telecom room/no existing elevations. There is no BCHT-701 schedule in the drawing index, so WAO/cable-tray totals must be field verified from plans and contractor coordination drawings. • BCHT-604 identifies a 12RU TE elevation: APC UPS, two PDUs, network switch, 48-port Cat6A patch panel and Fiber LIU. Also shows BCH Crescent House Room 107 new telecom room elevation. Confirm governing rack/enclosure and labeling. | • Telecom/electrical notes reference new IP-addressable camera with wall mount at 8'-6" A.F.F. and VMS integration. Verify whether PACS applies; TE buildings typically do not create full TR door/PACS scope. • Verify existing camera/security conditions, protection-in-place, and any recabling or VMS integration required. | • High: Existing conditions for Crescent House Room 107 not field verified — Perform existing conditions survey with photos before mobilization • High: Mechanical and fire protection are excluded despite telecom/electronics installation — Verify existing environmental and life-safety conditions support TE equipment; confirm no dedicated HVAC/FP requirement applies • High: Rack/elevation conflict: TE 12RU enclosure versus BCH Room 107 new telecom room elevation — Submit RFI/confirm with AE which elevation governs and map room/equipment in PMIS • Critical: Active services and existing devices may require phasing/temporary service — Document active services, maintain existing service, use phasing plan, temporary utilities and OIT cutover windows • High: UPS/PDU/receptacle source and grounding/bonding not verified — Verify circuit source, receptacle type, UPS/PDU load, grounding bar, bonding and labels • High: Cable tray, sleeve and pathway quantities not scheduled in a BCHT-701 sheet — Require coordination drawings showing route, supports, fill, penetrations, sleeves and cable counts | • BCH-Q1 — Confirm final BCH scope: Room 107 TE enclosure only, or a new telecom room/rack buildout? [Open] Impact: PMIS scope and acceptance criteria unclear • BCH-Q2 — Why does BCHT-604 show a T78 12RU TE enclosure and a separate BCH Crescent House Room 107 new telecom room elevation? [Open] Impact: Rack/equipment mapping conflict • BCH-Q3 — What active services currently serve Crescent House and where are existing terminations located? [Open] Impact: Cutover/outage risk • BCH-Q4 — What is the approved power source, receptacle type and circuit capacity for the new UPS/PDU? [Open] Impact: Electrical readiness unknown • BCH-Q5 — Is existing HVAC/ambient condition acceptable for TE/network equipment since mechanical scope is excluded? [Open] Impact: Heat/load risk • BCH-Q6 — Are cable tray route, sleeve locations, supports and firestopping details shown/field verified without a BCHT-701 schedule? [Open] Impact: Install delay or firestop gap | Crescent House/BCH is a Telecom Enclosure (TE) scope with mechanical and fire protection excluded by the cover sheet. Scope centers on first-level Room 107 and rack/equipment location shown as Room 00-107 / BCH Crescent House. Field verification, room naming, wall-mounted TE versus 45RU room/rack elevation conflict, active-service cutover, power/UPS/PDU source, firestopping, fiber A/B routing, and cable tray/WAO quantities remain open.
MCR | MCR | MCR_Assessment | • MCR has full fire protection scope including wet pipe and clean-agent fire suppression system. Verify preaction/clean-agent design, agent release interface, fire alarm matrix, detection, abort/release stations, room integrity and acceptance testing. • Verify fiber entrance room protection, rated penetrations, firestopping, detector/strobe coverage and no gaps after cable tray installation. • Verify sprinkler/clean-agent coverage around MDA equipment, fire alarm devices, rack clearance and final firestop assemblies. • Verify clean-agent coverage, detector placement, alarm interfaces, and open cabinet airflow protection. • Existing systems must remain protected during temporary fiber, umbilical cord and core relocation work. Verify no impairment without approved fire watch/impairment plan. | • Telecom notes call for indoor computer room air conditioner (CRAC) units tied to building management system. Mechanical sheets included; verify redundant capacity, setpoints, humidity, condensate, controls, alarms and emergency power. • UPS rooms/equipment require thermal load validation, ventilation, emergency power and alarm integration. Verify battery/UPS environmental requirements. • Verify airflow/cold aisle/hot aisle assumptions, blanking panels, floor/ceiling distribution and temperature monitoring. • Server cabinets and patch fields require stable 24/7 cooling and monitoring. Confirm no local hot spots at dense LIU/patch panel zones. • During split-core temporary phase, existing MCR/server equipment remains active. Verify existing cooling remains in service until cutover and decommissioning are complete. | • Electrical set includes site plan, enlarged MCR plans, one-lines and schedules. Verify switchboard/service, ATS/generator integration, normal/emergency/UPS distribution, grounding, lightning protection, SPD, load measurements and commissioning. • MDA rack elevations include new 4-post floor cabinets, LIUs and network elements. Verify redundant A/B power feeds and PDU arrangements. • HDA cabinets include server cabinet front/rear elevations with patch panels and active equipment. Confirm A/B feed separation, PDU mounting, load capacity and labels. • Existing rack elevations identify multiple APC/Chatsworth/HP PDUs, APC Smart UPS and Eaton 9PX units. Verify what transfers, what stays, and temporary power during migration. • New MCR is standalone critical infrastructure. Verify utility service, generator/ATS paths, emergency distribution, grounding electrode and ductbank/site electrical coordination. | • MCRT-101 shows new MCR with MDA-A/B, HDA-A/B, UPS-A/B, cameras and fiber path legend. MCRT-701 shows 10 WAO total, 720 WAO available, 98.1% expansion capacity, 10 total ports with 20% allowance and 359 ft cable tray. • MCRT-701 Data Device and Circuit Schedule - Fiber Entrance Room 1: outlets 31-A/B/C/D plus security devices 07-CAM-03/04/07/08/11; Rack ID TR01-031-1. • MCRT-607: MDA A/B racks contain horizontal distribution LIUs, hybrid FOC, 48x Cat6A to HDA, and reserved LAN/spine/aggregation elements. Maintain A/B path separation. • MCRT-608/609: HDA A/B include 48-port Cat6A patch panels, HD fiber LIUs, backbone side A/B LIU and server cabinet arrangements. • Existing MCR rows 1-3 and B61 server cabinet transfer references are extensive. Maintain service using temporary fiber/umbilical cords and phased core relocation. | • MCRT-101 identifies cameras 07-CAM-01 through 07-CAM-12 around the MCR. Telecom notes call for IP-addressable network cameras integrated into existing VMS and PACS/access-control systems including iSTAR Edge/Avigilon ACM controller. • MCRT-701 includes security camera/data devices assigned to TR01-031-1. Confirm camera IDs, mounting, cabling, and VMS commissioning. • Verify camera coverage, door/access points, VMS monitoring and access control zones for critical equipment. • Verify coverage of HDA cabinets, doors, motion detection and any lockable cabinet/security requirements. • Existing security systems must remain functional during transition; protect existing camera angles and access controls until final turnover. | • Critical: MCR is a new standalone critical facility with 120-sheet multi-discipline scope — Use discipline-by-discipline pre-install checklist, coordination drawings, third-party inspections and commissioning tracker • Critical: Existing MCR/server/core equipment transfer may interrupt hospital network operations — Require detailed OIT cutover plan, temporary fiber/umbilicals, rollback plan, VA activation windows and after-hours phasing • Critical: A/B fiber path diversity and backbone commissioning not verified — Verify OSP/ISP Path A/B routing, no intermediate splices, test results, labeling and geographic diversity • Critical: UPS-A/B, ATS/generator, panel source and PDU coordination could delay activation — Verify one-line, load banks, breaker settings, panel labels, generator/ATS tests, UPS start-up and A/B power mapping • Critical: CRAC capacity, redundancy, condensate, BMS/FMS alarms and emergency power not verified — Confirm mechanical schedules, CRAC start-up, controls, alarm points, emergency source, environmental monitoring and hot/cold aisle performance • Critical: Clean-agent/preaction/fire alarm interface and room integrity acceptance risk — Track clean-agent calculations, room integrity test, release/abort stations, FA matrix, sprinkler/preaction tests and AHJ/third-party acceptance | • MCR-Q1 — Confirm final room naming and PMIS mapping: MCR Room 107, Fiber Entrance Room 031, Existing 107/137 server/MCR references. [Open] Impact: Room inventory and turnover mapping could be wrong • MCR-Q2 — What existing core/server/rack equipment is being relocated from the existing MCR/server rooms, and what remains? [Open] Impact: Cutover and outage risk • MCR-Q3 — What is the approved MCR activation sequence and required VA/OIT hold points? [Open] Impact: Schedule/cutover impact • MCR-Q4 — Are UPS-A/B, generator/ATS and emergency power paths commissioned and mapped to each rack/PDU? [Open] Impact: Electrical readiness unknown • MCR-Q5 — Are CRAC units fully commissioned with BMS/FMS alarms, redundancy and emergency power? [Open] Impact: Cooling continuity risk • MCR-Q6 — Are clean-agent/preaction/fire alarm systems fully designed, tested and accepted? [Open] Impact: Life-safety acceptance risk | MCR is the most critical EHRM infrastructure building. Scope includes new Main Computer Room, new MDA A/B rows, HDA A/B rows, existing server/MCR equipment transfer from 107/137, redundant fiber Path A/B, new CRAC cooling, UPS A/B, electrical service/ATS/generator integration, clean-agent fire suppression, wet sprinkler/fire alarm interfaces, PACS/CCTV, 359 ft cable tray, and MCR activation window. Major risk is service continuity during backbone/core migration and VA activation.
SPEC | SPEC | SPEC_Assessment | • No fire / life safety items captured for this building. | • No hvac / cooling items captured for this building. | • No electrical / ups items captured for this building. | • No telecom / fiber items captured for this building. | • No security / pacs / cctv items captured for this building. | • No owner risks items captured for this building. | • No open questions items captured for this building.
Campus | Campus | Campus | • No fire / life safety items captured for this building. | • No hvac / cooling items captured for this building. | • No electrical / ups items captured for this building. | • No telecom / fiber items captured for this building. | • No security / pacs / cctv items captured for this building. | • No owner risks items captured for this building. | • No open questions items captured for this building.
SITE | SITE | SITE_Assesment | • General notes require fire lanes, hydrants and fire department access roads operational at all times; maintain egress and provide fire watch/temporary protection when required. • Trench barricades, accessible parking/public access and right-of-way impacts must be coordinated with owner prior to construction. • Rated wall/floor penetrations must be firestopped; temporary firestopping required if penetrations remain open between shifts. • Backbone work affects facility operations. Any required shutdowns must be limited to one at a time and coordinated with approved phasing plan. | • No hvac / cooling items captured for this building. | • Electrical site plans ES101/ES401 are included. Existing utility locations are approximate; coordinate electrical vaults, underground electrical, storm drain manholes and sanitary manholes. • Locking covers and handhole/manhole locations must be field verified. Confirm bonding/grounding requirements where metallic components are present. • T-601 shows WAN/provider fiber entrances and new fiber Path A/B to the MCR. Coordinate with Century Link/service provider and MCR activation. • Coordinate conduit penetrations with building electrical/telecom/firestop scope and avoid conflicts with existing services. | • Legend identifies new fiber in A route, B route, and A+B routes in separate conduits. Confirm no cross-connect gaps at THHs/manholes. • Site one-line shows WAN fiber from service provider and temporary/provider extension pathways. Coordinate with MCR activation and OIT. • Each building tie-in must be tested, labeled, and accepted before connection to active operations. • T-601 one-line lists THH #1-#19 and path counts such as 6 Path A + 4 Path B, 6 Path A + 6 Path B, 7 Path A + 7 Path B, 5 Path A + 4 Path B, and 9 Path A + 7 Path B. | • Coordinate staging, access, material storage, noisy work, utility interruption, trench barricades and public access with owner. • General notes specifically identify accessible parking and public right-of-way impacts; temporary barricades must prevent injury and protect parking signage. • Hand digging at existing utility crossings is in base bid. Confirm permits, Dig Safe, VA utility locate and escort requirements before excavation. | • Critical: Existing utility locations are approximate and field conditions may vary from survey — Complete utility locate, GPR review, potholing/hand-digging at crossings and VA utility coordination before excavation • Critical: A/B fiber path separation may not be maintained through common ductbank or congested areas — Verify separate conduits, route diversity, THH labels, T-601 path counts and as-built documentation • High: Concrete ductbank could be backfilled before inspection — Establish inspection hold point; trench remains open until concrete duct inspection and photos are accepted • Critical: WAN/provider fiber and MCR activation sequence could delay campus cutover — Coordinate Century Link/service provider, temporary fiber, provider extension, MCR readiness and OIT activation plan • High: Trenching/restoration may disrupt accessible parking, fire lanes, public access and campus traffic — Submit traffic/pedestrian/staging plan, maintain fire lanes/hydrants and restore surfaces to match existing • High: Building entry penetrations/firestopping may not align with building PMIS packages — Cross-check every site tie-in against building assessment, T-101 continuation sheets and firestop photos | • SITE-Q1 — Confirm final list of all site fiber buildings and whether Buildings 1-22, 33, 61, 62, 70, 78/78A, 80, 81, 82, Crescent House and MCR are included in one site backbone turnover package. [Open] Impact: Scope and turnover package mapping unclear • SITE-Q2 — Which THH/manhole numbers are new versus existing, and which require locking cover replacement only? [Open] Impact: Structure inventory and inspection scope unclear • SITE-Q3 — Are all A and B routes physically diverse enough and in separate conduit wherever common ductbank is used? [Open] Impact: Redundancy risk • SITE-Q4 — What are the approved utility-locate/potholing requirements before excavation at each crossing? [Open] Impact: Utility strike risk • SITE-Q5 — What inspection hold points are required for ductbank forms, conduit placement, concrete pour, pull string, mandrel and backfill? [Open] Impact: QA acceptance risk • SITE-Q6 — Are directional boring alternatives allowed anywhere, or is all base-bid work trenching unless separately approved by Government? [Open] Impact: Means/methods and cost/schedule risk | Site package controls the redundant telecommunications backbone for the full EHRM campus. Scope includes site survey, electrical site plans, telecom site plans, enlarged views, plan/profile sheets for Path A/B, concrete ductbank, direct-bury conduit, handholes THH #1-#19, communication manholes with locking covers, concrete pullboxes, trench restoration, and the site one-line fiber diagram. Major risks are existing utility conflicts, A/B path separation, ductbank inspection before backfill, MCR activation sequencing, and coordination of multiple building tie-ins.
Source flow: Building Assessment Sheets → _Assessment_Full_View → PMIS_Trade_Notes → _Command_Trade_Notes compatibility layer → Command_Center. Do not manually edit notes here.

## Today's_Focus (hidden)
BEDFORD VA EHRM PMIS — TODAY'S FOCUS / PRIORITY WORKLIST
Purpose: Shows which buildings need attention first. Priority is calculated from shutdowns, open risks, open questions, and readiness gaps. Data remains driven by Building Assessments → PMIS_Data.
Priority | Building | Driver / Major Blocker | Recommended Action | Open Assessment | Command Center |  | Focus Metrics
10.0044 | SITE | Site package controls the redundant telecommunications backbone for the full EHRM campus. Scope includes site survey, electrical site plans, telecom site plans, enlarged views, plan/profile sheets for Path A/B, concrete ductbank, direct-bury conduit, handholes THH #1-#19, communication manholes with locking covers, concrete pullboxes, trench restoration, and the site one-line fiber diagram. Major risks are existing utility conflicts, A/B path separation, ductbank inspection before backfill, MCR activation sequencing, and coordination of multiple building tie-ins. | Complete assessment gaps | Open Assessment | Go to Selector |  | Open Risks | 0
10.0043 | MCR | MCR is the most critical EHRM infrastructure building. Scope includes new Main Computer Room, new MDA A/B rows, HDA A/B rows, existing server/MCR equipment transfer from 107/137, redundant fiber Path A/B, new CRAC cooling, UPS A/B, electrical service/ATS/generator integration, clean-agent fire suppression, wet sprinkler/fire alarm interfaces, PACS/CCTV, 359 ft cable tray, and MCR activation window. Major risk is service continuity during backbone/core migration and VA activation. | Complete assessment gaps | Open Assessment | Go to Selector |  | Open Questions | 0
10.0042 | BCH | Crescent House/BCH is a Telecom Enclosure (TE) scope with mechanical and fire protection excluded by the cover sheet. Scope centers on first-level Room 107 and rack/equipment location shown as Room 00-107 / BCH Crescent House. Field verification, room naming, wall-mounted TE versus 45RU room/rack elevation conflict, active-service cutover, power/UPS/PDU source, firestopping, fiber A/B routing, and cable tray/WAO quantities remain open. | Complete assessment gaps | Open Assessment | Go to Selector |  | Active Shutdowns | 0
10.0041 | 82 | Building 82 is identified as a Telecom Enclosure (TE) building on the cover sheet, with fire protection scope excluded, but mechanical sheets show IU-1-01/CU-1-01 dedicated cooling for Room 102 and electrical drawings show B82-MDP/B82-P-EMER power. Scope centers on new first-level Telecom Room 102 / 12RU enclosure and existing first-level Telecom Room B01-A transition point. Field verification, active-equipment transfer, 278 ft cable tray, firestopping, UPS/PDU power, HVAC controls, fiber/copper cutover, and room/equipment mapping remain open. | Complete assessment gaps | Open Assessment | Go to Selector |  | Avg Readiness | 50.67%
10.004 | 80 | Building 80 includes a new first-level Telecom Room 102 and existing Tel Closet 127A / photo-reference Room 126 transition point. Field verification, active equipment transfer, dedicated cooling IU-1-01/CU-1-01, B80-TR102A/B power, 811 ft cable tray, firestopping, PACS/CCTV, existing two-post rack migration, and room-number mapping remain open. | Complete assessment gaps | Open Assessment | Go to Selector |  | Not Ready | 29
Building | Assessment Sheet | Readiness | Open Risks | Open Questions | Shutdowns | Major Blocker | Priority Score | Recommended Action | Open Assessment | Unique Sort Score
01 | B01_Assessment | 50% | 0 | 0 | 0 | Building 01 is a full-scope telecom room building with new First-Level Telecom Room 107 and existing telecom transition rooms B02, 138, and 282. Scope includes architectural, hazardous, fire protection, mechanical, electrical, telecom, security, rack elevations, schedules, and photo references. Major open items include active service transfer from existing rooms, IU-1-01/CU-1-01 cooling, B01-TR107A/B normal/emergency power, UPS/PDU rack power, PACS/CCTV, 394 ft cable tray, firestopping, fiber Path A/B, and room/equipment cutover planning. | 10 | Complete assessment gaps | Open | 10.0015
02 | B02_Assessment | 50% | 0 | 0 | 0 | Building 02 is a large full-scope telecom room building with new Telecom Rooms 141, 236, and 342, plus existing telecom transition rooms B-06, 141, and 236. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, schedules, PACS/CCTV, and photo references. Major open items include active service transfer, multiple panel sets B02-TR141/236/342 A/B, dedicated cooling CU-1/2/3-01, firestopping, PACS/CCTV integration, 2,560 ft cable tray, and high WAO/cable quantity acceptance. | 10 | Complete assessment gaps | Open | 10.0016
03 | B03_Assessment | 50% | 0 | 0 | 0 | Building 03 is a full-scope telecom room building centered on new/renovated Telecom Room 101E, with existing Basement Telecom Room 107 and existing first-floor DMARC/telecom Room 101C as transition points. Scope includes architectural, infection control, fire protection, mechanical, electrical, telecommunications, rack elevations, Room 107 inventory, PACS/CCTV, 961 ft cable tray, and 206 total ports with allowance. Major open items include transfer from existing 107/101C, active DMARC/fiber protection, B03-TR101CA/B panel sources, CU-01 cooling, firestopping, camera 101C-CAM-01, and OIT acceptance. | 10 | Complete assessment gaps | Open | 10.0017
04 | B04_Assessment | 50% | 0 | 0 | 0 | B04 has multiple TRs across basement/first/second levels; field verification, abatement coordination, cooling power, firestopping, and cutover phasing remain open. | 10 | Complete assessment gaps | Open | 10.0018
05 | B05_Assessment | 55% | 0 | 0 | 0 | Building 05 receives a Telecom Enclosure only; mechanical and fire protection scope is excluded, so TE power, telecom cutover, existing room conditions, and fire/life-safety interfaces must be verified. | 10 | Complete assessment gaps | Open | 10.0019
06 | B06_Assessment | 50% | 0 | 0 | 0 | Building 06 has active existing telecom equipment plus new TR work in Rooms 178 and 233; field verification, cutover phasing, cooling, firestopping, and emergency power remain open. | 10 | Complete assessment gaps | Open | 10.002
07 | B07_Assessment | 50% | 0 | 0 | 0 | Building 07 includes basement TR B-18 and second-level TR 228A; field verification, active-service cutover, cooling, firestopping, rated construction, and power source confirmation remain open. | 10 | Complete assessment gaps | Open | 10.0021
08 | B08_Assessment | 50% | 0 | 0 | 0 | Building 08 includes existing basement telecom equipment at B-15, basement TE/cabling scope at B12B, and new second-level TR 2065A; field verification, abatement, rated construction, cooling/power, firestopping, and cutover phasing remain open. | 10 | Complete assessment gaps | Open | 10.0022
09 | B09_Assessment | 50% | 0 | 0 | 0 | Building 09 includes three telecom spaces across basement, first, and second levels; field verification, hazardous material coordination, active service cutover, cooling, power/panel source, firestopping, and rated wall/door work remain open. | 10 | Complete assessment gaps | Open | 10.0023
10 | B10_Assessment | 50% | 0 | 0 | 0 | Building 10 scope centers on attic Telecom Room 200A with related basement electrical source rooms B24/B25, attic hazardous material abatement, dedicated cooling, new telecom panels, rack/UPS/PDU equipment, firestopping, and cutover coordination. | 10 | Complete assessment gaps | Open | 10.0024
12 | B12_Assessment | 60% | 0 | 0 | 0 | Building 12 is explicitly identified as fiber-only with no new TR buildout, no new rack, and no electrical/HVAC/fire protection drawing packages; key owner risk is confirming pull-through fiber path, existing service continuity, pathway/firestopping, and VA/OIT acceptance before cutover. | 10 | Complete assessment gaps | Open | 10.0025
13 | B13_Assessment | 50% | 0 | 0 | 0 | Building 13 includes new first-level Telecom Room 124 and existing second-level Tel Room 222; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 10 | Complete assessment gaps | Open | 10.0026
14 | B14_Assessment | 50% | 0 | 0 | 0 | Building 14 includes new first-level Telecom Room 119 and existing basement telecom rooms B.01/B2; field verification, active service cutover, 240V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 10 | Complete assessment gaps | Open | 10.0027
15 | B15_Assessment | 50% | 0 | 0 | 0 | Building 15 includes new first-level Telecom Room 124A and existing telecom transition points at second-level Tel Room 222 and basement B01; field verification, active service cutover, 240V UPS/PDU power, dedicated heat-pump cooling, first-level hazardous material coordination, firestopping, and PACS/CCTV integration remain open. | 10 | Complete assessment gaps | Open | 10.0028
16 | B16_Assessment | 50% | 0 | 0 | 0 | Building 16 includes new basement Telecom Room 015 and existing basement Telecom Room 014; field verification, active service transfer, 240V UPS/PDU power, dedicated cooling, panel replacement/source coordination, firestopping, PACS/CCTV integration, and cable tray coordination remain open. | 10 | Complete assessment gaps | Open | 10.0029
17 | B17_Assessment | 50% | 0 | 0 | 0 | Building 17_29 includes new first-level Telecom Room 118 serving Building 17 and Building 29, plus existing basement Telecom Closet B35A; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, first-level hazardous material coordination, cable tray, firestopping, and PACS/CCTV integration remain open. | 10 | Complete assessment gaps | Open | 10.003
18 | B18_Assessment | 50% | 0 | 0 | 0 | Building 18 includes new first-level Telecom Room 110 and existing telecom transition rooms 111B and 213; field verification, active-service transfer, 208V UPS/PDU power, dedicated cooling, lead-paint/first-level hazardous material coordination, firestopping, cable tray, and PACS/CCTV integration remain open. | 10 | Complete assessment gaps | Open | 10.0031
20 | B20_Assessment | 50% | 0 | 0 | 0 | Building 20 is a telecom-enclosure building, not a full TR buildout. Scope centers on new first-level Office 1B wall-mount TE enclosure and existing Tel/Data Closet 8A; mechanical and fire protection scope are excluded by the cover sheet, but field verification, active equipment transfer, fiber/copper cutover, cable tray, firestopping, power/UPS/PDU, and existing equipment protection remain open. | 10 | Complete assessment gaps | Open | 10.0032
21 | B21_Assessment | 50% | 0 | 0 | 0 | Building 21 is combined with Building 19 and is primarily a telecom-enclosure scope. New first-level M&O Foreman Office 100A / RM 104 schedule is served by a new 12RU TE enclosure, while existing Building 21 B1.TR and Building 19 B05TR equipment remain transition points. Fire protection scope is excluded, but mechanical/electrical sheets exist for equipment support. Field verification, active-service transfer, 659 ft cable tray, firestopping, UPS/PDU power, fiber/copper cutover, and B19/B21 scope boundary remain open. | 10 | Complete assessment gaps | Open | 10.0033
22 | B22_Assessment | 50% | 0 | 0 | 0 | Building 22 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new first-level Break Room 102 TE enclosure and existing first-level wall/wall-mount TE Room 103. Field verification, active service transfer, 139 ft cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, and B19 utility service relationship remain open. | 10 | Complete assessment gaps | Open | 10.0034
33 | B33_Assessment | 50% | 0 | 0 | 0 | Building 33 is a telecom-enclosure building with mechanical and fire protection scope excluded. Scope centers on new basement EEO Manager Office B23 TE enclosure and existing Tel Closet B17. Field verification, active service transfer, 102 ft basement cable tray, 10 Cat6A cross-connect cables, UPS/PDU power, firestopping, fiber/copper cutover, and legacy service relationships to Buildings 3, 80 and 82 remain open. | 10 | Complete assessment gaps | Open | 10.0035
61 | B61_Assessment | 55% | 0 | 0 | 0 | Building 61 is a large full-scope TR building with hazardous abatement, architectural, fire protection, plumbing, mechanical, electrical, security, telecom, server/demarc and rack elevation scope. Primary new telecom rooms include basement B13H-A, first-level 124, second-level 226, and existing Room 137/137A demarc/server equipment. Major open issues include active-service cutover, dedicated cooling IU/CU-0-01/1-01/2-01, panel source coordination, rack UPS/PDU power, cable tray coordination, firestopping, PACS/CCTV, and turnover testing. | 10 | Complete assessment gaps | Open | 10.0036
62 | B62_TR_Assessment | 50% | 0 | 0 | 0 | Cooling / emergency power not verified | 10 | Complete assessment gaps | Open | 10.0037
70 | B70_TR_Assessment | 50% | 0 | 0 | 0 | Cooling / emergency power and existing TR phasing not verified | 10 | Complete assessment gaps | Open | 10.0038
78 | B78_Assessment | 50% | 0 | 0 | 0 | Building 78/78A is a very large full-scope TR building with basement through fourth-level telecom rooms, existing telecom rooms, hazardous abatement, architectural, fire protection, mechanical, electrical, security, telecom, rack elevations and photo references. Major open issues include active service cutover, dedicated HVAC validation, panel/UPS/PDU coordination, 4,849 ft cable tray routes, firestopping, PACS/CCTV, existing rack transfers, and turnover testing. | 10 | Complete assessment gaps | Open | 10.0039
80 | B80_Assessment | 50% | 0 | 0 | 0 | Building 80 includes a new first-level Telecom Room 102 and existing Tel Closet 127A / photo-reference Room 126 transition point. Field verification, active equipment transfer, dedicated cooling IU-1-01/CU-1-01, B80-TR102A/B power, 811 ft cable tray, firestopping, PACS/CCTV, existing two-post rack migration, and room-number mapping remain open. | 10 | Complete assessment gaps | Open | 10.004
82 | B82_Assessment | 50% | 0 | 0 | 0 | Building 82 is identified as a Telecom Enclosure (TE) building on the cover sheet, with fire protection scope excluded, but mechanical sheets show IU-1-01/CU-1-01 dedicated cooling for Room 102 and electrical drawings show B82-MDP/B82-P-EMER power. Scope centers on new first-level Telecom Room 102 / 12RU enclosure and existing first-level Telecom Room B01-A transition point. Field verification, active-equipment transfer, 278 ft cable tray, firestopping, UPS/PDU power, HVAC controls, fiber/copper cutover, and room/equipment mapping remain open. | 10 | Complete assessment gaps | Open | 10.0041
BCH | BCH_Assessment | 50% | 0 | 0 | 0 | Crescent House/BCH is a Telecom Enclosure (TE) scope with mechanical and fire protection excluded by the cover sheet. Scope centers on first-level Room 107 and rack/equipment location shown as Room 00-107 / BCH Crescent House. Field verification, room naming, wall-mounted TE versus 45RU room/rack elevation conflict, active-service cutover, power/UPS/PDU source, firestopping, fiber A/B routing, and cable tray/WAO quantities remain open. | 10 | Complete assessment gaps | Open | 10.0042
MCR | MCR_Assessment | 50% | 0 | 0 | 0 | MCR is the most critical EHRM infrastructure building. Scope includes new Main Computer Room, new MDA A/B rows, HDA A/B rows, existing server/MCR equipment transfer from 107/137, redundant fiber Path A/B, new CRAC cooling, UPS A/B, electrical service/ATS/generator integration, clean-agent fire suppression, wet sprinkler/fire alarm interfaces, PACS/CCTV, 359 ft cable tray, and MCR activation window. Major risk is service continuity during backbone/core migration and VA activation. | 10 | Complete assessment gaps | Open | 10.0043
SITE | SITE_Assesment | 50% | 0 | 0 | 0 | Site package controls the redundant telecommunications backbone for the full EHRM campus. Scope includes site survey, electrical site plans, telecom site plans, enlarged views, plan/profile sheets for Path A/B, concrete ductbank, direct-bury conduit, handholes THH #1-#19, communication manholes with locking covers, concrete pullboxes, trench restoration, and the site one-line fiber diagram. Major risks are existing utility conflicts, A/B path separation, ductbank inspection before backfill, MCR activation sequencing, and coordination of multiple building tie-ins. | 10 | Complete assessment gaps | Open | 10.0044